## Geometry Summary (hidden)
Abbreviation | Building Type | Shape | Number of Floors | Aspect Ratio | Zone Height_1 | Zone Height_2 | Zone Height_3 | Plenum Height | Floor to Floor Height (feet) | Floor to Ceiling Height (feet)
Asm | Assembly | #VALUE! | 1 | 1 | 12.0006 | na | na | 3.0001 | 12.0006 | 15.0007
ECC | Education - Community College | #VALUE! | 3 | 5.7 | 9.0004 | 13.0006 | na | 4.0002 | 9 / 13 | 13 / 17
EPr | Education - Primary School | #VALUE! | 1 | 2 | 9.0004 | 12.0006 | na | 3.0001 | 9 / 12 | 12 / 15
ERC | Education - Relocatable Classroom | #VALUE! | 1 | 1.7 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
ESe | Education - Secondary School | #VALUE! | 2 | 2.5/1.0 | 9.0004 | 13.0006 | na | 4.0002 | 9 / 13 | 13 / 17
EUn | Education - University | #VALUE! | 4 | 2.0/15.0 | 10.0005 | 9.0004 | 14.0007 | 4.0002 | 9 / 10 / 14 | 13 / 14 / 18
Fin | Financial buildings, incl. banks | #VALUE! | 1 | 1 | 11.0005 | na | na | na | 11.0005 | 11.0005
Gro | Grocery | #VALUE! | 1 | 1 | 25.0012 | na | na | na | 25.0012 | 25.0012
Hsp | Health/Medical - Hospital | #VALUE! | 3 | 1 | 10.007 | 12.9927 | na | 2.9857 | 10 / 13 | 13 / 16
Htl | Lodging - Hotel | #VALUE! | 4 | 6.6 | 8.0004 | 10.5005 | na | 1.5001 | 8 / 11 | 10 / 12
Lib | Libraries | #VALUE! | 1 | 1 | 13.0006 | na | na | na | 13.0006 | 13.0006
MBT | Manufacturing Biotech | #VALUE! | 1 | 6 | 9.0004 | na | na | 6.0003 | 9.0004 | 15.0008
MLI | Manufacturing Light Industrial | #VALUE! | 1 | 1 | 35.0017 | na | na | na | 35.0017 | 35.0017
Mtl | Lodging - Motel | #VALUE! | 2 | 5.1 | 9.0004 | na | na | na | 9.0004 | 9.0004
Nrs | Health/Medical - Nursing Home | #VALUE! | 2 | 10.3 | 12.9986 | 9.0005 | na | 4.0055 | 9 / 13 | 13 / 17
OfL | Office - Large | #VALUE! | 3 | 1.5 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
OfS | Office - Small | #VALUE! | 2 | 1.5 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
Rel | Religious assembly buildings | #VALUE! | 1 | 2.5 | 37.5018 | 15.0007 | na | na | 38 / 15 | 38 / 15
RFF | Restaurant - Fast-Food | #VALUE! | 1 | 1 | 10.0005 | na | na | 3.0002 | 10.0005 | 13.0007
RSD | Restaurant - Sit-Down | #VALUE! | 1 | 1 | 10.0005 | na | na | 3.0001 | 10.0005 | 13.0006
Rt3 | Retail - Multistory Large | #VALUE! | 3 | 1 | 15.0007 | na | na | 5.8002 | 15.0007 | 20.8009
RtL | Retail - Single-Story Large | #VALUE! | 1 | 1 | 20.501 | na | na | na | 20.501 | 20.501
RtS | Retail - Small | #VALUE! | 1 | 1 | 10.0005 | na | na | 2.0001 | 10.0005 | 12.0006
SCn | Storage - Conditioned | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023
SUn | Storage - Unconditioned | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023
WRf | Warehouse - Refrigerated | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023

## Prototype
TRC, Updated Febuary 2026
Education - Primary School
Characteristic | Value
Building Type | Education - Primary School
Building Category | Nonresidential
Vintages | Two vintages: Existing and New Construction
Shape | #VALUE!
Total Floor Area (ft²) | 40749.5
Aspect Ratio | 2
Number of Floors | 1
Roof Type | Flat Roof
Gross Window to Wall Ratio (%) | 20.99
Shading Geometry | No Shading
Floor to Floor Height (feet) | 9 / 12
Floor to Ceiling Height (feet) | 12 / 15
Glazing Sill Height (feet) | 3

## Notes
Prototype Overview
Name | Description
Asm | Assembly
ECC | Education - Community College
EPr | Education - Primary School
ERC | Education - Relocatable Classroom
ESe | Education - Secondary School
EUn | Education - University
Fin | Financial buildings, incl. banks
Gro | Grocery
Hsp | Health/Medical - Hospital
Htl | Lodging - Hotel
Lib | Libraries
MBT | Manufacturing Biotech
MLI | Manufacturing Light Industrial
Mtl | Lodging - Motel
Nrs | Health/Medical - Nursing Home
OfL | Office - Large
OfS | Office - Small
Rel | Religious assembly buildings
RFF | Restaurant - Fast-Food
RSD | Restaurant - Sit-Down
Rt3 | Retail - Multistory Large
RtL | Retail - Single-Story Large
RtS | Retail - Small
SCn | Storage - Conditioned
SUn | Storage - Unconditioned
WRf | Warehouse - Refrigerated
Vintages
Existing | Weighted average of Title 24 requirements based on vintages from 1975 to 2022
New Construction | Title 24 2025
Run Begin Day
Begin Month | Begin Day of Month | Day of Week for Start Day
1 | 1 | Sunday
Special Days
Name | Start Date | Duration (days) | Special Day Type
New Years Day | January 1 | 1 | Holiday
Veterans Day | November 11 | 1 | Holiday
Christmas | December 25 | 1 | Holiday
Independence Day | July 4 | 1 | Holiday
MLK Day | 3rd Monday in January | 1 | Holiday
Presidents Day | 3rd Monday in February | 1 | Holiday
Memorial Day | Last Monday in May | 1 | Holiday
Labor Day | 1st Monday in September | 1 | Holiday
Columbus Day | 2nd Monday in October | 1 | Holiday
Thanksgiving | 4th Thursday in November | 1 | Holiday

## Raw_runbeginday (hidden)
Begin Month | Begin Day of Month | Day of Week for Start Day
1 | 1 | Sunday

## Raw_specialdays (hidden)
Name | Start Day | Duration | Special Day Type
New Years Day | January 1 | 1 | Holiday
Veterans Day | November 11 | 1 | Holiday
Christmas | December 25 | 1 | Holiday
Independence Day | July 4 | 1 | Holiday
MLK Day | 3rd Monday in January | 1 | Holiday
Presidents Day | 3rd Monday in February | 1 | Holiday
Memorial Day | Last Monday in May | 1 | Holiday
Labor Day | 1st Monday in September | 1 | Holiday
Columbus Day | 2nd Monday in October | 1 | Holiday
Thanksgiving | 4th Thursday in November | 1 | Holiday

## Climate Zone
Climate Zones - All Prototypes
Climate Zone | Representative City | Weather File Name
CZ01 | Eureka | CA_EUREKA_725940S_CZ2022.epw
CZ02 | Napa | CA_NAPA-CO_724955S_CZ2022.epw
CZ03 | Oakland | CA_OAKLAND-METRO-AP_724930S_CZ2022.epw
CZ04 | San Jose | CA_SAN-JOSE-IAP_724945S_CZ2022.epw
CZ05 | Santa Maria | CA_SANTA-MARIA-PUBLIC-AP_723940S_CZ2022.epw
CZ06 | Los Angeles | CA_LOS-ANGELES-IAP_722950S_CZ2022.epw
CZ07 | San Diego-Lindbergh | CA_SAN-DIEGO-LINDBERGH-FLD_722900S_CZ2022.epw
CZ08 | Long Beach-Daugherty | CA_LONG-BEACH-DAUGHERTY-FLD_722970S_CZ2022.epw
CZ09 | Los Angeles | CA_LOS-ANGELES-DOWNTOWN-USC_722874S_CZ2022.epw
CZ10 | Riverside | CA_RIVERSIDE-MUNI_722869S_CZ2022.epw
CZ11 | Red Bluff | CA_RED-BLUFF-MUNI-AP_725910S_CZ2022.epw
CZ12 | Stockton | CA_STOCKTON-METRO-AP_724920S_CZ2022.epw
CZ13 | Fresno Yosemite | CA_FRESNO-YOSEMITE-IAP_723890S_CZ2022.epw
CZ14 | Daggett Barstow | CA_DAGGETT-BARSTOW-AP_723815S_CZ2022.epw
CZ15 | El Centro | CA_EL-CENTRO-NAF_722810S_CZ2022.epw
CZ16 | Bishop | CA_BISHOP-AP_724800S_CZ2022.epw
Source: California Energy Commission, https://cecgis-caenergy.opendata.arcgis.com/datasets/CAEnergy::california-building-climate-zones/about

## Zones
Zone Summary - Education - Primary School
Space | Zone Name | Conditioned [Y/N] | Zone Type | HVAC System Identifier (Main/Alternative/Customized) | Schedule Identifier | Area Fraction | Area (Excluding Plenums and Crawl Space) (ft²) | Volume (ft³) | Multipliers | People (Persons/1,000 ft²) | Note
CLASSROOM G.E1 | CLASSROOM G.E1 | Yes | Classroom_class | Main | School | 14.11% | 5751.45 | 51765.56 | 1 | 25
CLASSROOM G.NNE2 | CLASSROOM G.NNE2 | Yes | Classroom_class | Main | School | 8.151% | 3321.4 | 29894.07 | 1 | 25
CLASSROOM G.SSE3 | CLASSROOM G.SSE3 | Yes | Classroom_class | Main | School | 8.151% | 3321.39 | 29893.97 | 1 | 25
CLASSROOM G.W4 | CLASSROOM G.W4 | Yes | Classroom_class | Main | School | 8.232% | 3354.33 | 30190.42 | 1 | 25
DINING G.SSW1 | DINING G.SSW1 | Yes | Dining_fast | Main | School | 9.213% | 3754.31 | 45053.94 | 1 | 33.33
GYMNASIUM G.N2 | GYMNASIUM G.N2 | Yes | Gym | Main | School | 9.196% | 3747.29 | 44969.62 | 1 | 33.33
KITCHEN G.E3 | KITCHEN G.E3 | Yes | Kitchen | Customized | Kitchen | 4.296% | 1750.76 | 21010.09 | 1 | 2.5
PLENUM G.E5 | PLENUM G.E5 | No | Plenum | - | Plenum | 14.11% | 5751.45 | 17255.19 | 1 | 0
PLENUM G.NNE6 | PLENUM G.NNE6 | No | Plenum | - | Plenum | 8.151% | 3321.4 | 9964.69 | 1 | 0
PLENUM G.SSE7 | PLENUM G.SSE7 | No | Plenum | - | Plenum | 8.151% | 3321.39 | 9964.66 | 1 | 0
PLENUM G.W8 | PLENUM G.W8 | No | Plenum | - | Plenum | 8.232% | 3354.33 | 10063.47 | 1 | 0
Total (11 Space) | Total (11 Space) | Total (7 Conditioned zones, 4 Unconditioned Zones) |  |  |  |  | 40749.5

## Envelope
Envelope - Education - Primary School
Element | Prototype | Assembly Type | Construction | Unit | Vintage | Selected T24 | Note | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Education - Primary School | - | Stucco+Wall Continuous Insulation+Gypsum 5/8in | U-value IP | Existing | Weighted average |  | 0.118 | 0.109 | 0.119 | 0.107 | 0.116 | 0.118 | 0.112 | 0.117 | 0.11 | 0.091 | 0.103 | 0.103 | 0.102 | 0.097 | 0.086 | 0.098
External Wall | Education - Primary School | - | Stucco+Wall Continuous Insulation+Gypsum 5/8in | U-value IP | New Construction | 2025 |  | 0.084 | 0.055 | 0.112 | 0.055 | 0.103 | 0.112 | 0.112 | 0.103 | 0.055 | 0.055 | 0.044 | 0.055 | 0.055 | 0.055 | 0.039 | 0.055
Roof | Education - Primary School | - | Roof Membrane+Roof Continuous Insulation+Metal Decking | U-value IP | Existing | Weighted average |  | 0.067 | 0.066 | 0.067 | 0.065 | 0.067 | 0.074 | 0.073 | 0.073 | 0.07 | 0.061 | 0.063 | 0.063 | 0.063 | 0.061 | 0.059 | 0.061
Roof | Education - Primary School | - | Roof Membrane+Roof Continuous Insulation+Metal Decking | U-value IP | New Construction | 2025 |  | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.048 | 0.048 | 0.048 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | Education - Primary School | - | Theoretical Glazing | U-value IP | Existing | Weighted average |  | 1.024 | 1.078 | 1.131 | 1.108 | 1.109 | 1.115 | 1.075 | 1.114 | 1.112 | 0.875 | 0.942 | 0.94 | 0.929 | 0.886 | 0.831 | 0.885
Windows | Education - Primary School | - | Theoretical Glazing | U-value IP | New Construction | 2025 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
Windows | Education - Primary School | - | Theoretical Glazing | SHGC | Existing | Weighted average |  | 0.70708 | 0.70715 | 0.73753 | 0.71836 | 0.75308 | 0.7254 | 0.72673 | 0.7241 | 0.72365 | 0.5734 | 0.64366 | 0.64394 | 0.6358 | 0.60724 | 0.57129 | 0.62767
Windows | Education - Primary School | - | Theoretical Glazing | SHGC | New Construction | 2025 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Windows | Education - Primary School | - | Theoretical Glazing | Visible Transmittance | Existing | Weighted average |  | 0.26089 | 0.26141 | 0.26004 | 0.26231 | 0.26223 | 0.26197 | 0.26576 | 0.26213 | 0.26228 | 0.27816 | 0.26665 | 0.26607 | 0.26793 | 0.27125 | 0.27583 | 0.27139
Windows | Education - Primary School | - | Theoretical Glazing | Visible Transmittance | New Construction | 2025 |  | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
Infiltration - Education - Primary School
|  |  |  | Element | Unit | Vintage | Note | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
|  |  |  | Infiltration Rate | CFM/ft2 | Existing | Infiltration rate is flow rate per exterior surface area at 10 mph wind speed, modeled proportionally to wind speed. | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801
[6 empty] | New Construction |  | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801

## Raw_envelope (hidden)
Climate Zone | Vintage | Exterior Roof Layers | Roof U-Value [Btu/h-ft2-F] | Exterior Wall Layers | Wall U-Value [Btu/h-ft2-F] | Exterior Window Layers | Window U-Value [Btu/h-ft2-F] | Window SHGC | Window VT
CZ01 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.067 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.118 | Theoretical Glazing | 1.024 | 0.70708 | 0.26089
CZ02 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.066 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.109 | Theoretical Glazing | 1.078 | 0.70715 | 0.26141
CZ03 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.067 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.119 | Theoretical Glazing | 1.131 | 0.73753 | 0.26004
CZ04 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.107 | Theoretical Glazing | 1.108 | 0.71836 | 0.26231
CZ05 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.067 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.116 | Theoretical Glazing | 1.109 | 0.75308 | 0.26223
CZ06 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.074 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.118 | Theoretical Glazing | 1.115 | 0.7254 | 0.26197
CZ07 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.073 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.112 | Theoretical Glazing | 1.075 | 0.72673 | 0.26576
CZ08 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.073 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.117 | Theoretical Glazing | 1.114 | 0.7241 | 0.26213
CZ09 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.07 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.11 | Theoretical Glazing | 1.112 | 0.72365 | 0.26228
CZ10 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.091 | Theoretical Glazing | 0.875 | 0.5734 | 0.27816
CZ11 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.063 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.103 | Theoretical Glazing | 0.942 | 0.64366 | 0.26665
CZ12 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.063 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.103 | Theoretical Glazing | 0.94 | 0.64394 | 0.26607
CZ13 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.063 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.102 | Theoretical Glazing | 0.929 | 0.6358 | 0.26793
CZ14 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.097 | Theoretical Glazing | 0.886 | 0.60724 | 0.27125
CZ15 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.059 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.086 | Theoretical Glazing | 0.831 | 0.57129 | 0.27583
CZ16 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.098 | Theoretical Glazing | 0.885 | 0.62767 | 0.27139
CZ01 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.084 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ02 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ03 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.112 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ04 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ05 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.103 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ06 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.048 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.112 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ07 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.048 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.112 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ08 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.048 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.103 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ09 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ10 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ11 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.044 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ12 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ13 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ14 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ15 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.039 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ16 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.36 | 0.25 | 0.42

## Raw_infiltrationcfmft (hidden)
Vintage | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Existing | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801
New Construction | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801

## Thermostat
Thermostat Setpoints - Education - Primary School | [18 empty] | Zone Type
Schedule Identifier | Setpoint | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Notes | Kitchen
Kitchen | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | School
Kitchen | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
School | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
School | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
School | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Raw_thermostatsetpoints (hidden)
Climate Zone | Schedule Identifier | Heating Setpoint (F) | Heating Setback (F) | Cooling Setpoint (F) | Cooling Setback (F)
CZ01 | Kitchen | 70 | 60 | 75 | 85
CZ01 | School | 70 | 60 | 75 | 85
CZ02 | Kitchen | 70 | 60 | 75 | 85
CZ02 | School | 70 | 60 | 75 | 85
CZ03 | Kitchen | 70 | 60 | 75 | 85
CZ03 | School | 70 | 60 | 75 | 85
CZ04 | Kitchen | 70 | 60 | 75 | 85
CZ04 | School | 70 | 60 | 75 | 85
CZ05 | Kitchen | 70 | 60 | 75 | 85
CZ05 | School | 70 | 60 | 75 | 85
CZ06 | Kitchen | 70 | 60 | 75 | 85
CZ06 | School | 70 | 60 | 75 | 85
CZ07 | Kitchen | 70 | 60 | 75 | 85
CZ07 | School | 70 | 60 | 75 | 85
CZ08 | Kitchen | 70 | 60 | 75 | 85
CZ08 | School | 70 | 60 | 75 | 85
CZ09 | Kitchen | 70 | 60 | 75 | 85
CZ09 | School | 70 | 60 | 75 | 85
CZ10 | Kitchen | 70 | 60 | 75 | 85
CZ10 | School | 70 | 60 | 75 | 85
CZ11 | Kitchen | 70 | 60 | 75 | 85
CZ11 | School | 70 | 60 | 75 | 85
CZ12 | Kitchen | 70 | 60 | 75 | 85
CZ12 | School | 70 | 60 | 75 | 85
CZ13 | Kitchen | 70 | 60 | 75 | 85
CZ13 | School | 70 | 60 | 75 | 85
CZ14 | Kitchen | 70 | 60 | 75 | 85
CZ14 | School | 70 | 60 | 75 | 85
CZ15 | Kitchen | 70 | 60 | 75 | 85
CZ15 | School | 70 | 60 | 75 | 85
CZ16 | Kitchen | 70 | 60 | 75 | 85
CZ16 | School | 70 | 60 | 75 | 85

## HVAC System
HVAC system - Education - Primary School
Vintage | System Name | Category | Heating Type* | Cooling Type* | Air Distribution | Heating Efficiency | Cooling Efficiency | Note
Existing | cDXGF | Main | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.65
Existing | cDXGF | Alternative | - | - | - | - | -
Existing | cDXGF | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.8476
New Construction | cDXGF | Main | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.65
New Construction | cDXGF | Alternative | - | - | - | - | -
New Construction | cDXGF | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.8476
Existing | cDXHP | Main | DX-AIR | DX-AIR | SZ-CAV | 3.738 | 3.65
Existing | cDXHP | Alternative | - | - | - | - | -
Existing | cDXHP | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.8476
New Construction | cDXHP | Main | DX-AIR | DX-AIR | SZ-CAV | 3.738 | 3.65
New Construction | cDXHP | Alternative | - | - | - | - | -
New Construction | cDXHP | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.8476
Existing | cAVVG | Main | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Alternative | - | - | - | - | -
Existing | cAVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.8476
New Construction | cAVVG | Main | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Alternative | - | - | - | - | -
New Construction | cAVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.8476
Existing | cDXOH | Main | None | DX-AIR | SZ-CAV | - | 3.65
Existing | cDXOH | Alternative | - | - | - | - | -
Existing | cDXOH | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.8476
New Construction | cDXOH | Main | None | DX-AIR | SZ-CAV | - | 3.65
New Construction | cDXOH | Alternative | - | - | - | - | -
New Construction | cDXOH | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.8476
Existing | cPVVG | Main | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.65
Existing | cPVVG | Alternative | - | - | - | - | -
Existing | cPVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.8476
New Construction | cPVVG | Main | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.65
New Construction | cPVVG | Alternative | - | - | - | - | -
New Construction | cPVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.8476
*DX Heating and cooling COPs are calculated based on coil-only input power and exclude fan power
Fan Power - Education - Primary School
Vintage | System Name | HVAC System Identifier | Fan System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm | Note
Existing | cAVVG | Main | MZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cAVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cAVVG | Main | MZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cAVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXGF | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXGF | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXGF | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXGF | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXHP | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXHP | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXHP | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXHP | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXOH | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXOH | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXOH | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXOH | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cPVVG | Main | SZ-VAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cPVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cPVVG | Main | SZ-VAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cPVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7

## Raw_fanoverview (hidden)
Vintage | HVAC name | System type | HVAC System Identifier | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm
Existing | cAVVG | MZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cAVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cAVVG | MZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cAVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXGF | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXGF | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXGF | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXGF | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXHP | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXHP | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXHP | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXHP | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXOH | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXOH | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXOH | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXOH | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cPVVG | SZ-VAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cPVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cPVVG | SZ-VAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cPVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7

## Raw_hvac (hidden)
Vintage | System Name | HVAC System Identifier | Air Distribution | Heating Efficiency | Cooling Efficiency | Cooling Coil Type | Heating Coil Type
Existing | cAVVG | Main | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Customized | SZ-CAV | 0.8 | 3.8476 | DX-AIR | COMBUSTION
New Construction | cAVVG | Main | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Customized | SZ-CAV | 0.8 | 3.8476 | DX-AIR | COMBUSTION
Existing | cDXGF | Main | SZ-CAV | 0.8 | 3.65
Existing | cDXGF | Customized | SZ-CAV | 0.8 | 3.8476 | DX-AIR | COMBUSTION
New Construction | cDXGF | Main | SZ-CAV | 0.8 | 3.65
New Construction | cDXGF | Customized | SZ-CAV | 0.8 | 3.8476 | DX-AIR | COMBUSTION
Existing | cDXHP | Main | SZ-CAV | 3.738 | 3.65
Existing | cDXHP | Customized | SZ-CAV | 0.8 | 3.8476 | DX-AIR | COMBUSTION
New Construction | cDXHP | Main | SZ-CAV | 3.738 | 3.65
New Construction | cDXHP | Customized | SZ-CAV | 0.8 | 3.8476 | DX-AIR | COMBUSTION
Existing | cDXOH | Main | SZ-CAV | - | 3.65
Existing | cDXOH | Customized | SZ-CAV | 0.8 | 3.8476 | DX-AIR | COMBUSTION
New Construction | cDXOH | Main | SZ-CAV | - | 3.65
New Construction | cDXOH | Customized | SZ-CAV | 0.8 | 3.8476 | DX-AIR | COMBUSTION
Existing | cPVVG | Main | SZ-VAV | 0.8 | 3.65
Existing | cPVVG | Customized | SZ-CAV | 0.8 | 3.8476 | DX-AIR | COMBUSTION
New Construction | cPVVG | Main | SZ-VAV | 0.8 | 3.65
New Construction | cPVVG | Customized | SZ-CAV | 0.8 | 3.8476 | DX-AIR | COMBUSTION

## Ventilation
Outdoor Airflow Rate - Education - Primary School | [19 empty] | Zone Type
Zone Type | Floor area (ft²) | cfm/person | cfm/ft² | cfm | Notes | [14 empty] | Classroom_class
Classroom_class | 15748.57 | 0 | 0.38 | 5984.4566 | [15 empty] | Dining_fast
Dining_fast | 3754.31 | 0 | 0.5 | 1877.155 | [15 empty] | Gym
Gym | 3747.29 | 0 | 0.5 | 1873.645 | [15 empty] | Kitchen
Kitchen | 1750.76 | 0 | 0.15 | 262.614 | [15 empty] | Plenum
Plenum | 15748.57 | 0 | 0 | 0
OA Controller - Education - Primary School
Element | Vintage | Unit | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Notes
Economizer Maximum Limit Dry-Bulb Temperature | Existing | °F | 75 | 73 | 75 | 73 | 75 | 71 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 75 | 75 | 75
| New Construction | °F | 75 | 73 | 75 | 73 | 75 | 71 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 75 | 75 | 75
Exhaust hood - Education - Primary School
Type of Hood | Max Exhaust Flow Rate (cfm/ft) | Hood Length (ft) | Hood Exhaust Rate (cfm) | Note
- | - | - | -

## Raw_outdoorairflowrate (hidden)
Zone Type | Floor Area (ft2) | cfm/person | cfm/ft2
Classroom_class | 15748.57 | 0 | 0.38
Dining_fast | 3754.31 | 0 | 0.5
Gym | 3747.29 | 0 | 0.5
Kitchen | 1750.76 | 0 | 0.15
Plenum | 15748.57 | 0 | 0

## Raw_oacontroller (hidden)
Climate Zone | Vintage | Economizer Maximum Limit Dry-Bulb Temperature (F)
CZ01 | Existing | 75
CZ02 | Existing | 73
CZ03 | Existing | 75
CZ04 | Existing | 73
CZ05 | Existing | 75
CZ06 | Existing | 71
CZ07 | Existing | 69
CZ08 | Existing | 71
CZ09 | Existing | 71
CZ10 | Existing | 73
CZ11 | Existing | 75
CZ12 | Existing | 75
CZ13 | Existing | 75
CZ14 | Existing | 75
CZ15 | Existing | 75
CZ16 | Existing | 75
CZ01 | New Construction | 75
CZ02 | New Construction | 73
CZ03 | New Construction | 75
CZ04 | New Construction | 73
CZ05 | New Construction | 75
CZ06 | New Construction | 71
CZ07 | New Construction | 69
CZ08 | New Construction | 71
CZ09 | New Construction | 71
CZ10 | New Construction | 73
CZ11 | New Construction | 75
CZ12 | New Construction | 75
CZ13 | New Construction | 75
CZ14 | New Construction | 75
CZ15 | New Construction | 75
CZ16 | New Construction | 75

## Water Heater
Water Heater - Education - Primary School
Vintage | Fuel type | Burner Efficiency | Maximum Heater Capacity (Btu/hr) | Tank Volume (gallon) | Tank Loss |  | Notes
[5 empty] | Off Cycle (W/K) | On Cycle (W/K)
Existing | Gas | 0.8 | 305926.16 | 64.16 | 1.6282 | 1.6282
New Construction | Gas | 0.8 | 305926.16 | 64.16 | 1.6282 | 1.6282
Peak Hot Water Consumption - Education - Primary School
Space | Floor Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Notes
CLASSROOM G.E1 | 5751.45 | 25 | 2.0705 | 51.763 | 0.86272
CLASSROOM G.NNE2 | 3321.4 | 25 | 1.1957 | 29.8925 | 0.49821
CLASSROOM G.SSE3 | 3321.39 | 25 | 1.1957 | 29.8925 | 0.49821
CLASSROOM G.W4 | 3354.33 | 25 | 1.2076 | 30.1889 | 0.50315
DINING G.SSW1 | 3754.31 | 33.33 | 2.3897 | 79.6484 | 1.3275
GYMNASIUM G.N2 | 3747.29 | 33.33 | 0.40475 | 13.4902 | 0.22484
KITCHEN G.E3 | 1750.76 | 2.5 | 2.0239 | 5.0597 | 0.084328
PLENUM G.E5 | 5751.45 | 0 | 0 | 0 | 0
PLENUM G.NNE6 | 3321.4 | 0 | 0 | 0 | 0
PLENUM G.SSE7 | 3321.39 | 0 | 0 | 0 | 0
PLENUM G.W8 | 3354.33 | 0 | 0 | 0 | 0
Total (11 Space)

## Raw_waterheater (hidden)
Vintage | Burner Efficiency | Maximum Heater Capacity (Btu/h) | Tank Volume (ft3) | Tank Loss_Off Cycle (W/K) | Tank Loss_On Cycle (W/K)
Existing | 0.8 | 305926.16 | 64.16 | 1.6282 | 1.6282
New Construction | 0.8 | 305926.16 | 64.16 | 1.6282 | 1.6282

## Raw_dhwpeakflowbyzone (hidden)
Space | Peak hot water usage (gal/hr) | Zone Name
Classroom G.E1 | 51.763 | CLASSROOM G.E1
Classroom G.NNE2 | 29.8925 | CLASSROOM G.NNE2
Classroom G.SSE3 | 29.8925 | CLASSROOM G.SSE3
Classroom G.W4 | 30.1889 | CLASSROOM G.W4
Dining G.SSW1 | 79.6484 | DINING G.SSW1
Gymnasium G.N2 | 13.4902 | GYMNASIUM G.N2
Kitchen G.E3 | 5.0597 | KITCHEN G.E3

## Interior Lights
Interior Lighting - Education - Primary School
Vintage | Method | Zone type | Floor area (ft²) | Lighting Power Density (Watts/ft²) | Additional Lighting Power for Portable Lighting (Watts/ft²) | Technology | Notes
Existing | Space by space | Classroom_class | 15748.57 | 1.313 | NA | NA
Existing | Space by space | Dining_fast | 3754.31 | 1.2136 | NA | NA
Existing | Space by space | Gym | 3747.29 | 0.98463 | NA | NA
Existing | Space by space | Kitchen | 1750.76 | 1.6492 | NA | NA
Existing | Space by space | Plenum | 15748.57 | 0 | NA | NA
New Construction | Space by space | Classroom_class | 15748.57 | 0.59992 | NA | NA
New Construction | Space by space | Dining_fast | 3754.31 | 0.44995 | NA | NA
New Construction | Space by space | Gym | 3747.29 | 0.49992 | NA | NA
New Construction | Space by space | Kitchen | 1750.76 | 0.94987 | NA | NA
New Construction | Space by space | Plenum | 15748.57 | 0 | NA | NA

## Ext Lighting
Exterior Lighting - Education - Primary School
Vintage | Non-Motion Controlled Luminaires (W) | Motion-Controlled Luminaires (W) | Total (W) | Notes
Existing | NA | NA | NA
New Consturction | NA | NA | NA

## Raw_interiorlights (hidden)
Vintage | Zone Type | Floor Area (ft2) | Lighting Power Density(W/ft2)
Existing | Classroom_class | 15748.57 | 1.313
Existing | Dining_fast | 3754.31 | 1.2136
Existing | Gym | 3747.29 | 0.98463
Existing | Kitchen | 1750.76 | 1.6492
Existing | Plenum | 15748.57 | 0
New Construction | Classroom_class | 15748.57 | 0.59992
New Construction | Dining_fast | 3754.31 | 0.44995
New Construction | Gym | 3747.29 | 0.49992
New Construction | Kitchen | 1750.76 | 0.94987
New Construction | Plenum | 15748.57 | 0

## Equipment
Equipment - Education - Primary School
Zone Type | Floor Area (ft²) | Plug Load Intensity (W/ft²) | Gas Power Density (Btu/hr-ft²)
Classroom_class | 15748.57 | 0.99987 | 0
Dining_fast | 3754.31 | 0.74991 | 0
Gym | 3747.29 | 0.49992 | 0
Kitchen | 1750.76 | 7.7581 | 17.5354
Plenum | 15748.57 | 0 | 0
Refrigeration - Education - Primary School
Refrigeration System Name | Condenser Fan Power | Refrigeration System Working Fluid | Condenser Type
Elevator - Education - Primary School
Vintage | No. of Elevators | Cab Lighting Power Limit | Lighting Shutoff | Cab Fan Control | Fan Power Limit | Regenerative Drive Threshold | Design load (W) | Note
Existing | - | - | - | - | - | - | -
New Construction | - | - | - | - | - | - | -

## Raw_equipment (hidden)
Vintage | Zone Type | Floor Area (ft2) | Plug Load Intensity (W/ft2)
Existing | Classroom_class | 15748.57 | 0.99987
Existing | Dining_fast | 3754.31 | 0.74991
Existing | Gym | 3747.29 | 0.49992
Existing | Kitchen | 1750.76 | 7.7581
Existing | Plenum | 15748.57 | 0
New Construction | Classroom_class | 15748.57 | 0.99987
New Construction | Dining_fast | 3754.31 | 0.74991
New Construction | Gym | 3747.29 | 0.49992
New Construction | Kitchen | 1750.76 | 7.7581
New Construction | Plenum | 15748.57 | 0

## Raw_gasequipment (hidden)
Vintage | Zone Name | Gas Loads (Btu/h-ft2) | Zone Type
Existing | Kitchen G.E3 | 17.5354 | Kitchen
New Construction | Kitchen G.E3 | 17.5354 | Kitchen

## Raw_refrigerationsystem (hidden)
Vintage | Refrigeration System Name | Condenser Fan Power | Working fluid | Condenser Type
No refrigeration system was found

## Schedules
Schedule by Hour - Education - Primary School
Schedule Identifier | Space type | Type | Notes | Hour
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Cooling Setpoint Schedule | Kitchen | AllOtherDays | Cooling/Heating setpoints are in °F; others are intensity (0–100%) | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Cooling Setpoint Schedule | Kitchen | Saturdays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Cooling Setpoint Schedule | Kitchen | Weekdays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | Kitchen | AllOtherDays |  | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
DHW Sch | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
DHW Sch | Kitchen | Weekdays |  | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
Elec Equip Sch | Kitchen | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | Kitchen | AllOtherDays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Elec Equip Sch | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Elec Equip Sch | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Heating Setpoint Schedule | Kitchen | AllOtherDays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Heating Setpoint Schedule | Kitchen | Saturdays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Heating Setpoint Schedule | Kitchen | Weekdays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | Kitchen | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Kitchen | AllOtherDays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
Lighting Schedule | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Lighting Schedule | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
OA Schedule | Kitchen | AllOtherDays |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OA Schedule | Kitchen | Saturdays |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OA Schedule | Kitchen | Weekdays |  | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Occupant Sch | Kitchen | AllOtherDays |  | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Occupant Sch | Kitchen | Saturdays |  | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
Occupant Sch | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Infiltration Schedule | Plenum | AllDays | bar: Hour 1 to Hour 24
Cooling Setpoint Schedule | School | AllOtherDays (Through 1/11) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 4/3) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 4/12) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 5/22) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 5/31) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 8/7) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 8/16) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 12/11) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 12/31) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Saturdays (Through 4/3) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Saturdays (Through 5/22) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Saturdays (Through 8/7) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Saturdays (Through 12/11) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Weekdays (Through 4/3) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Weekdays (Through 5/22) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Weekdays (Through 8/7) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Weekdays (Through 12/11) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
DHW Sch | School | AllOtherDays (Through 1/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | School | AllOtherDays (Through 4/3) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | AllOtherDays (Through 4/12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | School | AllOtherDays (Through 5/22) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | AllOtherDays (Through 5/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | School | AllOtherDays (Through 8/7) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | AllOtherDays (Through 8/16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | School | AllOtherDays (Through 12/11) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | AllOtherDays (Through 12/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | School | Saturdays (Through 4/3) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | Saturdays (Through 5/22) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | Saturdays (Through 8/7) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | Saturdays (Through 12/11) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | Weekdays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
DHW Sch | School | Weekdays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
DHW Sch | School | Weekdays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
DHW Sch | School | Weekdays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
Elec Equip Sch | School | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | School | AllOtherDays (Through 1/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | School | AllOtherDays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | AllOtherDays (Through 4/12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | School | AllOtherDays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | AllOtherDays (Through 5/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | School | AllOtherDays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | AllOtherDays (Through 8/16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | School | AllOtherDays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | AllOtherDays (Through 12/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | School | Saturdays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | Saturdays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | Saturdays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | Saturdays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | Weekdays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Elec Equip Sch | School | Weekdays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Elec Equip Sch | School | Weekdays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Elec Equip Sch | School | Weekdays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Heating Setpoint Schedule | School | AllOtherDays (Through 1/11) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 4/3) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 4/12) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 5/22) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 5/31) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 8/7) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 8/16) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 12/11) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 12/31) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | Saturdays (Through 4/3) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | Saturdays (Through 5/22) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | Saturdays (Through 8/7) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | Saturdays (Through 12/11) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | Weekdays (Through 4/3) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
Heating Setpoint Schedule | School | Weekdays (Through 5/22) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
Heating Setpoint Schedule | School | Weekdays (Through 8/7) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
Heating Setpoint Schedule | School | Weekdays (Through 12/11) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
Infiltration Schedule | School | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | School | AllOtherDays (Through 1/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting Schedule | School | AllOtherDays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | AllOtherDays (Through 4/12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting Schedule | School | AllOtherDays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | AllOtherDays (Through 5/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting Schedule | School | AllOtherDays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | AllOtherDays (Through 8/16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting Schedule | School | AllOtherDays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | AllOtherDays (Through 12/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting Schedule | School | Saturdays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | Saturdays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | Saturdays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | Saturdays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | Weekdays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Lighting Schedule | School | Weekdays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Lighting Schedule | School | Weekdays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Lighting Schedule | School | Weekdays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
OA Schedule | School | AllOtherDays (Through 1/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 4/12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 5/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 8/16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 12/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | Saturdays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | Saturdays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | Saturdays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | Saturdays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | Weekdays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OA Schedule | School | Weekdays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OA Schedule | School | Weekdays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OA Schedule | School | Weekdays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 1/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 4/12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 5/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 8/16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 12/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | Saturdays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | Saturdays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | Saturdays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | Saturdays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | Weekdays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
Occupant Sch | School | Weekdays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
Occupant Sch | School | Weekdays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
Occupant Sch | School | Weekdays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0

## Schedule_Figures
Schedule Figures (linked to Schedules tab)

## Raw_schedule (hidden)
Schedule Identifier | Schedule Name | Type | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Kitchen | Cooling Setpoint Schedule | AllOtherDays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | Cooling Setpoint Schedule | Saturdays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | Cooling Setpoint Schedule | Weekdays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | DHW Sch | AllOtherDays | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Kitchen | DHW Sch | Saturdays | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
Kitchen | DHW Sch | Weekdays | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
Kitchen | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Elec Equip Sch | AllOtherDays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Kitchen | Elec Equip Sch | Saturdays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Kitchen | Elec Equip Sch | Weekdays | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Kitchen | Heating Setpoint Schedule | AllOtherDays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Heating Setpoint Schedule | Saturdays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Heating Setpoint Schedule | Weekdays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Lighting Schedule | AllOtherDays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
Kitchen | Lighting Schedule | Saturdays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Kitchen | Lighting Schedule | Weekdays | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Kitchen | OA Schedule | AllOtherDays | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | OA Schedule | Saturdays | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | OA Schedule | Weekdays | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Occupant Sch | AllOtherDays | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Kitchen | Occupant Sch | Saturdays | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
Kitchen | Occupant Sch | Weekdays | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Plenum | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
School | Cooling Setpoint Schedule | AllOtherDays (Through 1/11) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 4/3) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 4/12) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 5/22) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 5/31) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 8/7) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 8/16) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 12/11) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 12/31) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Saturdays (Through 4/3) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Saturdays (Through 5/22) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Saturdays (Through 8/7) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Saturdays (Through 12/11) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Weekdays (Through 4/3) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Weekdays (Through 5/22) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Weekdays (Through 8/7) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Weekdays (Through 12/11) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
School | DHW Sch | AllOtherDays (Through 1/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | DHW Sch | AllOtherDays (Through 4/3) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | AllOtherDays (Through 4/12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | DHW Sch | AllOtherDays (Through 5/22) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | AllOtherDays (Through 5/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | DHW Sch | AllOtherDays (Through 8/7) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | AllOtherDays (Through 8/16) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | DHW Sch | AllOtherDays (Through 12/11) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | AllOtherDays (Through 12/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | DHW Sch | Saturdays (Through 4/3) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | Saturdays (Through 5/22) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | Saturdays (Through 8/7) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | Saturdays (Through 12/11) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | Weekdays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
School | DHW Sch | Weekdays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
School | DHW Sch | Weekdays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
School | DHW Sch | Weekdays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
School | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
School | Elec Equip Sch | AllOtherDays (Through 1/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Elec Equip Sch | AllOtherDays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | AllOtherDays (Through 4/12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Elec Equip Sch | AllOtherDays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | AllOtherDays (Through 5/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Elec Equip Sch | AllOtherDays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | AllOtherDays (Through 8/16) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Elec Equip Sch | AllOtherDays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | AllOtherDays (Through 12/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Elec Equip Sch | Saturdays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | Saturdays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | Saturdays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | Saturdays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | Weekdays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Elec Equip Sch | Weekdays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Elec Equip Sch | Weekdays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Elec Equip Sch | Weekdays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Heating Setpoint Schedule | AllOtherDays (Through 1/11) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 4/3) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 4/12) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 5/22) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 5/31) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 8/7) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 8/16) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 12/11) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 12/31) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | Saturdays (Through 4/3) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | Saturdays (Through 5/22) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | Saturdays (Through 8/7) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | Saturdays (Through 12/11) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | Weekdays (Through 4/3) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
School | Heating Setpoint Schedule | Weekdays (Through 5/22) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
School | Heating Setpoint Schedule | Weekdays (Through 8/7) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
School | Heating Setpoint Schedule | Weekdays (Through 12/11) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
School | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
School | Lighting Schedule | AllOtherDays (Through 1/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Lighting Schedule | AllOtherDays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | AllOtherDays (Through 4/12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Lighting Schedule | AllOtherDays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | AllOtherDays (Through 5/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Lighting Schedule | AllOtherDays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | AllOtherDays (Through 8/16) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Lighting Schedule | AllOtherDays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | AllOtherDays (Through 12/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Lighting Schedule | Saturdays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | Saturdays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | Saturdays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | Saturdays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | Weekdays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Lighting Schedule | Weekdays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Lighting Schedule | Weekdays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Lighting Schedule | Weekdays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | OA Schedule | AllOtherDays (Through 1/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 4/12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 5/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 8/16) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 12/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | Saturdays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | Saturdays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | Saturdays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | Saturdays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | Weekdays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
School | OA Schedule | Weekdays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
School | OA Schedule | Weekdays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
School | OA Schedule | Weekdays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 1/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 4/12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 5/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 8/16) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 12/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | Saturdays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | Saturdays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | Saturdays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | Saturdays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | Weekdays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
School | Occupant Sch | Weekdays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
School | Occupant Sch | Weekdays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
School | Occupant Sch | Weekdays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0

## Energy Usage
Energy Consumption - Education - Primary School
Climate Zone | HVAC Type | Vintage | Total Floorspace (Excluding Plenums and Crawl Space) (ft²) | Annual Electricity Intensity (kBtu/ft²) | Annual Gas Intensity (kBtu/ft²) | Notes
CZ01 | cAVVG | Existing | 40749.5 | 16.2193 | 18.3249
CZ01 | cAVVG | New Construction | 40749.5 | 13.0878 | 18.5709
CZ01 | cDXGF | Existing | 40749.5 | 18.8987 | 15.3758
CZ01 | cDXGF | New Construction | 40749.5 | 14.3915 | 16.4242
CZ01 | cDXHP | Existing | 40749.5 | 19.986 | 10.8769
CZ01 | cDXHP | New Construction | 40749.5 | 15.7164 | 10.8692
CZ01 | cDXOH | Existing | 40749.5 | 18.9209 | 10.8778
CZ01 | cDXOH | New Construction | 40749.5 | 14.3799 | 10.8713
CZ01 | cPVVG | Existing | 40749.5 | 15.5797 | 17.4666
CZ01 | cPVVG | New Construction | 40749.5 | 12.1264 | 18.0767
CZ02 | cAVVG | Existing | 40749.5 | 20.1226 | 14.7111
CZ02 | cAVVG | New Construction | 40749.5 | 15.8137 | 14.7957
CZ02 | cDXGF | Existing | 40749.5 | 21.8304 | 12.7539
CZ02 | cDXGF | New Construction | 40749.5 | 16.3555 | 13.1587
CZ02 | cDXHP | Existing | 40749.5 | 22.4682 | 10.275
CZ02 | cDXHP | New Construction | 40749.5 | 17.0795 | 10.2669
CZ02 | cDXOH | Existing | 40749.5 | 21.8243 | 10.2754
CZ02 | cDXOH | New Construction | 40749.5 | 16.3024 | 10.2683
CZ02 | cPVVG | Existing | 40749.5 | 18.3583 | 13.9192
CZ02 | cPVVG | New Construction | 40749.5 | 14.0219 | 14.0981
CZ03 | cAVVG | Existing | 40749.5 | 17.9863 | 13.2569
CZ03 | cAVVG | New Construction | 40749.5 | 14.2423 | 13.4334
CZ03 | cDXGF | Existing | 40749.5 | 20.6357 | 11.7055
CZ03 | cDXGF | New Construction | 40749.5 | 15.6064 | 12.2416
CZ03 | cDXHP | Existing | 40749.5 | 20.9718 | 10.2539
CZ03 | cDXHP | New Construction | 40749.5 | 16.0726 | 10.2458
CZ03 | cDXOH | Existing | 40749.5 | 20.6267 | 10.2548
CZ03 | cDXOH | New Construction | 40749.5 | 15.5743 | 10.247
CZ03 | cPVVG | Existing | 40749.5 | 17.3284 | 12.5817
CZ03 | cPVVG | New Construction | 40749.5 | 13.2712 | 13.0727
CZ04 | cAVVG | Existing | 40749.5 | 20.177 | 12.8236
CZ04 | cAVVG | New Construction | 40749.5 | 15.7397 | 12.8519
CZ04 | cDXGF | Existing | 40749.5 | 22.4468 | 11.2953
CZ04 | cDXGF | New Construction | 40749.5 | 16.7505 | 11.6861
CZ04 | cDXHP | Existing | 40749.5 | 22.7458 | 10.018
CZ04 | cDXHP | New Construction | 40749.5 | 17.1486 | 10.0086
CZ04 | cDXOH | Existing | 40749.5 | 22.4335 | 10.0187
CZ04 | cDXOH | New Construction | 40749.5 | 16.7101 | 10.0094
CZ04 | cPVVG | Existing | 40749.5 | 19.0186 | 12.0837
CZ04 | cPVVG | New Construction | 40749.5 | 14.4417 | 12.3903
CZ05 | cAVVG | Existing | 40749.5 | 18.3377 | 13.2018
CZ05 | cAVVG | New Construction | 40749.5 | 14.4656 | 13.4227
CZ05 | cDXGF | Existing | 40749.5 | 20.9933 | 11.5693
CZ05 | cDXGF | New Construction | 40749.5 | 15.8793 | 12.1397
CZ05 | cDXHP | Existing | 40749.5 | 21.3092 | 10.2555
CZ05 | cDXHP | New Construction | 40749.5 | 16.3333 | 10.2433
CZ05 | cDXOH | Existing | 40749.5 | 20.9743 | 10.2552
CZ05 | cDXOH | New Construction | 40749.5 | 15.8223 | 10.2442
CZ05 | cPVVG | Existing | 40749.5 | 17.779 | 12.3262
CZ05 | cPVVG | New Construction | 40749.5 | 13.586 | 12.9028
CZ06 | cAVVG | Existing | 40749.5 | 20.9678 | 10.6825
CZ06 | cAVVG | New Construction | 40749.5 | 16.4516 | 10.9796
CZ06 | cDXGF | Existing | 40749.5 | 22.639 | 10.0107
CZ06 | cDXGF | New Construction | 40749.5 | 17.175 | 10.2024
CZ06 | cDXHP | Existing | 40749.5 | 22.5835 | 9.7289
CZ06 | cDXHP | New Construction | 40749.5 | 17.1895 | 9.7179
CZ06 | cDXOH | Existing | 40749.5 | 22.6335 | 9.7289
CZ06 | cDXOH | New Construction | 40749.5 | 17.1636 | 9.7192
CZ06 | cPVVG | Existing | 40749.5 | 19.4984 | 10.278
CZ06 | cPVVG | New Construction | 40749.5 | 14.8411 | 10.558
CZ07 | cAVVG | Existing | 40749.5 | 21.3919 | 10.7079
CZ07 | cAVVG | New Construction | 40749.5 | 16.8179 | 11.004
CZ07 | cDXGF | Existing | 40749.5 | 22.9161 | 9.9209
CZ07 | cDXGF | New Construction | 40749.5 | 17.3712 | 10.1036
CZ07 | cDXHP | Existing | 40749.5 | 22.8991 | 9.6448
CZ07 | cDXHP | New Construction | 40749.5 | 17.421 | 9.6342
CZ07 | cDXOH | Existing | 40749.5 | 22.9118 | 9.6447
CZ07 | cDXOH | New Construction | 40749.5 | 17.3604 | 9.636
CZ07 | cPVVG | Existing | 40749.5 | 19.7 | 10.177
CZ07 | cPVVG | New Construction | 40749.5 | 14.9898 | 10.4371
CZ08 | cAVVG | Existing | 40749.5 | 22.1673 | 11.0085
CZ08 | cAVVG | New Construction | 40749.5 | 17.3249 | 11.2466
CZ08 | cDXGF | Existing | 40749.5 | 23.773 | 10.0569
CZ08 | cDXGF | New Construction | 40749.5 | 17.9404 | 10.2993
CZ08 | cDXHP | Existing | 40749.5 | 23.8296 | 9.6348
CZ08 | cDXHP | New Construction | 40749.5 | 18.0754 | 9.6263
CZ08 | cDXOH | Existing | 40749.5 | 23.7653 | 9.635
CZ08 | cDXOH | New Construction | 40749.5 | 17.9215 | 9.6269
CZ08 | cPVVG | Existing | 40749.5 | 20.3906 | 10.3913
CZ08 | cPVVG | New Construction | 40749.5 | 15.5313 | 10.7154
CZ09 | cAVVG | Existing | 40749.5 | 23.4416 | 10.7416
CZ09 | cAVVG | New Construction | 40749.5 | 17.7826 | 10.9146
CZ09 | cDXGF | Existing | 40749.5 | 24.8065 | 9.8594
CZ09 | cDXGF | New Construction | 40749.5 | 18.0633 | 9.9939
CZ09 | cDXHP | Existing | 40749.5 | 24.8206 | 9.5518
CZ09 | cDXHP | New Construction | 40749.5 | 18.1359 | 9.5435
CZ09 | cDXOH | Existing | 40749.5 | 24.7993 | 9.5514
CZ09 | cDXOH | New Construction | 40749.5 | 18.0454 | 9.5401
CZ09 | cPVVG | Existing | 40749.5 | 21.2454 | 10.1476
CZ09 | cPVVG | New Construction | 40749.5 | 15.8071 | 10.301
CZ10 | cAVVG | Existing | 40749.5 | 24.3155 | 11.7201
CZ10 | cAVVG | New Construction | 40749.5 | 18.9334 | 11.6895
CZ10 | cDXGF | Existing | 40749.5 | 25.5253 | 10.4388
CZ10 | cDXGF | New Construction | 40749.5 | 19.2398 | 10.6789
CZ10 | cDXHP | Existing | 40749.5 | 25.7818 | 9.4845
CZ10 | cDXHP | New Construction | 40749.5 | 19.5619 | 9.4777
CZ10 | cDXOH | Existing | 40749.5 | 25.5049 | 9.4835
CZ10 | cDXOH | New Construction | 40749.5 | 19.1953 | 9.4729
CZ10 | cPVVG | Existing | 40749.5 | 22.0119 | 10.955
CZ10 | cPVVG | New Construction | 40749.5 | 16.9126 | 11.1679
CZ11 | cAVVG | Existing | 40749.5 | 25.2048 | 14.3651
CZ11 | cAVVG | New Construction | 40749.5 | 19.2933 | 13.7314
CZ11 | cDXGF | Existing | 40749.5 | 26.7987 | 12.062
CZ11 | cDXGF | New Construction | 40749.5 | 19.5192 | 12.3694
CZ11 | cDXHP | Existing | 40749.5 | 27.4613 | 9.6052
CZ11 | cDXHP | New Construction | 40749.5 | 20.2607 | 9.597
CZ11 | cDXOH | Existing | 40749.5 | 26.8197 | 9.6051
CZ11 | cDXOH | New Construction | 40749.5 | 19.4973 | 9.5958
CZ11 | cPVVG | Existing | 40749.5 | 22.8347 | 13.2501
CZ11 | cPVVG | New Construction | 40749.5 | 17.1813 | 13.2803
CZ12 | cAVVG | Existing | 40749.5 | 24.0868 | 13.6849
CZ12 | cAVVG | New Construction | 40749.5 | 18.6142 | 13.6644
CZ12 | cDXGF | Existing | 40749.5 | 25.0362 | 11.9432
CZ12 | cDXGF | New Construction | 40749.5 | 18.5121 | 12.2792
CZ12 | cDXHP | Existing | 40749.5 | 25.6074 | 9.7873
CZ12 | cDXHP | New Construction | 40749.5 | 19.1698 | 9.7774
CZ12 | cDXOH | Existing | 40749.5 | 25.0549 | 9.7873
CZ12 | cDXOH | New Construction | 40749.5 | 18.4808 | 9.7783
CZ12 | cPVVG | Existing | 40749.5 | 21.4178 | 12.9588
CZ12 | cPVVG | New Construction | 40749.5 | 16.2445 | 13.0639
CZ13 | cAVVG | Existing | 40749.5 | 26.4804 | 12.8045
CZ13 | cAVVG | New Construction | 40749.5 | 20.2173 | 12.5673
CZ13 | cDXGF | Existing | 40749.5 | 27.6108 | 11.085
CZ13 | cDXGF | New Construction | 40749.5 | 20.15 | 11.4312
CZ13 | cDXHP | Existing | 40749.5 | 28.0468 | 9.4274
CZ13 | cDXHP | New Construction | 40749.5 | 20.6772 | 9.42
CZ13 | cDXOH | Existing | 40749.5 | 27.6237 | 9.4273
CZ13 | cDXOH | New Construction | 40749.5 | 20.1305 | 9.4161
CZ13 | cPVVG | Existing | 40749.5 | 23.7053 | 11.9447
CZ13 | cPVVG | New Construction | 40749.5 | 17.8365 | 12.1302
CZ14 | cAVVG | Existing | 40749.5 | 28.6735 | 11.675
CZ14 | cAVVG | New Construction | 40749.5 | 21.9554 | 11.5266
CZ14 | cDXGF | Existing | 40749.5 | 30.0522 | 10.0619
CZ14 | cDXGF | New Construction | 40749.5 | 22.0135 | 10.3376
CZ14 | cDXHP | Existing | 40749.5 | 30.3286 | 9.1176
CZ14 | cDXHP | New Construction | 40749.5 | 22.3673 | 9.1075
CZ14 | cDXOH | Existing | 40749.5 | 30.0426 | 9.1183
CZ14 | cDXOH | New Construction | 40749.5 | 21.9811 | 9.108
CZ14 | cPVVG | Existing | 40749.5 | 25.8453 | 10.6744
CZ14 | cPVVG | New Construction | 40749.5 | 19.571 | 10.9056
CZ15 | cAVVG | Existing | 40749.5 | 33.5811 | 9.7802
CZ15 | cAVVG | New Construction | 40749.5 | 26.0902 | 9.9596
CZ15 | cDXGF | Existing | 40749.5 | 33.0202 | 8.8133
CZ15 | cDXGF | New Construction | 40749.5 | 24.2039 | 8.9411
CZ15 | cDXHP | Existing | 40749.5 | 33.1007 | 8.4946
CZ15 | cDXHP | New Construction | 40749.5 | 24.3323 | 8.4844
CZ15 | cDXOH | Existing | 40749.5 | 33.0088 | 8.4946
CZ15 | cDXOH | New Construction | 40749.5 | 24.1729 | 8.4849
CZ15 | cPVVG | Existing | 40749.5 | 29.1877 | 9.0331
CZ15 | cPVVG | New Construction | 40749.5 | 22.1618 | 9.1735
CZ16 | cAVVG | Existing | 40749.5 | 24.8102 | 15.9109
CZ16 | cAVVG | New Construction | 40749.5 | 19.2548 | 15.5388
CZ16 | cDXGF | Existing | 40749.5 | 26.7508 | 13.4388
CZ16 | cDXGF | New Construction | 40749.5 | 19.8477 | 13.763
CZ16 | cDXHP | Existing | 40749.5 | 27.8675 | 10.1347
CZ16 | cDXHP | New Construction | 40749.5 | 20.981 | 10.1234
CZ16 | cDXOH | Existing | 40749.5 | 26.8732 | 10.1348
CZ16 | cDXOH | New Construction | 40749.5 | 19.8777 | 10.1271
CZ16 | cPVVG | Existing | 40749.5 | 22.5126 | 14.9468
CZ16 | cPVVG | New Construction | 40749.5 | 17.1245 | 14.912

## Energy Usage_Figures
Energy Figures (from 'Energy Usage' Tab)
cAVVG ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cAVVG ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 16.2193 | 13.0878 | CZ01 | 18.3249 | 18.5709
CZ02 | 20.1226 | 15.8137 | CZ02 | 14.7111 | 14.7957
CZ03 | 17.9863 | 14.2423 | CZ03 | 13.2569 | 13.4334
CZ04 | 20.177 | 15.7397 | CZ04 | 12.8236 | 12.8519
CZ05 | 18.3377 | 14.4656 | CZ05 | 13.2018 | 13.4227
CZ06 | 20.9678 | 16.4516 | CZ06 | 10.6825 | 10.9796
CZ07 | 21.3919 | 16.8179 | CZ07 | 10.7079 | 11.004
CZ08 | 22.1673 | 17.3249 | CZ08 | 11.0085 | 11.2466
CZ09 | 23.4416 | 17.7826 | CZ09 | 10.7416 | 10.9146
CZ10 | 24.3155 | 18.9334 | CZ10 | 11.7201 | 11.6895
CZ11 | 25.2048 | 19.2933 | CZ11 | 14.3651 | 13.7314
CZ12 | 24.0868 | 18.6142 | CZ12 | 13.6849 | 13.6644
CZ13 | 26.4804 | 20.2173 | CZ13 | 12.8045 | 12.5673
CZ14 | 28.6735 | 21.9554 | CZ14 | 11.675 | 11.5266
CZ15 | 33.5811 | 26.0902 | CZ15 | 9.7802 | 9.9596
CZ16 | 24.8102 | 19.2548 | CZ16 | 15.9109 | 15.5388
cDXGF ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXGF ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 18.8987 | 14.3915 | CZ01 | 15.3758 | 16.4242
CZ02 | 21.8304 | 16.3555 | CZ02 | 12.7539 | 13.1587
CZ03 | 20.6357 | 15.6064 | CZ03 | 11.7055 | 12.2416
CZ04 | 22.4468 | 16.7505 | CZ04 | 11.2953 | 11.6861
CZ05 | 20.9933 | 15.8793 | CZ05 | 11.5693 | 12.1397
CZ06 | 22.639 | 17.175 | CZ06 | 10.0107 | 10.2024
CZ07 | 22.9161 | 17.3712 | CZ07 | 9.9209 | 10.1036
CZ08 | 23.773 | 17.9404 | CZ08 | 10.0569 | 10.2993
CZ09 | 24.8065 | 18.0633 | CZ09 | 9.8594 | 9.9939
CZ10 | 25.5253 | 19.2398 | CZ10 | 10.4388 | 10.6789
CZ11 | 26.7987 | 19.5192 | CZ11 | 12.062 | 12.3694
CZ12 | 25.0362 | 18.5121 | CZ12 | 11.9432 | 12.2792
CZ13 | 27.6108 | 20.15 | CZ13 | 11.085 | 11.4312
CZ14 | 30.0522 | 22.0135 | CZ14 | 10.0619 | 10.3376
CZ15 | 33.0202 | 24.2039 | CZ15 | 8.8133 | 8.9411
CZ16 | 26.7508 | 19.8477 | CZ16 | 13.4388 | 13.763
cDXHP ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXHP ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 19.986 | 15.7164 | CZ01 | 10.8769 | 10.8692
CZ02 | 22.4682 | 17.0795 | CZ02 | 10.275 | 10.2669
CZ03 | 20.9718 | 16.0726 | CZ03 | 10.2539 | 10.2458
CZ04 | 22.7458 | 17.1486 | CZ04 | 10.018 | 10.0086
CZ05 | 21.3092 | 16.3333 | CZ05 | 10.2555 | 10.2433
CZ06 | 22.5835 | 17.1895 | CZ06 | 9.7289 | 9.7179
CZ07 | 22.8991 | 17.421 | CZ07 | 9.6448 | 9.6342
CZ08 | 23.8296 | 18.0754 | CZ08 | 9.6348 | 9.6263
CZ09 | 24.8206 | 18.1359 | CZ09 | 9.5518 | 9.5435
CZ10 | 25.7818 | 19.5619 | CZ10 | 9.4845 | 9.4777
CZ11 | 27.4613 | 20.2607 | CZ11 | 9.6052 | 9.597
CZ12 | 25.6074 | 19.1698 | CZ12 | 9.7873 | 9.7774
CZ13 | 28.0468 | 20.6772 | CZ13 | 9.4274 | 9.42
CZ14 | 30.3286 | 22.3673 | CZ14 | 9.1176 | 9.1075
CZ15 | 33.1007 | 24.3323 | CZ15 | 8.4946 | 8.4844
CZ16 | 27.8675 | 20.981 | CZ16 | 10.1347 | 10.1234
cDXOH ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXOH ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 18.9209 | 14.3799 | CZ01 | 10.8778 | 10.8713
CZ02 | 21.8243 | 16.3024 | CZ02 | 10.2754 | 10.2683
CZ03 | 20.6267 | 15.5743 | CZ03 | 10.2548 | 10.247
CZ04 | 22.4335 | 16.7101 | CZ04 | 10.0187 | 10.0094
CZ05 | 20.9743 | 15.8223 | CZ05 | 10.2552 | 10.2442
CZ06 | 22.6335 | 17.1636 | CZ06 | 9.7289 | 9.7192
CZ07 | 22.9118 | 17.3604 | CZ07 | 9.6447 | 9.636
CZ08 | 23.7653 | 17.9215 | CZ08 | 9.635 | 9.6269
CZ09 | 24.7993 | 18.0454 | CZ09 | 9.5514 | 9.5401
CZ10 | 25.5049 | 19.1953 | CZ10 | 9.4835 | 9.4729
CZ11 | 26.8197 | 19.4973 | CZ11 | 9.6051 | 9.5958
CZ12 | 25.0549 | 18.4808 | CZ12 | 9.7873 | 9.7783
CZ13 | 27.6237 | 20.1305 | CZ13 | 9.4273 | 9.4161
CZ14 | 30.0426 | 21.9811 | CZ14 | 9.1183 | 9.108
CZ15 | 33.0088 | 24.1729 | CZ15 | 8.4946 | 8.4849
CZ16 | 26.8732 | 19.8777 | CZ16 | 10.1348 | 10.1271
cPVVG ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cPVVG ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 15.5797 | 12.1264 | CZ01 | 17.4666 | 18.0767
CZ02 | 18.3583 | 14.0219 | CZ02 | 13.9192 | 14.0981
CZ03 | 17.3284 | 13.2712 | CZ03 | 12.5817 | 13.0727
CZ04 | 19.0186 | 14.4417 | CZ04 | 12.0837 | 12.3903
CZ05 | 17.779 | 13.586 | CZ05 | 12.3262 | 12.9028
CZ06 | 19.4984 | 14.8411 | CZ06 | 10.278 | 10.558
CZ07 | 19.7 | 14.9898 | CZ07 | 10.177 | 10.4371
CZ08 | 20.3906 | 15.5313 | CZ08 | 10.3913 | 10.7154
CZ09 | 21.2454 | 15.8071 | CZ09 | 10.1476 | 10.301
CZ10 | 22.0119 | 16.9126 | CZ10 | 10.955 | 11.1679
CZ11 | 22.8347 | 17.1813 | CZ11 | 13.2501 | 13.2803
CZ12 | 21.4178 | 16.2445 | CZ12 | 12.9588 | 13.0639
CZ13 | 23.7053 | 17.8365 | CZ13 | 11.9447 | 12.1302
CZ14 | 25.8453 | 19.571 | CZ14 | 10.6744 | 10.9056
CZ15 | 29.1877 | 22.1618 | CZ15 | 9.0331 | 9.1735
CZ16 | 22.5126 | 17.1245 | CZ16 | 14.9468 | 14.912

## Raw_totalendusesannual (hidden)
Vintage | Climate Zone | HVAC System | Electricity (kBtu) | Natural Gas (kBtu)
Existing | CZ01 | cAVVG | 660929.61 | 746730.28
Existing | CZ02 | cAVVG | 819986.71 | 599469.48
Existing | CZ03 | cAVVG | 732933.11 | 540211.67
Existing | CZ04 | cAVVG | 822204.41 | 522557.28
Existing | CZ05 | cAVVG | 747250.1 | 537965.65
Existing | CZ06 | cAVVG | 854429.06 | 435304.85
Existing | CZ07 | cAVVG | 871710.39 | 436342.91
Existing | CZ08 | cAVVG | 903305.64 | 448592.05
Existing | CZ09 | cAVVG | 955234.63 | 437716.6
Existing | CZ10 | cAVVG | 990842.51 | 477589.53
Existing | CZ11 | cAVVG | 1027084.54 | 585371.45
Existing | CZ12 | cAVVG | 981527 | 557652.33
Existing | CZ13 | cAVVG | 1079063.04 | 521775.05
Existing | CZ14 | cAVVG | 1168429.27 | 475748.71
Existing | CZ15 | cAVVG | 1368413.97 | 398539.98
Existing | CZ16 | cAVVG | 1011003.27 | 648362.2
New Construction | CZ01 | cAVVG | 533320.61 | 756754.14
New Construction | CZ02 | cAVVG | 644398.64 | 602915.99
New Construction | CZ03 | cAVVG | 580367.95 | 547403.4
New Construction | CZ04 | cAVVG | 641383.81 | 523708.23
New Construction | CZ05 | cAVVG | 589465.54 | 546969.8
New Construction | CZ06 | cAVVG | 670396.48 | 447414.47
New Construction | CZ07 | cAVVG | 685319.43 | 448405.66
New Construction | CZ08 | cAVVG | 705980.71 | 458294.68
New Construction | CZ09 | cAVVG | 724633.29 | 444762.67
New Construction | CZ10 | cAVVG | 771527.18 | 476342.68
New Construction | CZ11 | cAVVG | 786193.17 | 559549.08
New Construction | CZ12 | cAVVG | 758518.76 | 556816.78
New Construction | CZ13 | cAVVG | 823845.85 | 512110.36
New Construction | CZ14 | cAVVG | 894670.45 | 469703.56
New Construction | CZ15 | cAVVG | 1063160.6 | 405846.71
New Construction | CZ16 | cAVVG | 784625.12 | 633198.93
Existing | CZ01 | cDXGF | 770111.68 | 626555.36
Existing | CZ02 | cDXGF | 889578.57 | 519716.18
Existing | CZ03 | cDXGF | 840895.39 | 476993.48
Existing | CZ04 | cDXGF | 914695.41 | 460278.28
Existing | CZ05 | cDXGF | 855467.14 | 471443.02
Existing | CZ06 | cDXGF | 922526.64 | 407931.73
Existing | CZ07 | cDXGF | 933821.18 | 404272.67
Existing | CZ08 | cDXGF | 968739.35 | 409814.04
Existing | CZ09 | cDXGF | 1010851.59 | 401767.53
Existing | CZ10 | cDXGF | 1040144.33 | 425375.78
Existing | CZ11 | cDXGF | 1092032.99 | 491521.85
Existing | CZ12 | cDXGF | 1020211.44 | 486679.15
Existing | CZ13 | cDXGF | 1125127.59 | 451709.61
Existing | CZ14 | cDXGF | 1224610.7 | 410015.87
Existing | CZ15 | cDXGF | 1345556.15 | 359137.94
Existing | CZ16 | cDXGF | 1090082.01 | 547624.65
New Construction | CZ01 | cDXGF | 586448.02 | 669279.67
New Construction | CZ02 | cDXGF | 666479.2 | 536210.03
New Construction | CZ03 | cDXGF | 635951.26 | 498840.38
New Construction | CZ04 | cDXGF | 682575.44 | 476202.52
New Construction | CZ05 | cDXGF | 647074.48 | 494686.96
New Construction | CZ06 | cDXGF | 699872.86 | 415744.51
New Construction | CZ07 | cDXGF | 707865.69 | 411715.83
New Construction | CZ08 | cDXGF | 731060.97 | 419691.21
New Construction | CZ09 | cDXGF | 736071.22 | 407244.94
New Construction | CZ10 | cDXGF | 784011.39 | 435160.18
New Construction | CZ11 | cDXGF | 795397.05 | 504048.85
New Construction | CZ12 | cDXGF | 754359.6 | 500372.29
New Construction | CZ13 | cDXGF | 821103.53 | 465813.81
New Construction | CZ14 | cDXGF | 897041.11 | 421253.12
New Construction | CZ15 | cDXGF | 986298.67 | 364345.45
New Construction | CZ16 | cDXGF | 808785.11 | 560833.42
Existing | CZ01 | cDXHP | 814418.68 | 443226.31
Existing | CZ02 | cDXHP | 915569.62 | 418702.45
Existing | CZ03 | cDXHP | 854591.86 | 417840.87
Existing | CZ04 | cDXHP | 926878.16 | 408229.82
Existing | CZ05 | cDXHP | 868338.17 | 417906.79
Existing | CZ06 | cDXHP | 920265.24 | 396447.79
Existing | CZ07 | cDXHP | 933128.67 | 393020.15
Existing | CZ08 | cDXHP | 971044.6 | 392614.68
Existing | CZ09 | cDXHP | 1011428.38 | 389231.34
Existing | CZ10 | cDXHP | 1050597.26 | 386490.28
Existing | CZ11 | cDXHP | 1119035.85 | 391408.37
Existing | CZ12 | cDXHP | 1043489.7 | 398827.32
Existing | CZ13 | cDXHP | 1142892.79 | 384163.48
Existing | CZ14 | cDXHP | 1235875.76 | 371538.89
Existing | CZ15 | cDXHP | 1348838.25 | 346150.46
Existing | CZ16 | cDXHP | 1135587.91 | 412982.85
New Construction | CZ01 | cDXHP | 640435.46 | 442914.82
New Construction | CZ02 | cDXHP | 695979.9 | 418372.77
New Construction | CZ03 | cDXHP | 654952.39 | 417511.18
New Construction | CZ04 | cDXHP | 698795.58 | 407844.04
New Construction | CZ05 | cDXHP | 665574.31 | 417410.96
New Construction | CZ06 | cDXHP | 700463.46 | 396001.34
New Construction | CZ07 | cDXHP | 709897.41 | 392588.97
New Construction | CZ08 | cDXHP | 736564.14 | 392266.02
New Construction | CZ09 | cDXHP | 739029.94 | 388891.27
New Construction | CZ10 | cDXHP | 797137.17 | 386211.87
New Construction | CZ11 | cDXHP | 825612.52 | 391071.49
New Construction | CZ12 | cDXHP | 781160.75 | 398425.39
New Construction | CZ13 | cDXHP | 842587.04 | 383862.31
New Construction | CZ14 | cDXHP | 911455.39 | 371125.18
New Construction | CZ15 | cDXHP | 991527.12 | 345733.32
New Construction | CZ16 | cDXHP | 854963.8 | 412523.51
Existing | CZ01 | cDXOH | 771018.23 | 443263.9
Existing | CZ02 | cDXOH | 889329.21 | 418718.67
Existing | CZ03 | cDXOH | 840528.57 | 417879.89
Existing | CZ04 | cDXOH | 914154.04 | 408257.84
Existing | CZ05 | cDXOH | 854692.16 | 417893.29
Existing | CZ06 | cDXOH | 922304.81 | 396447.77
Existing | CZ07 | cDXOH | 933644.84 | 393018.13
Existing | CZ08 | cDXOH | 968422.76 | 392622.52
Existing | CZ09 | cDXOH | 1010560.67 | 389215.55
Existing | CZ10 | cDXOH | 1039311.45 | 386448
Existing | CZ11 | cDXOH | 1092888.34 | 391403.55
Existing | CZ12 | cDXOH | 1020973.58 | 398828.63
Existing | CZ13 | cDXOH | 1125651.22 | 384158.38
Existing | CZ14 | cDXOH | 1224221.34 | 371565.22
Existing | CZ15 | cDXOH | 1345093.16 | 346149.09
Existing | CZ16 | cDXOH | 1095069.13 | 412988.18
New Construction | CZ01 | cDXOH | 585972.07 | 443001.7
New Construction | CZ02 | cDXOH | 664313.6 | 418427.61
New Construction | CZ03 | cDXOH | 634646.39 | 417560.28
New Construction | CZ04 | cDXOH | 680928.38 | 407878.83
New Construction | CZ05 | cDXOH | 644751.48 | 417444.86
New Construction | CZ06 | cDXOH | 699409.18 | 396051.51
New Construction | CZ07 | cDXOH | 707426.53 | 392661.27
New Construction | CZ08 | cDXOH | 730294 | 392292.44
New Construction | CZ09 | cDXOH | 735341.91 | 388752.62
New Construction | CZ10 | cDXOH | 782200.69 | 386016.18
New Construction | CZ11 | cDXOH | 794506.71 | 391025.07
New Construction | CZ12 | cDXOH | 753082.99 | 398462.41
New Construction | CZ13 | cDXOH | 820307.67 | 383699.75
New Construction | CZ14 | cDXOH | 895718.37 | 371147.21
New Construction | CZ15 | cDXOH | 985031.69 | 345753.43
New Construction | CZ16 | cDXOH | 810006.98 | 412674.28
Existing | CZ01 | cPVVG | 634865.56 | 711755.62
Existing | CZ02 | cPVVG | 748091.97 | 567201.5
Existing | CZ03 | cPVVG | 706121.93 | 512699.92
Existing | CZ04 | cPVVG | 774999.8 | 492406.51
Existing | CZ05 | cPVVG | 724483.58 | 502285.05
Existing | CZ06 | cPVVG | 794551.09 | 418822.18
Existing | CZ07 | cPVVG | 802763.57 | 414708.33
Existing | CZ08 | cPVVG | 830908.75 | 423438.43
Existing | CZ09 | cPVVG | 865739.45 | 413510.63
Existing | CZ10 | cPVVG | 896975.19 | 446410.3
Existing | CZ11 | cPVVG | 930502.55 | 539935.57
Existing | CZ12 | cPVVG | 872763.54 | 528064.12
Existing | CZ13 | cPVVG | 965980.07 | 486741
Existing | CZ14 | cPVVG | 1053183.16 | 434977.56
Existing | CZ15 | cPVVG | 1189385.9 | 368093.15
Existing | CZ16 | cPVVG | 917375.45 | 609076.48
New Construction | CZ01 | cPVVG | 494145.9 | 736616.2
New Construction | CZ02 | cPVVG | 571384.99 | 574489.77
New Construction | CZ03 | cPVVG | 540793.63 | 532707.27
New Construction | CZ04 | cPVVG | 588492.03 | 504899.56
New Construction | CZ05 | cPVVG | 553623.71 | 525782.33
New Construction | CZ06 | cPVVG | 604767.9 | 430233.29
New Construction | CZ07 | cPVVG | 610825.76 | 425307.81
New Construction | CZ08 | cPVVG | 632890.7 | 436646.61
New Construction | CZ09 | cPVVG | 644132.79 | 419760.64
New Construction | CZ10 | cPVVG | 689181.03 | 455087.82
New Construction | CZ11 | cPVVG | 700128.48 | 541166.37
New Construction | CZ12 | cPVVG | 661956.13 | 532346.42
New Construction | CZ13 | cPVVG | 726827.75 | 494299.3
New Construction | CZ14 | cPVVG | 797508.82 | 444396.13
New Construction | CZ15 | cPVVG | 903083.02 | 373816.75
New Construction | CZ16 | cPVVG | 697815.45 | 607658.51

## Energy Usage by End Use
Energy Consumption by End Use - Education - Primary School
Climate Zone | HVAC System | Vintage | End Use | Electricity (kBtu) | Natural Gas (kBtu) | Note
CZ01 | cAVVG | Existing | Heating | 0 | 303496.96
CZ01 | cAVVG | Existing | Cooling | 31162.39 | 0
CZ01 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ01 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ01 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ01 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ01 | cAVVG | Existing | Fans | 132265.77 | 0
CZ01 | cAVVG | Existing | Pumps | 559.71 | 0
CZ01 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ01 | cAVVG | Existing | Humidification | 0 | 0
CZ01 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ01 | cAVVG | Existing | Water Systems | 0 | 297531.38
CZ01 | cAVVG | Existing | Refrigeration | 0 | 0
CZ01 | cAVVG | Existing | Generators | 0 | 0
CZ01 | cAVVG | Existing | Total End Uses | 660929.61 | 746730.28
CZ02 | cAVVG | Existing | Heating | 0 | 180733.3
CZ02 | cAVVG | Existing | Cooling | 146394.15 | 0
CZ02 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ02 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ02 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ02 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ02 | cAVVG | Existing | Fans | 172938.16 | 0
CZ02 | cAVVG | Existing | Pumps | 3712.65 | 0
CZ02 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ02 | cAVVG | Existing | Humidification | 0 | 0
CZ02 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ02 | cAVVG | Existing | Water Systems | 0 | 273034.24
CZ02 | cAVVG | Existing | Refrigeration | 0 | 0
CZ02 | cAVVG | Existing | Generators | 0 | 0
CZ02 | cAVVG | Existing | Total End Uses | 819986.71 | 599469.48
CZ03 | cAVVG | Existing | Heating | 0 | 122305.83
CZ03 | cAVVG | Existing | Cooling | 101239.93 | 0
CZ03 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ03 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ03 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ03 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ03 | cAVVG | Existing | Fans | 131750.06 | 0
CZ03 | cAVVG | Existing | Pumps | 3001.37 | 0
CZ03 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ03 | cAVVG | Existing | Humidification | 0 | 0
CZ03 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ03 | cAVVG | Existing | Water Systems | 0 | 272203.9
CZ03 | cAVVG | Existing | Refrigeration | 0 | 0
CZ03 | cAVVG | Existing | Generators | 0 | 0
CZ03 | cAVVG | Existing | Total End Uses | 732933.11 | 540211.67
CZ04 | cAVVG | Existing | Heating | 0 | 114318.22
CZ04 | cAVVG | Existing | Cooling | 171867.77 | 0
CZ04 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ04 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ04 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ04 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ04 | cAVVG | Existing | Fans | 149141.1 | 0
CZ04 | cAVVG | Existing | Pumps | 4253.79 | 0
CZ04 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ04 | cAVVG | Existing | Humidification | 0 | 0
CZ04 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ04 | cAVVG | Existing | Water Systems | 0 | 262537.11
CZ04 | cAVVG | Existing | Refrigeration | 0 | 0
CZ04 | cAVVG | Existing | Generators | 0 | 0
CZ04 | cAVVG | Existing | Total End Uses | 822204.41 | 522557.28
CZ05 | cAVVG | Existing | Heating | 0 | 120049.64
CZ05 | cAVVG | Existing | Cooling | 117311.44 | 0
CZ05 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ05 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ05 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ05 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ05 | cAVVG | Existing | Fans | 129430.87 | 0
CZ05 | cAVVG | Existing | Pumps | 3566.04 | 0
CZ05 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ05 | cAVVG | Existing | Humidification | 0 | 0
CZ05 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ05 | cAVVG | Existing | Water Systems | 0 | 272214.06
CZ05 | cAVVG | Existing | Refrigeration | 0 | 0
CZ05 | cAVVG | Existing | Generators | 0 | 0
CZ05 | cAVVG | Existing | Total End Uses | 747250.1 | 537965.65
CZ06 | cAVVG | Existing | Heating | 0 | 38872.94
CZ06 | cAVVG | Existing | Cooling | 196185.64 | 0
CZ06 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ06 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ06 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ06 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ06 | cAVVG | Existing | Fans | 154517.95 | 0
CZ06 | cAVVG | Existing | Pumps | 6783.72 | 0
CZ06 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ06 | cAVVG | Existing | Humidification | 0 | 0
CZ06 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ06 | cAVVG | Existing | Water Systems | 0 | 250729.96
CZ06 | cAVVG | Existing | Refrigeration | 0 | 0
CZ06 | cAVVG | Existing | Generators | 0 | 0
CZ06 | cAVVG | Existing | Total End Uses | 854429.06 | 435304.85
CZ07 | cAVVG | Existing | Heating | 0 | 43302.27
CZ07 | cAVVG | Existing | Cooling | 213546.19 | 0
CZ07 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ07 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ07 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ07 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ07 | cAVVG | Existing | Fans | 155271.11 | 0
CZ07 | cAVVG | Existing | Pumps | 5951.33 | 0
CZ07 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ07 | cAVVG | Existing | Humidification | 0 | 0
CZ07 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ07 | cAVVG | Existing | Water Systems | 0 | 247338.69
CZ07 | cAVVG | Existing | Refrigeration | 0 | 0
CZ07 | cAVVG | Existing | Generators | 0 | 0
CZ07 | cAVVG | Existing | Total End Uses | 871710.39 | 436342.91
CZ08 | cAVVG | Existing | Heating | 0 | 55953.74
CZ08 | cAVVG | Existing | Cooling | 239947.54 | 0
CZ08 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ08 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ08 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ08 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ08 | cAVVG | Existing | Fans | 160200.06 | 0
CZ08 | cAVVG | Existing | Pumps | 6216.29 | 0
CZ08 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ08 | cAVVG | Existing | Humidification | 0 | 0
CZ08 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ08 | cAVVG | Existing | Water Systems | 0 | 246936.36
CZ08 | cAVVG | Existing | Refrigeration | 0 | 0
CZ08 | cAVVG | Existing | Generators | 0 | 0
CZ08 | cAVVG | Existing | Total End Uses | 903305.64 | 448592.05
CZ09 | cAVVG | Existing | Heating | 0 | 48492.74
CZ09 | cAVVG | Existing | Cooling | 271118.13 | 0
CZ09 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ09 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ09 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ09 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ09 | cAVVG | Existing | Fans | 180555.92 | 0
CZ09 | cAVVG | Existing | Pumps | 6618.83 | 0
CZ09 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ09 | cAVVG | Existing | Humidification | 0 | 0
CZ09 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ09 | cAVVG | Existing | Water Systems | 0 | 243521.92
CZ09 | cAVVG | Existing | Refrigeration | 0 | 0
CZ09 | cAVVG | Existing | Generators | 0 | 0
CZ09 | cAVVG | Existing | Total End Uses | 955234.63 | 437716.6
CZ10 | cAVVG | Existing | Heating | 0 | 91122.13
CZ10 | cAVVG | Existing | Cooling | 307385.46 | 0
CZ10 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ10 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ10 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ10 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ10 | cAVVG | Existing | Fans | 180172 | 0
CZ10 | cAVVG | Existing | Pumps | 6343.29 | 0
CZ10 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ10 | cAVVG | Existing | Humidification | 0 | 0
CZ10 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ10 | cAVVG | Existing | Water Systems | 0 | 240765.45
CZ10 | cAVVG | Existing | Refrigeration | 0 | 0
CZ10 | cAVVG | Existing | Generators | 0 | 0
CZ10 | cAVVG | Existing | Total End Uses | 990842.51 | 477589.53
CZ11 | cAVVG | Existing | Heating | 0 | 193991.3
CZ11 | cAVVG | Existing | Cooling | 323146.19 | 0
CZ11 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ11 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ11 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ11 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ11 | cAVVG | Existing | Fans | 200886.95 | 0
CZ11 | cAVVG | Existing | Pumps | 6109.65 | 0
CZ11 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ11 | cAVVG | Existing | Humidification | 0 | 0
CZ11 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ11 | cAVVG | Existing | Water Systems | 0 | 245678.21
CZ11 | cAVVG | Existing | Refrigeration | 0 | 0
CZ11 | cAVVG | Existing | Generators | 0 | 0
CZ11 | cAVVG | Existing | Total End Uses | 1027084.54 | 585371.45
CZ12 | cAVVG | Existing | Heating | 0 | 158825.05
CZ12 | cAVVG | Existing | Cooling | 274680.38 | 0
CZ12 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ12 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ12 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ12 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ12 | cAVVG | Existing | Fans | 204054.9 | 0
CZ12 | cAVVG | Existing | Pumps | 5849.97 | 0
CZ12 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ12 | cAVVG | Existing | Humidification | 0 | 0
CZ12 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ12 | cAVVG | Existing | Water Systems | 0 | 253125.34
CZ12 | cAVVG | Existing | Refrigeration | 0 | 0
CZ12 | cAVVG | Existing | Generators | 0 | 0
CZ12 | cAVVG | Existing | Total End Uses | 981527 | 557652.33
CZ13 | cAVVG | Existing | Heating | 0 | 137620.04
CZ13 | cAVVG | Existing | Cooling | 361932.82 | 0
CZ13 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ13 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ13 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ13 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ13 | cAVVG | Existing | Fans | 213020.18 | 0
CZ13 | cAVVG | Existing | Pumps | 7168.29 | 0
CZ13 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ13 | cAVVG | Existing | Humidification | 0 | 0
CZ13 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ13 | cAVVG | Existing | Water Systems | 0 | 238453.06
CZ13 | cAVVG | Existing | Refrigeration | 0 | 0
CZ13 | cAVVG | Existing | Generators | 0 | 0
CZ13 | cAVVG | Existing | Total End Uses | 1079063.04 | 521775.05
CZ14 | cAVVG | Existing | Heating | 0 | 104167.94
CZ14 | cAVVG | Existing | Cooling | 437490.84 | 0
CZ14 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ14 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ14 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ14 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ14 | cAVVG | Existing | Fans | 227132.76 | 0
CZ14 | cAVVG | Existing | Pumps | 6863.92 | 0
CZ14 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ14 | cAVVG | Existing | Humidification | 0 | 0
CZ14 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ14 | cAVVG | Existing | Water Systems | 0 | 225878.82
CZ14 | cAVVG | Existing | Refrigeration | 0 | 0
CZ14 | cAVVG | Existing | Generators | 0 | 0
CZ14 | cAVVG | Existing | Total End Uses | 1168429.27 | 475748.71
CZ15 | cAVVG | Existing | Heating | 0 | 52382.54
CZ15 | cAVVG | Existing | Cooling | 623702.82 | 0
CZ15 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ15 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ15 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ15 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ15 | cAVVG | Existing | Fans | 237678.99 | 0
CZ15 | cAVVG | Existing | Pumps | 10090.41 | 0
CZ15 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ15 | cAVVG | Existing | Humidification | 0 | 0
CZ15 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ15 | cAVVG | Existing | Water Systems | 0 | 200455.5
CZ15 | cAVVG | Existing | Refrigeration | 0 | 0
CZ15 | cAVVG | Existing | Generators | 0 | 0
CZ15 | cAVVG | Existing | Total End Uses | 1368413.97 | 398539.98
CZ16 | cAVVG | Existing | Heating | 0 | 235439.61
CZ16 | cAVVG | Existing | Cooling | 277046.46 | 0
CZ16 | cAVVG | Existing | Interior Lighting | 216717.02 | 0
CZ16 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ16 | cAVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ16 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ16 | cAVVG | Existing | Fans | 230774.5 | 0
CZ16 | cAVVG | Existing | Pumps | 6240.56 | 0
CZ16 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ16 | cAVVG | Existing | Humidification | 0 | 0
CZ16 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ16 | cAVVG | Existing | Water Systems | 0 | 267220.64
CZ16 | cAVVG | Existing | Refrigeration | 0 | 0
CZ16 | cAVVG | Existing | Generators | 0 | 0
CZ16 | cAVVG | Existing | Total End Uses | 1011003.27 | 648362.2
CZ01 | cAVVG | New Construction | Heating | 0 | 313791.1
CZ01 | cAVVG | New Construction | Cooling | 27402.13 | 0
CZ01 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ01 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ01 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ01 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ01 | cAVVG | New Construction | Fans | 121794.95 | 0
CZ01 | cAVVG | New Construction | Pumps | 500.43 | 0
CZ01 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ01 | cAVVG | New Construction | Humidification | 0 | 0
CZ01 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ01 | cAVVG | New Construction | Water Systems | 0 | 297261.09
CZ01 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ01 | cAVVG | New Construction | Generators | 0 | 0
CZ01 | cAVVG | New Construction | Total End Uses | 533320.61 | 756754.14
CZ02 | cAVVG | New Construction | Heating | 0 | 184521.17
CZ02 | cAVVG | New Construction | Cooling | 116908.95 | 0
CZ02 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ02 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ02 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ02 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ02 | cAVVG | New Construction | Fans | 141101.95 | 0
CZ02 | cAVVG | New Construction | Pumps | 2764.66 | 0
CZ02 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ02 | cAVVG | New Construction | Humidification | 0 | 0
CZ02 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ02 | cAVVG | New Construction | Water Systems | 0 | 272692.87
CZ02 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ02 | cAVVG | New Construction | Generators | 0 | 0
CZ02 | cAVVG | New Construction | Total End Uses | 644398.64 | 602915.99
CZ03 | cAVVG | New Construction | Heating | 0 | 129913.56
CZ03 | cAVVG | New Construction | Cooling | 82325.2 | 0
CZ03 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ03 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ03 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ03 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ03 | cAVVG | New Construction | Fans | 112100.05 | 0
CZ03 | cAVVG | New Construction | Pumps | 2319.6 | 0
CZ03 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ03 | cAVVG | New Construction | Humidification | 0 | 0
CZ03 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ03 | cAVVG | New Construction | Water Systems | 0 | 271787.89
CZ03 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ03 | cAVVG | New Construction | Generators | 0 | 0
CZ03 | cAVVG | New Construction | Total End Uses | 580367.95 | 547403.4
CZ04 | cAVVG | New Construction | Heating | 0 | 115810.85
CZ04 | cAVVG | New Construction | Cooling | 133099.57 | 0
CZ04 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ04 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ04 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ04 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ04 | cAVVG | New Construction | Fans | 121590.51 | 0
CZ04 | cAVVG | New Construction | Pumps | 3070.63 | 0
CZ04 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ04 | cAVVG | New Construction | Humidification | 0 | 0
CZ04 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ04 | cAVVG | New Construction | Water Systems | 0 | 262195.43
CZ04 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ04 | cAVVG | New Construction | Generators | 0 | 0
CZ04 | cAVVG | New Construction | Total End Uses | 641383.81 | 523708.23
CZ05 | cAVVG | New Construction | Heating | 0 | 129392.39
CZ05 | cAVVG | New Construction | Cooling | 94224.84 | 0
CZ05 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ05 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ05 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ05 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ05 | cAVVG | New Construction | Fans | 108853.93 | 0
CZ05 | cAVVG | New Construction | Pumps | 2763.68 | 0
CZ05 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ05 | cAVVG | New Construction | Humidification | 0 | 0
CZ05 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ05 | cAVVG | New Construction | Water Systems | 0 | 271875.46
CZ05 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ05 | cAVVG | New Construction | Generators | 0 | 0
CZ05 | cAVVG | New Construction | Total End Uses | 589465.54 | 546969.8
CZ06 | cAVVG | New Construction | Heating | 0 | 51417.29
CZ06 | cAVVG | New Construction | Cooling | 155515.31 | 0
CZ06 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ06 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ06 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ06 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ06 | cAVVG | New Construction | Fans | 126013.47 | 0
CZ06 | cAVVG | New Construction | Pumps | 5244.61 | 0
CZ06 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ06 | cAVVG | New Construction | Humidification | 0 | 0
CZ06 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ06 | cAVVG | New Construction | Water Systems | 0 | 250295.23
CZ06 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ06 | cAVVG | New Construction | Generators | 0 | 0
CZ06 | cAVVG | New Construction | Total End Uses | 670396.48 | 447414.47
CZ07 | cAVVG | New Construction | Heating | 0 | 55689.2
CZ07 | cAVVG | New Construction | Cooling | 169026.68 | 0
CZ07 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ07 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ07 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ07 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ07 | cAVVG | New Construction | Fans | 128241.94 | 0
CZ07 | cAVVG | New Construction | Pumps | 4427.72 | 0
CZ07 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ07 | cAVVG | New Construction | Humidification | 0 | 0
CZ07 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ07 | cAVVG | New Construction | Water Systems | 0 | 247014.52
CZ07 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ07 | cAVVG | New Construction | Generators | 0 | 0
CZ07 | cAVVG | New Construction | Total End Uses | 685319.43 | 448405.66
CZ08 | cAVVG | New Construction | Heating | 0 | 66073.28
CZ08 | cAVVG | New Construction | Cooling | 187936.59 | 0
CZ08 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ08 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ08 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ08 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ08 | cAVVG | New Construction | Fans | 129920.18 | 0
CZ08 | cAVVG | New Construction | Pumps | 4500.85 | 0
CZ08 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ08 | cAVVG | New Construction | Humidification | 0 | 0
CZ08 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ08 | cAVVG | New Construction | Water Systems | 0 | 246519.46
CZ08 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ08 | cAVVG | New Construction | Generators | 0 | 0
CZ08 | cAVVG | New Construction | Total End Uses | 705980.71 | 458294.68
CZ09 | cAVVG | New Construction | Heating | 0 | 55878.7
CZ09 | cAVVG | New Construction | Cooling | 200406.81 | 0
CZ09 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ09 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ09 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ09 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ09 | cAVVG | New Construction | Fans | 136176.08 | 0
CZ09 | cAVVG | New Construction | Pumps | 4427.31 | 0
CZ09 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ09 | cAVVG | New Construction | Humidification | 0 | 0
CZ09 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ09 | cAVVG | New Construction | Water Systems | 0 | 243182.03
CZ09 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ09 | cAVVG | New Construction | Generators | 0 | 0
CZ09 | cAVVG | New Construction | Total End Uses | 724633.29 | 444762.67
CZ10 | cAVVG | New Construction | Heating | 0 | 90234.72
CZ10 | cAVVG | New Construction | Cooling | 243905.65 | 0
CZ10 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ10 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ10 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ10 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ10 | cAVVG | New Construction | Fans | 139469.11 | 0
CZ10 | cAVVG | New Construction | Pumps | 4529.32 | 0
CZ10 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ10 | cAVVG | New Construction | Humidification | 0 | 0
CZ10 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ10 | cAVVG | New Construction | Water Systems | 0 | 240406.01
CZ10 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ10 | cAVVG | New Construction | Generators | 0 | 0
CZ10 | cAVVG | New Construction | Total End Uses | 771527.18 | 476342.68
CZ11 | cAVVG | New Construction | Heating | 0 | 168450.71
CZ11 | cAVVG | New Construction | Cooling | 249145.35 | 0
CZ11 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ11 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ11 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ11 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ11 | cAVVG | New Construction | Fans | 149419.27 | 0
CZ11 | cAVVG | New Construction | Pumps | 4005.45 | 0
CZ11 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ11 | cAVVG | New Construction | Humidification | 0 | 0
CZ11 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ11 | cAVVG | New Construction | Water Systems | 0 | 245396.42
CZ11 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ11 | cAVVG | New Construction | Generators | 0 | 0
CZ11 | cAVVG | New Construction | Total End Uses | 786193.17 | 559549.08
CZ12 | cAVVG | New Construction | Heating | 0 | 158419.48
CZ12 | cAVVG | New Construction | Cooling | 214062.05 | 0
CZ12 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ12 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ12 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ12 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ12 | cAVVG | New Construction | Fans | 156697.53 | 0
CZ12 | cAVVG | New Construction | Pumps | 4136.08 | 0
CZ12 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ12 | cAVVG | New Construction | Humidification | 0 | 0
CZ12 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ12 | cAVVG | New Construction | Water Systems | 0 | 252695.35
CZ12 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ12 | cAVVG | New Construction | Generators | 0 | 0
CZ12 | cAVVG | New Construction | Total End Uses | 758518.76 | 556816.78
CZ13 | cAVVG | New Construction | Heating | 0 | 128291.8
CZ13 | cAVVG | New Construction | Cooling | 278061.5 | 0
CZ13 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ13 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ13 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ13 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ13 | cAVVG | New Construction | Fans | 157428.4 | 0
CZ13 | cAVVG | New Construction | Pumps | 4732.85 | 0
CZ13 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ13 | cAVVG | New Construction | Humidification | 0 | 0
CZ13 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ13 | cAVVG | New Construction | Water Systems | 0 | 238116.62
CZ13 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ13 | cAVVG | New Construction | Generators | 0 | 0
CZ13 | cAVVG | New Construction | Total End Uses | 823845.85 | 512110.36
CZ14 | cAVVG | New Construction | Heating | 0 | 98450.48
CZ14 | cAVVG | New Construction | Cooling | 341489.42 | 0
CZ14 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ14 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ14 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ14 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ14 | cAVVG | New Construction | Fans | 165120.09 | 0
CZ14 | cAVVG | New Construction | Pumps | 4437.84 | 0
CZ14 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ14 | cAVVG | New Construction | Humidification | 0 | 0
CZ14 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ14 | cAVVG | New Construction | Water Systems | 0 | 225551.13
CZ14 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ14 | cAVVG | New Construction | Generators | 0 | 0
CZ14 | cAVVG | New Construction | Total End Uses | 894670.45 | 469703.56
CZ15 | cAVVG | New Construction | Heating | 0 | 60045.45
CZ15 | cAVVG | New Construction | Cooling | 494669.72 | 0
CZ15 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ15 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ15 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ15 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ15 | cAVVG | New Construction | Fans | 178131.74 | 0
CZ15 | cAVVG | New Construction | Pumps | 6736.05 | 0
CZ15 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ15 | cAVVG | New Construction | Humidification | 0 | 0
CZ15 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ15 | cAVVG | New Construction | Water Systems | 0 | 200099.32
CZ15 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ15 | cAVVG | New Construction | Generators | 0 | 0
CZ15 | cAVVG | New Construction | Total End Uses | 1063160.6 | 405846.71
CZ16 | cAVVG | New Construction | Heating | 0 | 220578.32
CZ16 | cAVVG | New Construction | Cooling | 218343.78 | 0
CZ16 | cAVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ16 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ16 | cAVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ16 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ16 | cAVVG | New Construction | Fans | 178244.48 | 0
CZ16 | cAVVG | New Construction | Pumps | 4413.77 | 0
CZ16 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ16 | cAVVG | New Construction | Humidification | 0 | 0
CZ16 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ16 | cAVVG | New Construction | Water Systems | 0 | 266918.67
CZ16 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ16 | cAVVG | New Construction | Generators | 0 | 0
CZ16 | cAVVG | New Construction | Total End Uses | 784625.12 | 633198.93
CZ01 | cDXGF | Existing | Heating | 0 | 183329.06
CZ01 | cDXGF | Existing | Cooling | 27363.16 | 0
CZ01 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ01 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ01 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXGF | Existing | Fans | 245806.77 | 0
CZ01 | cDXGF | Existing | Pumps | 0 | 0
CZ01 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ01 | cDXGF | Existing | Humidification | 0 | 0
CZ01 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ01 | cDXGF | Existing | Water Systems | 0 | 297524.36
CZ01 | cDXGF | Existing | Refrigeration | 0 | 0
CZ01 | cDXGF | Existing | Generators | 0 | 0
CZ01 | cDXGF | Existing | Total End Uses | 770111.68 | 626555.36
CZ02 | cDXGF | Existing | Heating | 0 | 101000.78
CZ02 | cDXGF | Existing | Cooling | 115331.88 | 0
CZ02 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ02 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ02 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXGF | Existing | Fans | 277304.94 | 0
CZ02 | cDXGF | Existing | Pumps | 0 | 0
CZ02 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ02 | cDXGF | Existing | Humidification | 0 | 0
CZ02 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ02 | cDXGF | Existing | Water Systems | 0 | 273013.46
CZ02 | cDXGF | Existing | Refrigeration | 0 | 0
CZ02 | cDXGF | Existing | Generators | 0 | 0
CZ02 | cDXGF | Existing | Total End Uses | 889578.57 | 519716.18
CZ03 | cDXGF | Existing | Heating | 0 | 59152.61
CZ03 | cDXGF | Existing | Cooling | 78928.82 | 0
CZ03 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ03 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ03 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXGF | Existing | Fans | 265024.82 | 0
CZ03 | cDXGF | Existing | Pumps | 0 | 0
CZ03 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ03 | cDXGF | Existing | Humidification | 0 | 0
CZ03 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ03 | cDXGF | Existing | Water Systems | 0 | 272138.93
CZ03 | cDXGF | Existing | Refrigeration | 0 | 0
CZ03 | cDXGF | Existing | Generators | 0 | 0
CZ03 | cDXGF | Existing | Total End Uses | 840895.39 | 476993.48
CZ04 | cDXGF | Existing | Heating | 0 | 52049.29
CZ04 | cDXGF | Existing | Cooling | 138187.61 | 0
CZ04 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ04 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ04 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXGF | Existing | Fans | 279566.05 | 0
CZ04 | cDXGF | Existing | Pumps | 0 | 0
CZ04 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ04 | cDXGF | Existing | Humidification | 0 | 0
CZ04 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ04 | cDXGF | Existing | Water Systems | 0 | 262527.05
CZ04 | cDXGF | Existing | Refrigeration | 0 | 0
CZ04 | cDXGF | Existing | Generators | 0 | 0
CZ04 | cDXGF | Existing | Total End Uses | 914695.41 | 460278.28
CZ05 | cDXGF | Existing | Heating | 0 | 53531.18
CZ05 | cDXGF | Existing | Cooling | 95501.65 | 0
CZ05 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ05 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ05 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXGF | Existing | Fans | 263023.74 | 0
CZ05 | cDXGF | Existing | Pumps | 0 | 0
CZ05 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ05 | cDXGF | Existing | Humidification | 0 | 0
CZ05 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ05 | cDXGF | Existing | Water Systems | 0 | 272209.89
CZ05 | cDXGF | Existing | Refrigeration | 0 | 0
CZ05 | cDXGF | Existing | Generators | 0 | 0
CZ05 | cDXGF | Existing | Total End Uses | 855467.14 | 471443.02
CZ06 | cDXGF | Existing | Heating | 0 | 11495.75
CZ06 | cDXGF | Existing | Cooling | 149358.86 | 0
CZ06 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ06 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ06 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXGF | Existing | Fans | 276226.02 | 0
CZ06 | cDXGF | Existing | Pumps | 0 | 0
CZ06 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ06 | cDXGF | Existing | Humidification | 0 | 0
CZ06 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ06 | cDXGF | Existing | Water Systems | 0 | 250734.03
CZ06 | cDXGF | Existing | Refrigeration | 0 | 0
CZ06 | cDXGF | Existing | Generators | 0 | 0
CZ06 | cDXGF | Existing | Total End Uses | 922526.64 | 407931.73
CZ07 | cDXGF | Existing | Heating | 0 | 11252.79
CZ07 | cDXGF | Existing | Cooling | 163438.53 | 0
CZ07 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ07 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ07 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXGF | Existing | Fans | 273440.9 | 0
CZ07 | cDXGF | Existing | Pumps | 0 | 0
CZ07 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ07 | cDXGF | Existing | Humidification | 0 | 0
CZ07 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ07 | cDXGF | Existing | Water Systems | 0 | 247317.93
CZ07 | cDXGF | Existing | Refrigeration | 0 | 0
CZ07 | cDXGF | Existing | Generators | 0 | 0
CZ07 | cDXGF | Existing | Total End Uses | 933821.18 | 404272.67
CZ08 | cDXGF | Existing | Heating | 0 | 17199.37
CZ08 | cDXGF | Existing | Cooling | 184673.4 | 0
CZ08 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ08 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ08 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXGF | Existing | Fans | 287124.2 | 0
CZ08 | cDXGF | Existing | Pumps | 0 | 0
CZ08 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ08 | cDXGF | Existing | Humidification | 0 | 0
CZ08 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ08 | cDXGF | Existing | Water Systems | 0 | 246912.73
CZ08 | cDXGF | Existing | Refrigeration | 0 | 0
CZ08 | cDXGF | Existing | Generators | 0 | 0
CZ08 | cDXGF | Existing | Total End Uses | 968739.35 | 409814.04
CZ09 | cDXGF | Existing | Heating | 0 | 12536.35
CZ09 | cDXGF | Existing | Cooling | 211373.37 | 0
CZ09 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ09 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ09 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXGF | Existing | Fans | 302536.47 | 0
CZ09 | cDXGF | Existing | Pumps | 0 | 0
CZ09 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ09 | cDXGF | Existing | Humidification | 0 | 0
CZ09 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ09 | cDXGF | Existing | Water Systems | 0 | 243529.23
CZ09 | cDXGF | Existing | Refrigeration | 0 | 0
CZ09 | cDXGF | Existing | Generators | 0 | 0
CZ09 | cDXGF | Existing | Total End Uses | 1010851.59 | 401767.53
CZ10 | cDXGF | Existing | Heating | 0 | 38913.97
CZ10 | cDXGF | Existing | Cooling | 246493.87 | 0
CZ10 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ10 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ10 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXGF | Existing | Fans | 296708.72 | 0
CZ10 | cDXGF | Existing | Pumps | 0 | 0
CZ10 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ10 | cDXGF | Existing | Humidification | 0 | 0
CZ10 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ10 | cDXGF | Existing | Water Systems | 0 | 240759.86
CZ10 | cDXGF | Existing | Refrigeration | 0 | 0
CZ10 | cDXGF | Existing | Generators | 0 | 0
CZ10 | cDXGF | Existing | Total End Uses | 1040144.33 | 425375.78
CZ11 | cDXGF | Existing | Heating | 0 | 100122.02
CZ11 | cDXGF | Existing | Cooling | 264994.18 | 0
CZ11 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ11 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ11 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXGF | Existing | Fans | 330097.07 | 0
CZ11 | cDXGF | Existing | Pumps | 0 | 0
CZ11 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ11 | cDXGF | Existing | Humidification | 0 | 0
CZ11 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ11 | cDXGF | Existing | Water Systems | 0 | 245697.89
CZ11 | cDXGF | Existing | Refrigeration | 0 | 0
CZ11 | cDXGF | Existing | Generators | 0 | 0
CZ11 | cDXGF | Existing | Total End Uses | 1092032.99 | 491521.85
CZ12 | cDXGF | Existing | Heating | 0 | 87843.02
CZ12 | cDXGF | Existing | Cooling | 221182.33 | 0
CZ12 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ12 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ12 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXGF | Existing | Fans | 302087.35 | 0
CZ12 | cDXGF | Existing | Pumps | 0 | 0
CZ12 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ12 | cDXGF | Existing | Humidification | 0 | 0
CZ12 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ12 | cDXGF | Existing | Water Systems | 0 | 253134.19
CZ12 | cDXGF | Existing | Refrigeration | 0 | 0
CZ12 | cDXGF | Existing | Generators | 0 | 0
CZ12 | cDXGF | Existing | Total End Uses | 1020211.44 | 486679.15
CZ13 | cDXGF | Existing | Heating | 0 | 67537.43
CZ13 | cDXGF | Existing | Cooling | 296837.83 | 0
CZ13 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ13 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ13 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXGF | Existing | Fans | 331348.01 | 0
CZ13 | cDXGF | Existing | Pumps | 0 | 0
CZ13 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ13 | cDXGF | Existing | Humidification | 0 | 0
CZ13 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ13 | cDXGF | Existing | Water Systems | 0 | 238470.23
CZ13 | cDXGF | Existing | Refrigeration | 0 | 0
CZ13 | cDXGF | Existing | Generators | 0 | 0
CZ13 | cDXGF | Existing | Total End Uses | 1125127.59 | 451709.61
CZ14 | cDXGF | Existing | Heating | 0 | 38459.61
CZ14 | cDXGF | Existing | Cooling | 368345.53 | 0
CZ14 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ14 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ14 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXGF | Existing | Fans | 359323.42 | 0
CZ14 | cDXGF | Existing | Pumps | 0 | 0
CZ14 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ14 | cDXGF | Existing | Humidification | 0 | 0
CZ14 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ14 | cDXGF | Existing | Water Systems | 0 | 225854.31
CZ14 | cDXGF | Existing | Refrigeration | 0 | 0
CZ14 | cDXGF | Existing | Generators | 0 | 0
CZ14 | cDXGF | Existing | Total End Uses | 1224610.7 | 410015.87
CZ15 | cDXGF | Existing | Heating | 0 | 12987.48
CZ15 | cDXGF | Existing | Cooling | 496598.43 | 0
CZ15 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ15 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ15 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXGF | Existing | Fans | 352015.98 | 0
CZ15 | cDXGF | Existing | Pumps | 0 | 0
CZ15 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ15 | cDXGF | Existing | Humidification | 0 | 0
CZ15 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ15 | cDXGF | Existing | Water Systems | 0 | 200448.52
CZ15 | cDXGF | Existing | Refrigeration | 0 | 0
CZ15 | cDXGF | Existing | Generators | 0 | 0
CZ15 | cDXGF | Existing | Total End Uses | 1345556.15 | 359137.94
CZ16 | cDXGF | Existing | Heating | 0 | 134687.72
CZ16 | cDXGF | Existing | Cooling | 236288.98 | 0
CZ16 | cDXGF | Existing | Interior Lighting | 216717.02 | 0
CZ16 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXGF | Existing | Interior Equipment | 280224.73 | 145701.95
CZ16 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXGF | Existing | Fans | 356851.28 | 0
CZ16 | cDXGF | Existing | Pumps | 0 | 0
CZ16 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ16 | cDXGF | Existing | Humidification | 0 | 0
CZ16 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ16 | cDXGF | Existing | Water Systems | 0 | 267234.98
CZ16 | cDXGF | Existing | Refrigeration | 0 | 0
CZ16 | cDXGF | Existing | Generators | 0 | 0
CZ16 | cDXGF | Existing | Total End Uses | 1090082.01 | 547624.65
CZ01 | cDXGF | New Construction | Heating | 0 | 226364.85
CZ01 | cDXGF | New Construction | Cooling | 23205.7 | 0
CZ01 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ01 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ01 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXGF | New Construction | Fans | 179619.22 | 0
CZ01 | cDXGF | New Construction | Pumps | 0 | 0
CZ01 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXGF | New Construction | Humidification | 0 | 0
CZ01 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXGF | New Construction | Water Systems | 0 | 297212.87
CZ01 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ01 | cDXGF | New Construction | Generators | 0 | 0
CZ01 | cDXGF | New Construction | Total End Uses | 586448.02 | 669279.67
CZ02 | cDXGF | New Construction | Heating | 0 | 117853.73
CZ02 | cDXGF | New Construction | Cooling | 89025.02 | 0
CZ02 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ02 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ02 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXGF | New Construction | Fans | 193831.09 | 0
CZ02 | cDXGF | New Construction | Pumps | 0 | 0
CZ02 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXGF | New Construction | Humidification | 0 | 0
CZ02 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXGF | New Construction | Water Systems | 0 | 272654.36
CZ02 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ02 | cDXGF | New Construction | Generators | 0 | 0
CZ02 | cDXGF | New Construction | Total End Uses | 666479.2 | 536210.03
CZ03 | cDXGF | New Construction | Heating | 0 | 81293.47
CZ03 | cDXGF | New Construction | Cooling | 60772.63 | 0
CZ03 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ03 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ03 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXGF | New Construction | Fans | 191555.54 | 0
CZ03 | cDXGF | New Construction | Pumps | 0 | 0
CZ03 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXGF | New Construction | Humidification | 0 | 0
CZ03 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXGF | New Construction | Water Systems | 0 | 271844.96
CZ03 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ03 | cDXGF | New Construction | Generators | 0 | 0
CZ03 | cDXGF | New Construction | Total End Uses | 635951.26 | 498840.38
CZ04 | cDXGF | New Construction | Heating | 0 | 68341.48
CZ04 | cDXGF | New Construction | Cooling | 104335.57 | 0
CZ04 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ04 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ04 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXGF | New Construction | Fans | 194616.78 | 0
CZ04 | cDXGF | New Construction | Pumps | 0 | 0
CZ04 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXGF | New Construction | Humidification | 0 | 0
CZ04 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXGF | New Construction | Water Systems | 0 | 262159.09
CZ04 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ04 | cDXGF | New Construction | Generators | 0 | 0
CZ04 | cDXGF | New Construction | Total End Uses | 682575.44 | 476202.52
CZ05 | cDXGF | New Construction | Heating | 0 | 77200.72
CZ05 | cDXGF | New Construction | Cooling | 73237.29 | 0
CZ05 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ05 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ05 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXGF | New Construction | Fans | 190214.1 | 0
CZ05 | cDXGF | New Construction | Pumps | 0 | 0
CZ05 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXGF | New Construction | Humidification | 0 | 0
CZ05 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXGF | New Construction | Water Systems | 0 | 271784.29
CZ05 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ05 | cDXGF | New Construction | Generators | 0 | 0
CZ05 | cDXGF | New Construction | Total End Uses | 647074.48 | 494686.96
CZ06 | cDXGF | New Construction | Heating | 0 | 19705.72
CZ06 | cDXGF | New Construction | Cooling | 113356.42 | 0
CZ06 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ06 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ06 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXGF | New Construction | Fans | 202893.35 | 0
CZ06 | cDXGF | New Construction | Pumps | 0 | 0
CZ06 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXGF | New Construction | Humidification | 0 | 0
CZ06 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXGF | New Construction | Water Systems | 0 | 250336.84
CZ06 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ06 | cDXGF | New Construction | Generators | 0 | 0
CZ06 | cDXGF | New Construction | Total End Uses | 699872.86 | 415744.51
CZ07 | cDXGF | New Construction | Heating | 0 | 19143.84
CZ07 | cDXGF | New Construction | Cooling | 123003.1 | 0
CZ07 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ07 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ07 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXGF | New Construction | Fans | 201239.5 | 0
CZ07 | cDXGF | New Construction | Pumps | 0 | 0
CZ07 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXGF | New Construction | Humidification | 0 | 0
CZ07 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXGF | New Construction | Water Systems | 0 | 246870.04
CZ07 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ07 | cDXGF | New Construction | Generators | 0 | 0
CZ07 | cDXGF | New Construction | Total End Uses | 707865.69 | 411715.83
CZ08 | cDXGF | New Construction | Heating | 0 | 27425.19
CZ08 | cDXGF | New Construction | Cooling | 140126.84 | 0
CZ08 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ08 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ08 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXGF | New Construction | Fans | 207311.03 | 0
CZ08 | cDXGF | New Construction | Pumps | 0 | 0
CZ08 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXGF | New Construction | Humidification | 0 | 0
CZ08 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXGF | New Construction | Water Systems | 0 | 246564.08
CZ08 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ08 | cDXGF | New Construction | Generators | 0 | 0
CZ08 | cDXGF | New Construction | Total End Uses | 731060.97 | 419691.21
CZ09 | cDXGF | New Construction | Heating | 0 | 18353.46
CZ09 | cDXGF | New Construction | Cooling | 153268.16 | 0
CZ09 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ09 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ09 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXGF | New Construction | Fans | 199179.97 | 0
CZ09 | cDXGF | New Construction | Pumps | 0 | 0
CZ09 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXGF | New Construction | Humidification | 0 | 0
CZ09 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXGF | New Construction | Water Systems | 0 | 243189.54
CZ09 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ09 | cDXGF | New Construction | Generators | 0 | 0
CZ09 | cDXGF | New Construction | Total End Uses | 736071.22 | 407244.94
CZ10 | cDXGF | New Construction | Heating | 0 | 48982.39
CZ10 | cDXGF | New Construction | Cooling | 192399.8 | 0
CZ10 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ10 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ10 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXGF | New Construction | Fans | 207988.49 | 0
CZ10 | cDXGF | New Construction | Pumps | 0 | 0
CZ10 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXGF | New Construction | Humidification | 0 | 0
CZ10 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXGF | New Construction | Water Systems | 0 | 240475.85
CZ10 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ10 | cDXGF | New Construction | Generators | 0 | 0
CZ10 | cDXGF | New Construction | Total End Uses | 784011.39 | 435160.18
CZ11 | cDXGF | New Construction | Heating | 0 | 112965.5
CZ11 | cDXGF | New Construction | Cooling | 199407.23 | 0
CZ11 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ11 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ11 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXGF | New Construction | Fans | 212366.73 | 0
CZ11 | cDXGF | New Construction | Pumps | 0 | 0
CZ11 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXGF | New Construction | Humidification | 0 | 0
CZ11 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXGF | New Construction | Water Systems | 0 | 245381.41
CZ11 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ11 | cDXGF | New Construction | Generators | 0 | 0
CZ11 | cDXGF | New Construction | Total End Uses | 795397.05 | 504048.85
CZ12 | cDXGF | New Construction | Heating | 0 | 101870.26
CZ12 | cDXGF | New Construction | Cooling | 167918.96 | 0
CZ12 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ12 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ12 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXGF | New Construction | Fans | 202817.55 | 0
CZ12 | cDXGF | New Construction | Pumps | 0 | 0
CZ12 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXGF | New Construction | Humidification | 0 | 0
CZ12 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXGF | New Construction | Water Systems | 0 | 252800.08
CZ12 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ12 | cDXGF | New Construction | Generators | 0 | 0
CZ12 | cDXGF | New Construction | Total End Uses | 754359.6 | 500372.29
CZ13 | cDXGF | New Construction | Heating | 0 | 81981.33
CZ13 | cDXGF | New Construction | Cooling | 222994.45 | 0
CZ13 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ13 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ13 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXGF | New Construction | Fans | 214485.98 | 0
CZ13 | cDXGF | New Construction | Pumps | 0 | 0
CZ13 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXGF | New Construction | Humidification | 0 | 0
CZ13 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXGF | New Construction | Water Systems | 0 | 238130.54
CZ13 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ13 | cDXGF | New Construction | Generators | 0 | 0
CZ13 | cDXGF | New Construction | Total End Uses | 821103.53 | 465813.81
CZ14 | cDXGF | New Construction | Heating | 0 | 50127.85
CZ14 | cDXGF | New Construction | Cooling | 280410.1 | 0
CZ14 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ14 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ14 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXGF | New Construction | Fans | 233007.91 | 0
CZ14 | cDXGF | New Construction | Pumps | 0 | 0
CZ14 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXGF | New Construction | Humidification | 0 | 0
CZ14 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXGF | New Construction | Water Systems | 0 | 225423.32
CZ14 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ14 | cDXGF | New Construction | Generators | 0 | 0
CZ14 | cDXGF | New Construction | Total End Uses | 897041.11 | 421253.12
CZ15 | cDXGF | New Construction | Heating | 0 | 18622.11
CZ15 | cDXGF | New Construction | Cooling | 378910.18 | 0
CZ15 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ15 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ15 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXGF | New Construction | Fans | 223765.39 | 0
CZ15 | cDXGF | New Construction | Pumps | 0 | 0
CZ15 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXGF | New Construction | Humidification | 0 | 0
CZ15 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXGF | New Construction | Water Systems | 0 | 200021.39
CZ15 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ15 | cDXGF | New Construction | Generators | 0 | 0
CZ15 | cDXGF | New Construction | Total End Uses | 986298.67 | 364345.45
CZ16 | cDXGF | New Construction | Heating | 0 | 148215.47
CZ16 | cDXGF | New Construction | Cooling | 183689.15 | 0
CZ16 | cDXGF | New Construction | Interior Lighting | 103398.36 | 0
CZ16 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXGF | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ16 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXGF | New Construction | Fans | 241472.87 | 0
CZ16 | cDXGF | New Construction | Pumps | 0 | 0
CZ16 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXGF | New Construction | Humidification | 0 | 0
CZ16 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXGF | New Construction | Water Systems | 0 | 266916
CZ16 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ16 | cDXGF | New Construction | Generators | 0 | 0
CZ16 | cDXGF | New Construction | Total End Uses | 808785.11 | 560833.42
CZ01 | cDXHP | Existing | Heating | 44631.38 | 0
CZ01 | cDXHP | Existing | Cooling | 27038.77 | 0
CZ01 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ01 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ01 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXHP | Existing | Fans | 245806.77 | 0
CZ01 | cDXHP | Existing | Pumps | 0 | 0
CZ01 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ01 | cDXHP | Existing | Humidification | 0 | 0
CZ01 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ01 | cDXHP | Existing | Water Systems | 0 | 297524.36
CZ01 | cDXHP | Existing | Refrigeration | 0 | 0
CZ01 | cDXHP | Existing | Generators | 0 | 0
CZ01 | cDXHP | Existing | Total End Uses | 814418.68 | 443226.31
CZ02 | cDXHP | Existing | Heating | 27094.82 | 0.04
CZ02 | cDXHP | Existing | Cooling | 114229.54 | 0
CZ02 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ02 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ02 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXHP | Existing | Fans | 277303.51 | 0
CZ02 | cDXHP | Existing | Pumps | 0 | 0
CZ02 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ02 | cDXHP | Existing | Humidification | 0 | 0
CZ02 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ02 | cDXHP | Existing | Water Systems | 0 | 273000.47
CZ02 | cDXHP | Existing | Refrigeration | 0 | 0
CZ02 | cDXHP | Existing | Generators | 0 | 0
CZ02 | cDXHP | Existing | Total End Uses | 915569.62 | 418702.45
CZ03 | cDXHP | Existing | Heating | 14500.13 | 0
CZ03 | cDXHP | Existing | Cooling | 78125.16 | 0
CZ03 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ03 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ03 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXHP | Existing | Fans | 265024.82 | 0
CZ03 | cDXHP | Existing | Pumps | 0 | 0
CZ03 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ03 | cDXHP | Existing | Humidification | 0 | 0
CZ03 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ03 | cDXHP | Existing | Water Systems | 0 | 272138.93
CZ03 | cDXHP | Existing | Refrigeration | 0 | 0
CZ03 | cDXHP | Existing | Generators | 0 | 0
CZ03 | cDXHP | Existing | Total End Uses | 854591.86 | 417840.87
CZ04 | cDXHP | Existing | Heating | 12827.58 | 0
CZ04 | cDXHP | Existing | Cooling | 137542.78 | 0
CZ04 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ04 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ04 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXHP | Existing | Fans | 279566.05 | 0
CZ04 | cDXHP | Existing | Pumps | 0 | 0
CZ04 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ04 | cDXHP | Existing | Humidification | 0 | 0
CZ04 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ04 | cDXHP | Existing | Water Systems | 0 | 262527.87
CZ04 | cDXHP | Existing | Refrigeration | 0 | 0
CZ04 | cDXHP | Existing | Generators | 0 | 0
CZ04 | cDXHP | Existing | Total End Uses | 926878.16 | 408229.82
CZ05 | cDXHP | Existing | Heating | 13671.13 | 0
CZ05 | cDXHP | Existing | Cooling | 94701.54 | 0
CZ05 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ05 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ05 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXHP | Existing | Fans | 263023.74 | 0
CZ05 | cDXHP | Existing | Pumps | 0 | 0
CZ05 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ05 | cDXHP | Existing | Humidification | 0 | 0
CZ05 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ05 | cDXHP | Existing | Water Systems | 0 | 272204.85
CZ05 | cDXHP | Existing | Refrigeration | 0 | 0
CZ05 | cDXHP | Existing | Generators | 0 | 0
CZ05 | cDXHP | Existing | Total End Uses | 868338.17 | 417906.79
CZ06 | cDXHP | Existing | Heating | 2719.91 | 0
CZ06 | cDXHP | Existing | Cooling | 144377.56 | 0
CZ06 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ06 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ06 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXHP | Existing | Fans | 276226.02 | 0
CZ06 | cDXHP | Existing | Pumps | 0 | 0
CZ06 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ06 | cDXHP | Existing | Humidification | 0 | 0
CZ06 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ06 | cDXHP | Existing | Water Systems | 0 | 250745.84
CZ06 | cDXHP | Existing | Refrigeration | 0 | 0
CZ06 | cDXHP | Existing | Generators | 0 | 0
CZ06 | cDXHP | Existing | Total End Uses | 920265.24 | 396447.79
CZ07 | cDXHP | Existing | Heating | 2669.83 | 0
CZ07 | cDXHP | Existing | Cooling | 160076.18 | 0
CZ07 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ07 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ07 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXHP | Existing | Fans | 273440.9 | 0
CZ07 | cDXHP | Existing | Pumps | 0 | 0
CZ07 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ07 | cDXHP | Existing | Humidification | 0 | 0
CZ07 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ07 | cDXHP | Existing | Water Systems | 0 | 247318.2
CZ07 | cDXHP | Existing | Refrigeration | 0 | 0
CZ07 | cDXHP | Existing | Generators | 0 | 0
CZ07 | cDXHP | Existing | Total End Uses | 933128.67 | 393020.15
CZ08 | cDXHP | Existing | Heating | 4133.78 | 0
CZ08 | cDXHP | Existing | Cooling | 182844.87 | 0
CZ08 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ08 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ08 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXHP | Existing | Fans | 287124.2 | 0
CZ08 | cDXHP | Existing | Pumps | 0 | 0
CZ08 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ08 | cDXHP | Existing | Humidification | 0 | 0
CZ08 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ08 | cDXHP | Existing | Water Systems | 0 | 246912.73
CZ08 | cDXHP | Existing | Refrigeration | 0 | 0
CZ08 | cDXHP | Existing | Generators | 0 | 0
CZ08 | cDXHP | Existing | Total End Uses | 971044.6 | 392614.68
CZ09 | cDXHP | Existing | Heating | 2997.08 | 0
CZ09 | cDXHP | Existing | Cooling | 208953.08 | 0
CZ09 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ09 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ09 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXHP | Existing | Fans | 302536.47 | 0
CZ09 | cDXHP | Existing | Pumps | 0 | 0
CZ09 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ09 | cDXHP | Existing | Humidification | 0 | 0
CZ09 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ09 | cDXHP | Existing | Water Systems | 0 | 243529.4
CZ09 | cDXHP | Existing | Refrigeration | 0 | 0
CZ09 | cDXHP | Existing | Generators | 0 | 0
CZ09 | cDXHP | Existing | Total End Uses | 1011428.38 | 389231.34
CZ10 | cDXHP | Existing | Heating | 10695.66 | 0
CZ10 | cDXHP | Existing | Cooling | 246251.14 | 0
CZ10 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ10 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ10 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXHP | Existing | Fans | 296708.71 | 0
CZ10 | cDXHP | Existing | Pumps | 0 | 0
CZ10 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ10 | cDXHP | Existing | Humidification | 0 | 0
CZ10 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ10 | cDXHP | Existing | Water Systems | 0 | 240788.34
CZ10 | cDXHP | Existing | Refrigeration | 0 | 0
CZ10 | cDXHP | Existing | Generators | 0 | 0
CZ10 | cDXHP | Existing | Total End Uses | 1050597.26 | 386490.28
CZ11 | cDXHP | Existing | Heating | 26313.73 | 0
CZ11 | cDXHP | Existing | Cooling | 265690.5 | 0
CZ11 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ11 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ11 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXHP | Existing | Fans | 330089.87 | 0
CZ11 | cDXHP | Existing | Pumps | 0 | 0
CZ11 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ11 | cDXHP | Existing | Humidification | 0 | 0
CZ11 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ11 | cDXHP | Existing | Water Systems | 0 | 245706.43
CZ11 | cDXHP | Existing | Refrigeration | 0 | 0
CZ11 | cDXHP | Existing | Generators | 0 | 0
CZ11 | cDXHP | Existing | Total End Uses | 1119035.85 | 391408.37
CZ12 | cDXHP | Existing | Heating | 23317.01 | 0
CZ12 | cDXHP | Existing | Cooling | 221141.24 | 0
CZ12 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ12 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ12 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXHP | Existing | Fans | 302089.7 | 0
CZ12 | cDXHP | Existing | Pumps | 0 | 0
CZ12 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ12 | cDXHP | Existing | Humidification | 0 | 0
CZ12 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ12 | cDXHP | Existing | Water Systems | 0 | 253125.38
CZ12 | cDXHP | Existing | Refrigeration | 0 | 0
CZ12 | cDXHP | Existing | Generators | 0 | 0
CZ12 | cDXHP | Existing | Total End Uses | 1043489.7 | 398827.32
CZ13 | cDXHP | Existing | Heating | 17676.08 | 0
CZ13 | cDXHP | Existing | Cooling | 296926.95 | 0
CZ13 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ13 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ13 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXHP | Existing | Fans | 331348.01 | 0
CZ13 | cDXHP | Existing | Pumps | 0 | 0
CZ13 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ13 | cDXHP | Existing | Humidification | 0 | 0
CZ13 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ13 | cDXHP | Existing | Water Systems | 0 | 238461.54
CZ13 | cDXHP | Existing | Refrigeration | 0 | 0
CZ13 | cDXHP | Existing | Generators | 0 | 0
CZ13 | cDXHP | Existing | Total End Uses | 1142892.79 | 384163.48
CZ14 | cDXHP | Existing | Heating | 10530.56 | 0
CZ14 | cDXHP | Existing | Cooling | 369087.65 | 0
CZ14 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ14 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ14 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXHP | Existing | Fans | 359315.8 | 0
CZ14 | cDXHP | Existing | Pumps | 0 | 0
CZ14 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ14 | cDXHP | Existing | Humidification | 0 | 0
CZ14 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ14 | cDXHP | Existing | Water Systems | 0 | 225836.94
CZ14 | cDXHP | Existing | Refrigeration | 0 | 0
CZ14 | cDXHP | Existing | Generators | 0 | 0
CZ14 | cDXHP | Existing | Total End Uses | 1235875.76 | 371538.89
CZ15 | cDXHP | Existing | Heating | 3356.86 | 0
CZ15 | cDXHP | Existing | Cooling | 496523.66 | 0
CZ15 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ15 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ15 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXHP | Existing | Fans | 352015.98 | 0
CZ15 | cDXHP | Existing | Pumps | 0 | 0
CZ15 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ15 | cDXHP | Existing | Humidification | 0 | 0
CZ15 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ15 | cDXHP | Existing | Water Systems | 0 | 200448.52
CZ15 | cDXHP | Existing | Refrigeration | 0 | 0
CZ15 | cDXHP | Existing | Generators | 0 | 0
CZ15 | cDXHP | Existing | Total End Uses | 1348838.25 | 346150.46
CZ16 | cDXHP | Existing | Heating | 43537.54 | 30.01
CZ16 | cDXHP | Existing | Cooling | 238255.71 | 0
CZ16 | cDXHP | Existing | Interior Lighting | 216717.02 | 0
CZ16 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXHP | Existing | Interior Equipment | 280224.73 | 145701.95
CZ16 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXHP | Existing | Fans | 356852.91 | 0
CZ16 | cDXHP | Existing | Pumps | 0 | 0
CZ16 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ16 | cDXHP | Existing | Humidification | 0 | 0
CZ16 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ16 | cDXHP | Existing | Water Systems | 0 | 267250.89
CZ16 | cDXHP | Existing | Refrigeration | 0 | 0
CZ16 | cDXHP | Existing | Generators | 0 | 0
CZ16 | cDXHP | Existing | Total End Uses | 1135587.91 | 412982.85
CZ01 | cDXHP | New Construction | Heating | 54305.65 | 0
CZ01 | cDXHP | New Construction | Cooling | 22887.5 | 0
CZ01 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ01 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ01 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXHP | New Construction | Fans | 179619.22 | 0
CZ01 | cDXHP | New Construction | Pumps | 0 | 0
CZ01 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXHP | New Construction | Humidification | 0 | 0
CZ01 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXHP | New Construction | Water Systems | 0 | 297212.87
CZ01 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ01 | cDXHP | New Construction | Generators | 0 | 0
CZ01 | cDXHP | New Construction | Total End Uses | 640435.46 | 442914.82
CZ02 | cDXHP | New Construction | Heating | 30228.92 | 0
CZ02 | cDXHP | New Construction | Cooling | 88305.48 | 0
CZ02 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ02 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ02 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXHP | New Construction | Fans | 193822.41 | 0
CZ02 | cDXHP | New Construction | Pumps | 0 | 0
CZ02 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXHP | New Construction | Humidification | 0 | 0
CZ02 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXHP | New Construction | Water Systems | 0 | 272670.82
CZ02 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ02 | cDXHP | New Construction | Generators | 0 | 0
CZ02 | cDXHP | New Construction | Total End Uses | 695979.9 | 418372.77
CZ03 | cDXHP | New Construction | Heating | 19498.3 | 0
CZ03 | cDXHP | New Construction | Cooling | 60275.46 | 0
CZ03 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ03 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ03 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXHP | New Construction | Fans | 191555.54 | 0
CZ03 | cDXHP | New Construction | Pumps | 0 | 0
CZ03 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXHP | New Construction | Humidification | 0 | 0
CZ03 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXHP | New Construction | Water Systems | 0 | 271809.23
CZ03 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ03 | cDXHP | New Construction | Generators | 0 | 0
CZ03 | cDXHP | New Construction | Total End Uses | 654952.39 | 417511.18
CZ04 | cDXHP | New Construction | Heating | 16491.32 | 0
CZ04 | cDXHP | New Construction | Cooling | 104064.38 | 0
CZ04 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ04 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ04 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXHP | New Construction | Fans | 194616.78 | 0
CZ04 | cDXHP | New Construction | Pumps | 0 | 0
CZ04 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXHP | New Construction | Humidification | 0 | 0
CZ04 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXHP | New Construction | Water Systems | 0 | 262142.1
CZ04 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ04 | cDXHP | New Construction | Generators | 0 | 0
CZ04 | cDXHP | New Construction | Total End Uses | 698795.58 | 407844.04
CZ05 | cDXHP | New Construction | Heating | 18971.81 | 0
CZ05 | cDXHP | New Construction | Cooling | 72765.31 | 0
CZ05 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ05 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ05 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXHP | New Construction | Fans | 190214.1 | 0
CZ05 | cDXHP | New Construction | Pumps | 0 | 0
CZ05 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXHP | New Construction | Humidification | 0 | 0
CZ05 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXHP | New Construction | Water Systems | 0 | 271709.01
CZ05 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ05 | cDXHP | New Construction | Generators | 0 | 0
CZ05 | cDXHP | New Construction | Total End Uses | 665574.31 | 417410.96
CZ06 | cDXHP | New Construction | Heating | 4606.7 | 0
CZ06 | cDXHP | New Construction | Cooling | 109340.32 | 0
CZ06 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ06 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ06 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXHP | New Construction | Fans | 202893.35 | 0
CZ06 | cDXHP | New Construction | Pumps | 0 | 0
CZ06 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXHP | New Construction | Humidification | 0 | 0
CZ06 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXHP | New Construction | Water Systems | 0 | 250299.39
CZ06 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ06 | cDXHP | New Construction | Generators | 0 | 0
CZ06 | cDXHP | New Construction | Total End Uses | 700463.46 | 396001.34
CZ07 | cDXHP | New Construction | Heating | 4478.83 | 0
CZ07 | cDXHP | New Construction | Cooling | 120555.99 | 0
CZ07 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ07 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ07 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXHP | New Construction | Fans | 201239.5 | 0
CZ07 | cDXHP | New Construction | Pumps | 0 | 0
CZ07 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXHP | New Construction | Humidification | 0 | 0
CZ07 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXHP | New Construction | Water Systems | 0 | 246887.02
CZ07 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ07 | cDXHP | New Construction | Generators | 0 | 0
CZ07 | cDXHP | New Construction | Total End Uses | 709897.41 | 392588.97
CZ08 | cDXHP | New Construction | Heating | 6491.73 | 0
CZ08 | cDXHP | New Construction | Cooling | 139138.28 | 0
CZ08 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ08 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ08 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXHP | New Construction | Fans | 207311.03 | 0
CZ08 | cDXHP | New Construction | Pumps | 0 | 0
CZ08 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXHP | New Construction | Humidification | 0 | 0
CZ08 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXHP | New Construction | Water Systems | 0 | 246564.08
CZ08 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ08 | cDXHP | New Construction | Generators | 0 | 0
CZ08 | cDXHP | New Construction | Total End Uses | 736564.14 | 392266.02
CZ09 | cDXHP | New Construction | Heating | 4334.53 | 0
CZ09 | cDXHP | New Construction | Cooling | 151892.35 | 0
CZ09 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ09 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ09 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXHP | New Construction | Fans | 199179.97 | 0
CZ09 | cDXHP | New Construction | Pumps | 0 | 0
CZ09 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXHP | New Construction | Humidification | 0 | 0
CZ09 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXHP | New Construction | Water Systems | 0 | 243189.33
CZ09 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ09 | cDXHP | New Construction | Generators | 0 | 0
CZ09 | cDXHP | New Construction | Total End Uses | 739029.94 | 388891.27
CZ10 | cDXHP | New Construction | Heating | 12821.24 | 0
CZ10 | cDXHP | New Construction | Cooling | 192715.7 | 0
CZ10 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ10 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ10 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXHP | New Construction | Fans | 207977.14 | 0
CZ10 | cDXHP | New Construction | Pumps | 0 | 0
CZ10 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXHP | New Construction | Humidification | 0 | 0
CZ10 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXHP | New Construction | Water Systems | 0 | 240509.93
CZ10 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ10 | cDXHP | New Construction | Generators | 0 | 0
CZ10 | cDXHP | New Construction | Total End Uses | 797137.17 | 386211.87
CZ11 | cDXHP | New Construction | Heating | 28851.88 | 0
CZ11 | cDXHP | New Construction | Cooling | 200810.6 | 0
CZ11 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ11 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ11 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXHP | New Construction | Fans | 212326.95 | 0
CZ11 | cDXHP | New Construction | Pumps | 0 | 0
CZ11 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXHP | New Construction | Humidification | 0 | 0
CZ11 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXHP | New Construction | Water Systems | 0 | 245369.54
CZ11 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ11 | cDXHP | New Construction | Generators | 0 | 0
CZ11 | cDXHP | New Construction | Total End Uses | 825612.52 | 391071.49
CZ12 | cDXHP | New Construction | Heating | 26050.52 | 0
CZ12 | cDXHP | New Construction | Cooling | 168662.61 | 0
CZ12 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ12 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ12 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXHP | New Construction | Fans | 202824.52 | 0
CZ12 | cDXHP | New Construction | Pumps | 0 | 0
CZ12 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXHP | New Construction | Humidification | 0 | 0
CZ12 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXHP | New Construction | Water Systems | 0 | 252723.44
CZ12 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ12 | cDXHP | New Construction | Generators | 0 | 0
CZ12 | cDXHP | New Construction | Total End Uses | 781160.75 | 398425.39
CZ13 | cDXHP | New Construction | Heating | 20779.27 | 0
CZ13 | cDXHP | New Construction | Cooling | 223712.64 | 0
CZ13 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ13 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ13 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXHP | New Construction | Fans | 214472.03 | 0
CZ13 | cDXHP | New Construction | Pumps | 0 | 0
CZ13 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXHP | New Construction | Humidification | 0 | 0
CZ13 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXHP | New Construction | Water Systems | 0 | 238160.37
CZ13 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ13 | cDXHP | New Construction | Generators | 0 | 0
CZ13 | cDXHP | New Construction | Total End Uses | 842587.04 | 383862.31
CZ14 | cDXHP | New Construction | Heating | 13138.49 | 0
CZ14 | cDXHP | New Construction | Cooling | 281720.49 | 0
CZ14 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ14 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ14 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXHP | New Construction | Fans | 232973.32 | 0
CZ14 | cDXHP | New Construction | Pumps | 0 | 0
CZ14 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXHP | New Construction | Humidification | 0 | 0
CZ14 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXHP | New Construction | Water Systems | 0 | 225423.23
CZ14 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ14 | cDXHP | New Construction | Generators | 0 | 0
CZ14 | cDXHP | New Construction | Total End Uses | 911455.39 | 371125.18
CZ15 | cDXHP | New Construction | Heating | 4667.98 | 0
CZ15 | cDXHP | New Construction | Cooling | 379508.15 | 0
CZ15 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ15 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ15 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXHP | New Construction | Fans | 223727.89 | 0
CZ15 | cDXHP | New Construction | Pumps | 0 | 0
CZ15 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXHP | New Construction | Humidification | 0 | 0
CZ15 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXHP | New Construction | Water Systems | 0 | 200031.37
CZ15 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ15 | cDXHP | New Construction | Generators | 0 | 0
CZ15 | cDXHP | New Construction | Total End Uses | 991527.12 | 345733.32
CZ16 | cDXHP | New Construction | Heating | 45040.65 | 2.82
CZ16 | cDXHP | New Construction | Cooling | 184793.97 | 0
CZ16 | cDXHP | New Construction | Interior Lighting | 103398.36 | 0
CZ16 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXHP | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ16 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXHP | New Construction | Fans | 241506.09 | 0
CZ16 | cDXHP | New Construction | Pumps | 0 | 0
CZ16 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXHP | New Construction | Humidification | 0 | 0
CZ16 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXHP | New Construction | Water Systems | 0 | 266818.75
CZ16 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ16 | cDXHP | New Construction | Generators | 0 | 0
CZ16 | cDXHP | New Construction | Total End Uses | 854963.8 | 412523.51
CZ01 | cDXOH | Existing | Heating | 0 | 0
CZ01 | cDXOH | Existing | Cooling | 26365.43 | 0
CZ01 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ01 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ01 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXOH | Existing | Fans | 247711.04 | 0
CZ01 | cDXOH | Existing | Pumps | 0 | 0
CZ01 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ01 | cDXOH | Existing | Humidification | 0 | 0
CZ01 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ01 | cDXOH | Existing | Water Systems | 0 | 297561.96
CZ01 | cDXOH | Existing | Refrigeration | 0 | 0
CZ01 | cDXOH | Existing | Generators | 0 | 0
CZ01 | cDXOH | Existing | Total End Uses | 771018.23 | 443263.9
CZ02 | cDXOH | Existing | Heating | 0 | 0.03
CZ02 | cDXOH | Existing | Cooling | 114239.72 | 0
CZ02 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ02 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ02 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXOH | Existing | Fans | 278147.74 | 0
CZ02 | cDXOH | Existing | Pumps | 0 | 0
CZ02 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ02 | cDXOH | Existing | Humidification | 0 | 0
CZ02 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ02 | cDXOH | Existing | Water Systems | 0 | 273016.7
CZ02 | cDXOH | Existing | Refrigeration | 0 | 0
CZ02 | cDXOH | Existing | Generators | 0 | 0
CZ02 | cDXOH | Existing | Total End Uses | 889329.21 | 418718.67
CZ03 | cDXOH | Existing | Heating | 0 | 0
CZ03 | cDXOH | Existing | Cooling | 78440.21 | 0
CZ03 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ03 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ03 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXOH | Existing | Fans | 265146.6 | 0
CZ03 | cDXOH | Existing | Pumps | 0 | 0
CZ03 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ03 | cDXOH | Existing | Humidification | 0 | 0
CZ03 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ03 | cDXOH | Existing | Water Systems | 0 | 272177.94
CZ03 | cDXOH | Existing | Refrigeration | 0 | 0
CZ03 | cDXOH | Existing | Generators | 0 | 0
CZ03 | cDXOH | Existing | Total End Uses | 840528.57 | 417879.89
CZ04 | cDXOH | Existing | Heating | 0 | 0
CZ04 | cDXOH | Existing | Cooling | 137624.53 | 0
CZ04 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ04 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ04 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXOH | Existing | Fans | 279587.76 | 0
CZ04 | cDXOH | Existing | Pumps | 0 | 0
CZ04 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ04 | cDXOH | Existing | Humidification | 0 | 0
CZ04 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ04 | cDXOH | Existing | Water Systems | 0 | 262555.9
CZ04 | cDXOH | Existing | Refrigeration | 0 | 0
CZ04 | cDXOH | Existing | Generators | 0 | 0
CZ04 | cDXOH | Existing | Total End Uses | 914154.04 | 408257.84
CZ05 | cDXOH | Existing | Heating | 0 | 0
CZ05 | cDXOH | Existing | Cooling | 94679.28 | 0
CZ05 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ05 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ05 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXOH | Existing | Fans | 263071.13 | 0
CZ05 | cDXOH | Existing | Pumps | 0 | 0
CZ05 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ05 | cDXOH | Existing | Humidification | 0 | 0
CZ05 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ05 | cDXOH | Existing | Water Systems | 0 | 272191.34
CZ05 | cDXOH | Existing | Refrigeration | 0 | 0
CZ05 | cDXOH | Existing | Generators | 0 | 0
CZ05 | cDXOH | Existing | Total End Uses | 854692.16 | 417893.29
CZ06 | cDXOH | Existing | Heating | 0 | 0
CZ06 | cDXOH | Existing | Cooling | 149195.03 | 0
CZ06 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ06 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ06 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXOH | Existing | Fans | 276168.04 | 0
CZ06 | cDXOH | Existing | Pumps | 0 | 0
CZ06 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ06 | cDXOH | Existing | Humidification | 0 | 0
CZ06 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ06 | cDXOH | Existing | Water Systems | 0 | 250745.82
CZ06 | cDXOH | Existing | Refrigeration | 0 | 0
CZ06 | cDXOH | Existing | Generators | 0 | 0
CZ06 | cDXOH | Existing | Total End Uses | 922304.81 | 396447.77
CZ07 | cDXOH | Existing | Heating | 0 | 0
CZ07 | cDXOH | Existing | Cooling | 163282.43 | 0
CZ07 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ07 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ07 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXOH | Existing | Fans | 273420.65 | 0
CZ07 | cDXOH | Existing | Pumps | 0 | 0
CZ07 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ07 | cDXOH | Existing | Humidification | 0 | 0
CZ07 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ07 | cDXOH | Existing | Water Systems | 0 | 247316.18
CZ07 | cDXOH | Existing | Refrigeration | 0 | 0
CZ07 | cDXOH | Existing | Generators | 0 | 0
CZ07 | cDXOH | Existing | Total End Uses | 933644.84 | 393018.13
CZ08 | cDXOH | Existing | Heating | 0 | 0
CZ08 | cDXOH | Existing | Cooling | 184389.76 | 0
CZ08 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ08 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ08 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXOH | Existing | Fans | 287091.25 | 0
CZ08 | cDXOH | Existing | Pumps | 0 | 0
CZ08 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ08 | cDXOH | Existing | Humidification | 0 | 0
CZ08 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ08 | cDXOH | Existing | Water Systems | 0 | 246920.58
CZ08 | cDXOH | Existing | Refrigeration | 0 | 0
CZ08 | cDXOH | Existing | Generators | 0 | 0
CZ08 | cDXOH | Existing | Total End Uses | 968422.76 | 392622.52
CZ09 | cDXOH | Existing | Heating | 0 | 0
CZ09 | cDXOH | Existing | Cooling | 211146.69 | 0
CZ09 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ09 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ09 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXOH | Existing | Fans | 302472.24 | 0
CZ09 | cDXOH | Existing | Pumps | 0 | 0
CZ09 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ09 | cDXOH | Existing | Humidification | 0 | 0
CZ09 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ09 | cDXOH | Existing | Water Systems | 0 | 243513.6
CZ09 | cDXOH | Existing | Refrigeration | 0 | 0
CZ09 | cDXOH | Existing | Generators | 0 | 0
CZ09 | cDXOH | Existing | Total End Uses | 1010560.67 | 389215.55
CZ10 | cDXOH | Existing | Heating | 0 | 0
CZ10 | cDXOH | Existing | Cooling | 245723.02 | 0
CZ10 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ10 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ10 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXOH | Existing | Fans | 296646.68 | 0
CZ10 | cDXOH | Existing | Pumps | 0 | 0
CZ10 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ10 | cDXOH | Existing | Humidification | 0 | 0
CZ10 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ10 | cDXOH | Existing | Water Systems | 0 | 240746.05
CZ10 | cDXOH | Existing | Refrigeration | 0 | 0
CZ10 | cDXOH | Existing | Generators | 0 | 0
CZ10 | cDXOH | Existing | Total End Uses | 1039311.45 | 386448
CZ11 | cDXOH | Existing | Heating | 0 | 0
CZ11 | cDXOH | Existing | Cooling | 264116.46 | 0
CZ11 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ11 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ11 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXOH | Existing | Fans | 331830.13 | 0
CZ11 | cDXOH | Existing | Pumps | 0 | 0
CZ11 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ11 | cDXOH | Existing | Humidification | 0 | 0
CZ11 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ11 | cDXOH | Existing | Water Systems | 0 | 245701.6
CZ11 | cDXOH | Existing | Refrigeration | 0 | 0
CZ11 | cDXOH | Existing | Generators | 0 | 0
CZ11 | cDXOH | Existing | Total End Uses | 1092888.34 | 391403.55
CZ12 | cDXOH | Existing | Heating | 0 | 0
CZ12 | cDXOH | Existing | Cooling | 220337.8 | 0
CZ12 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ12 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ12 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXOH | Existing | Fans | 303694.03 | 0
CZ12 | cDXOH | Existing | Pumps | 0 | 0
CZ12 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ12 | cDXOH | Existing | Humidification | 0 | 0
CZ12 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ12 | cDXOH | Existing | Water Systems | 0 | 253126.69
CZ12 | cDXOH | Existing | Refrigeration | 0 | 0
CZ12 | cDXOH | Existing | Generators | 0 | 0
CZ12 | cDXOH | Existing | Total End Uses | 1020973.58 | 398828.63
CZ13 | cDXOH | Existing | Heating | 0 | 0
CZ13 | cDXOH | Existing | Cooling | 296279.02 | 0
CZ13 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ13 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ13 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXOH | Existing | Fans | 332430.45 | 0
CZ13 | cDXOH | Existing | Pumps | 0 | 0
CZ13 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ13 | cDXOH | Existing | Humidification | 0 | 0
CZ13 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ13 | cDXOH | Existing | Water Systems | 0 | 238456.43
CZ13 | cDXOH | Existing | Refrigeration | 0 | 0
CZ13 | cDXOH | Existing | Generators | 0 | 0
CZ13 | cDXOH | Existing | Total End Uses | 1125651.22 | 384158.38
CZ14 | cDXOH | Existing | Heating | 0 | 0
CZ14 | cDXOH | Existing | Cooling | 367787.5 | 0
CZ14 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ14 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ14 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXOH | Existing | Fans | 359492.08 | 0
CZ14 | cDXOH | Existing | Pumps | 0 | 0
CZ14 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ14 | cDXOH | Existing | Humidification | 0 | 0
CZ14 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ14 | cDXOH | Existing | Water Systems | 0 | 225863.27
CZ14 | cDXOH | Existing | Refrigeration | 0 | 0
CZ14 | cDXOH | Existing | Generators | 0 | 0
CZ14 | cDXOH | Existing | Total End Uses | 1224221.34 | 371565.22
CZ15 | cDXOH | Existing | Heating | 0 | 0
CZ15 | cDXOH | Existing | Cooling | 496200.02 | 0
CZ15 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ15 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ15 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXOH | Existing | Fans | 351951.4 | 0
CZ15 | cDXOH | Existing | Pumps | 0 | 0
CZ15 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ15 | cDXOH | Existing | Humidification | 0 | 0
CZ15 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ15 | cDXOH | Existing | Water Systems | 0 | 200447.14
CZ15 | cDXOH | Existing | Refrigeration | 0 | 0
CZ15 | cDXOH | Existing | Generators | 0 | 0
CZ15 | cDXOH | Existing | Total End Uses | 1345093.16 | 346149.09
CZ16 | cDXOH | Existing | Heating | 0 | 35.56
CZ16 | cDXOH | Existing | Cooling | 234696.43 | 0
CZ16 | cDXOH | Existing | Interior Lighting | 216717.02 | 0
CZ16 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXOH | Existing | Interior Equipment | 280224.73 | 145701.95
CZ16 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXOH | Existing | Fans | 363430.95 | 0
CZ16 | cDXOH | Existing | Pumps | 0 | 0
CZ16 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ16 | cDXOH | Existing | Humidification | 0 | 0
CZ16 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ16 | cDXOH | Existing | Water Systems | 0 | 267250.68
CZ16 | cDXOH | Existing | Refrigeration | 0 | 0
CZ16 | cDXOH | Existing | Generators | 0 | 0
CZ16 | cDXOH | Existing | Total End Uses | 1095069.13 | 412988.18
CZ01 | cDXOH | New Construction | Heating | 0 | 0
CZ01 | cDXOH | New Construction | Cooling | 21486.5 | 0
CZ01 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ01 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ01 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXOH | New Construction | Fans | 180862.48 | 0
CZ01 | cDXOH | New Construction | Pumps | 0 | 0
CZ01 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXOH | New Construction | Humidification | 0 | 0
CZ01 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXOH | New Construction | Water Systems | 0 | 297299.76
CZ01 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ01 | cDXOH | New Construction | Generators | 0 | 0
CZ01 | cDXOH | New Construction | Total End Uses | 585972.07 | 443001.7
CZ02 | cDXOH | New Construction | Heating | 0 | 0
CZ02 | cDXOH | New Construction | Cooling | 86269.06 | 0
CZ02 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ02 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ02 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXOH | New Construction | Fans | 194421.44 | 0
CZ02 | cDXOH | New Construction | Pumps | 0 | 0
CZ02 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXOH | New Construction | Humidification | 0 | 0
CZ02 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXOH | New Construction | Water Systems | 0 | 272725.66
CZ02 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ02 | cDXOH | New Construction | Generators | 0 | 0
CZ02 | cDXOH | New Construction | Total End Uses | 664313.6 | 418427.61
CZ03 | cDXOH | New Construction | Heating | 0 | 0
CZ03 | cDXOH | New Construction | Cooling | 59349.39 | 0
CZ03 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ03 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ03 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXOH | New Construction | Fans | 191673.9 | 0
CZ03 | cDXOH | New Construction | Pumps | 0 | 0
CZ03 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXOH | New Construction | Humidification | 0 | 0
CZ03 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXOH | New Construction | Water Systems | 0 | 271858.33
CZ03 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ03 | cDXOH | New Construction | Generators | 0 | 0
CZ03 | cDXOH | New Construction | Total End Uses | 634646.39 | 417560.28
CZ04 | cDXOH | New Construction | Heating | 0 | 0
CZ04 | cDXOH | New Construction | Cooling | 102697.3 | 0
CZ04 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ04 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ04 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXOH | New Construction | Fans | 194607.99 | 0
CZ04 | cDXOH | New Construction | Pumps | 0 | 0
CZ04 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXOH | New Construction | Humidification | 0 | 0
CZ04 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXOH | New Construction | Water Systems | 0 | 262176.88
CZ04 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ04 | cDXOH | New Construction | Generators | 0 | 0
CZ04 | cDXOH | New Construction | Total End Uses | 680928.38 | 407878.83
CZ05 | cDXOH | New Construction | Heating | 0 | 0
CZ05 | cDXOH | New Construction | Cooling | 70850.54 | 0
CZ05 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ05 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ05 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXOH | New Construction | Fans | 190277.85 | 0
CZ05 | cDXOH | New Construction | Pumps | 0 | 0
CZ05 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXOH | New Construction | Humidification | 0 | 0
CZ05 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXOH | New Construction | Water Systems | 0 | 271742.92
CZ05 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ05 | cDXOH | New Construction | Generators | 0 | 0
CZ05 | cDXOH | New Construction | Total End Uses | 644751.48 | 417444.86
CZ06 | cDXOH | New Construction | Heating | 0 | 0
CZ06 | cDXOH | New Construction | Cooling | 112894.6 | 0
CZ06 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ06 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ06 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXOH | New Construction | Fans | 202891.49 | 0
CZ06 | cDXOH | New Construction | Pumps | 0 | 0
CZ06 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXOH | New Construction | Humidification | 0 | 0
CZ06 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXOH | New Construction | Water Systems | 0 | 250349.56
CZ06 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ06 | cDXOH | New Construction | Generators | 0 | 0
CZ06 | cDXOH | New Construction | Total End Uses | 699409.18 | 396051.51
CZ07 | cDXOH | New Construction | Heating | 0 | 0
CZ07 | cDXOH | New Construction | Cooling | 122564 | 0
CZ07 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ07 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ07 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXOH | New Construction | Fans | 201239.43 | 0
CZ07 | cDXOH | New Construction | Pumps | 0 | 0
CZ07 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXOH | New Construction | Humidification | 0 | 0
CZ07 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXOH | New Construction | Water Systems | 0 | 246959.32
CZ07 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ07 | cDXOH | New Construction | Generators | 0 | 0
CZ07 | cDXOH | New Construction | Total End Uses | 707426.53 | 392661.27
CZ08 | cDXOH | New Construction | Heating | 0 | 0
CZ08 | cDXOH | New Construction | Cooling | 139356.42 | 0
CZ08 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ08 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ08 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXOH | New Construction | Fans | 207314.48 | 0
CZ08 | cDXOH | New Construction | Pumps | 0 | 0
CZ08 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXOH | New Construction | Humidification | 0 | 0
CZ08 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXOH | New Construction | Water Systems | 0 | 246590.49
CZ08 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ08 | cDXOH | New Construction | Generators | 0 | 0
CZ08 | cDXOH | New Construction | Total End Uses | 730294 | 392292.44
CZ09 | cDXOH | New Construction | Heating | 0 | 0
CZ09 | cDXOH | New Construction | Cooling | 152538.7 | 0
CZ09 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ09 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ09 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXOH | New Construction | Fans | 199180.12 | 0
CZ09 | cDXOH | New Construction | Pumps | 0 | 0
CZ09 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXOH | New Construction | Humidification | 0 | 0
CZ09 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXOH | New Construction | Water Systems | 0 | 243050.67
CZ09 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ09 | cDXOH | New Construction | Generators | 0 | 0
CZ09 | cDXOH | New Construction | Total End Uses | 735341.91 | 388752.62
CZ10 | cDXOH | New Construction | Heating | 0 | 0
CZ10 | cDXOH | New Construction | Cooling | 190546.21 | 0
CZ10 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ10 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ10 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXOH | New Construction | Fans | 208031.38 | 0
CZ10 | cDXOH | New Construction | Pumps | 0 | 0
CZ10 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXOH | New Construction | Humidification | 0 | 0
CZ10 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXOH | New Construction | Water Systems | 0 | 240314.23
CZ10 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ10 | cDXOH | New Construction | Generators | 0 | 0
CZ10 | cDXOH | New Construction | Total End Uses | 782200.69 | 386016.18
CZ11 | cDXOH | New Construction | Heating | 0 | 0
CZ11 | cDXOH | New Construction | Cooling | 197454.29 | 0
CZ11 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ11 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ11 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXOH | New Construction | Fans | 213429.32 | 0
CZ11 | cDXOH | New Construction | Pumps | 0 | 0
CZ11 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXOH | New Construction | Humidification | 0 | 0
CZ11 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXOH | New Construction | Water Systems | 0 | 245323.13
CZ11 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ11 | cDXOH | New Construction | Generators | 0 | 0
CZ11 | cDXOH | New Construction | Total End Uses | 794506.71 | 391025.07
CZ12 | cDXOH | New Construction | Heating | 0 | 0
CZ12 | cDXOH | New Construction | Cooling | 165841.51 | 0
CZ12 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ12 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ12 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXOH | New Construction | Fans | 203618.39 | 0
CZ12 | cDXOH | New Construction | Pumps | 0 | 0
CZ12 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXOH | New Construction | Humidification | 0 | 0
CZ12 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXOH | New Construction | Water Systems | 0 | 252760.46
CZ12 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ12 | cDXOH | New Construction | Generators | 0 | 0
CZ12 | cDXOH | New Construction | Total End Uses | 753082.99 | 398462.41
CZ13 | cDXOH | New Construction | Heating | 0 | 0
CZ13 | cDXOH | New Construction | Cooling | 221470.24 | 0
CZ13 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ13 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ13 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXOH | New Construction | Fans | 215214.34 | 0
CZ13 | cDXOH | New Construction | Pumps | 0 | 0
CZ13 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXOH | New Construction | Humidification | 0 | 0
CZ13 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXOH | New Construction | Water Systems | 0 | 237997.8
CZ13 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ13 | cDXOH | New Construction | Generators | 0 | 0
CZ13 | cDXOH | New Construction | Total End Uses | 820307.67 | 383699.75
CZ14 | cDXOH | New Construction | Heating | 0 | 0
CZ14 | cDXOH | New Construction | Cooling | 278953.25 | 0
CZ14 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ14 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ14 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXOH | New Construction | Fans | 233142.03 | 0
CZ14 | cDXOH | New Construction | Pumps | 0 | 0
CZ14 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXOH | New Construction | Humidification | 0 | 0
CZ14 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXOH | New Construction | Water Systems | 0 | 225445.27
CZ14 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ14 | cDXOH | New Construction | Generators | 0 | 0
CZ14 | cDXOH | New Construction | Total End Uses | 895718.37 | 371147.21
CZ15 | cDXOH | New Construction | Heating | 0 | 0
CZ15 | cDXOH | New Construction | Cooling | 377648.16 | 0
CZ15 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ15 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ15 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXOH | New Construction | Fans | 223760.43 | 0
CZ15 | cDXOH | New Construction | Pumps | 0 | 0
CZ15 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXOH | New Construction | Humidification | 0 | 0
CZ15 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXOH | New Construction | Water Systems | 0 | 200051.49
CZ15 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ15 | cDXOH | New Construction | Generators | 0 | 0
CZ15 | cDXOH | New Construction | Total End Uses | 985031.69 | 345753.43
CZ16 | cDXOH | New Construction | Heating | 0 | 2.83
CZ16 | cDXOH | New Construction | Cooling | 180357.65 | 0
CZ16 | cDXOH | New Construction | Interior Lighting | 103398.36 | 0
CZ16 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXOH | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ16 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXOH | New Construction | Fans | 246026.24 | 0
CZ16 | cDXOH | New Construction | Pumps | 0 | 0
CZ16 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXOH | New Construction | Humidification | 0 | 0
CZ16 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXOH | New Construction | Water Systems | 0 | 266969.5
CZ16 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ16 | cDXOH | New Construction | Generators | 0 | 0
CZ16 | cDXOH | New Construction | Total End Uses | 810006.98 | 412674.28
CZ01 | cPVVG | Existing | Heating | 0 | 268532.33
CZ01 | cPVVG | Existing | Cooling | 28110.16 | 0
CZ01 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ01 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ01 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ01 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ01 | cPVVG | Existing | Fans | 109813.65 | 0
CZ01 | cPVVG | Existing | Pumps | 0 | 0
CZ01 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ01 | cPVVG | Existing | Humidification | 0 | 0
CZ01 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ01 | cPVVG | Existing | Water Systems | 0 | 297521.34
CZ01 | cPVVG | Existing | Refrigeration | 0 | 0
CZ01 | cPVVG | Existing | Generators | 0 | 0
CZ01 | cPVVG | Existing | Total End Uses | 634865.56 | 711755.62
CZ02 | cPVVG | Existing | Heating | 0 | 148496.79
CZ02 | cPVVG | Existing | Cooling | 112545.13 | 0
CZ02 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ02 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ02 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ02 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ02 | cPVVG | Existing | Fans | 138605.08 | 0
CZ02 | cPVVG | Existing | Pumps | 0 | 0
CZ02 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ02 | cPVVG | Existing | Humidification | 0 | 0
CZ02 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ02 | cPVVG | Existing | Water Systems | 0 | 273002.76
CZ02 | cPVVG | Existing | Refrigeration | 0 | 0
CZ02 | cPVVG | Existing | Generators | 0 | 0
CZ02 | cPVVG | Existing | Total End Uses | 748091.97 | 567201.5
CZ03 | cPVVG | Existing | Heating | 0 | 94810.78
CZ03 | cPVVG | Existing | Cooling | 81160.9 | 0
CZ03 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ03 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ03 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ03 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ03 | cPVVG | Existing | Fans | 128019.28 | 0
CZ03 | cPVVG | Existing | Pumps | 0 | 0
CZ03 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ03 | cPVVG | Existing | Humidification | 0 | 0
CZ03 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ03 | cPVVG | Existing | Water Systems | 0 | 272187.2
CZ03 | cPVVG | Existing | Refrigeration | 0 | 0
CZ03 | cPVVG | Existing | Generators | 0 | 0
CZ03 | cPVVG | Existing | Total End Uses | 706121.93 | 512699.92
CZ04 | cPVVG | Existing | Heating | 0 | 84162.43
CZ04 | cPVVG | Existing | Cooling | 134964.23 | 0
CZ04 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ04 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ04 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ04 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ04 | cPVVG | Existing | Fans | 143093.82 | 0
CZ04 | cPVVG | Existing | Pumps | 0 | 0
CZ04 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ04 | cPVVG | Existing | Humidification | 0 | 0
CZ04 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ04 | cPVVG | Existing | Water Systems | 0 | 262542.14
CZ04 | cPVVG | Existing | Refrigeration | 0 | 0
CZ04 | cPVVG | Existing | Generators | 0 | 0
CZ04 | cPVVG | Existing | Total End Uses | 774999.8 | 492406.51
CZ05 | cPVVG | Existing | Heating | 0 | 84369.59
CZ05 | cPVVG | Existing | Cooling | 95802.44 | 0
CZ05 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ05 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ05 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ05 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ05 | cPVVG | Existing | Fans | 131739.39 | 0
CZ05 | cPVVG | Existing | Pumps | 0 | 0
CZ05 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ05 | cPVVG | Existing | Humidification | 0 | 0
CZ05 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ05 | cPVVG | Existing | Water Systems | 0 | 272213.51
CZ05 | cPVVG | Existing | Refrigeration | 0 | 0
CZ05 | cPVVG | Existing | Generators | 0 | 0
CZ05 | cPVVG | Existing | Total End Uses | 724483.58 | 502285.05
CZ06 | cPVVG | Existing | Heating | 0 | 22373.79
CZ06 | cPVVG | Existing | Cooling | 150100.68 | 0
CZ06 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ06 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ06 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ06 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ06 | cPVVG | Existing | Fans | 147508.66 | 0
CZ06 | cPVVG | Existing | Pumps | 0 | 0
CZ06 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ06 | cPVVG | Existing | Humidification | 0 | 0
CZ06 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ06 | cPVVG | Existing | Water Systems | 0 | 250746.44
CZ06 | cPVVG | Existing | Refrigeration | 0 | 0
CZ06 | cPVVG | Existing | Generators | 0 | 0
CZ06 | cPVVG | Existing | Total End Uses | 794551.09 | 418822.18
CZ07 | cPVVG | Existing | Heating | 0 | 21651.03
CZ07 | cPVVG | Existing | Cooling | 159408.78 | 0
CZ07 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ07 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ07 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ07 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ07 | cPVVG | Existing | Fans | 146413.04 | 0
CZ07 | cPVVG | Existing | Pumps | 0 | 0
CZ07 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ07 | cPVVG | Existing | Humidification | 0 | 0
CZ07 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ07 | cPVVG | Existing | Water Systems | 0 | 247355.35
CZ07 | cPVVG | Existing | Refrigeration | 0 | 0
CZ07 | cPVVG | Existing | Generators | 0 | 0
CZ07 | cPVVG | Existing | Total End Uses | 802763.57 | 414708.33
CZ08 | cPVVG | Existing | Heating | 0 | 30793.21
CZ08 | cPVVG | Existing | Cooling | 180286.94 | 0
CZ08 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ08 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ08 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ08 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ08 | cPVVG | Existing | Fans | 153680.06 | 0
CZ08 | cPVVG | Existing | Pumps | 0 | 0
CZ08 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ08 | cPVVG | Existing | Humidification | 0 | 0
CZ08 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ08 | cPVVG | Existing | Water Systems | 0 | 246943.28
CZ08 | cPVVG | Existing | Refrigeration | 0 | 0
CZ08 | cPVVG | Existing | Generators | 0 | 0
CZ08 | cPVVG | Existing | Total End Uses | 830908.75 | 423438.43
CZ09 | cPVVG | Existing | Heating | 0 | 24291.81
CZ09 | cPVVG | Existing | Cooling | 203467.57 | 0
CZ09 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ09 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ09 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ09 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ09 | cPVVG | Existing | Fans | 165330.13 | 0
CZ09 | cPVVG | Existing | Pumps | 0 | 0
CZ09 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ09 | cPVVG | Existing | Humidification | 0 | 0
CZ09 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ09 | cPVVG | Existing | Water Systems | 0 | 243516.87
CZ09 | cPVVG | Existing | Refrigeration | 0 | 0
CZ09 | cPVVG | Existing | Generators | 0 | 0
CZ09 | cPVVG | Existing | Total End Uses | 865739.45 | 413510.63
CZ10 | cPVVG | Existing | Heating | 0 | 59931.01
CZ10 | cPVVG | Existing | Cooling | 236661.63 | 0
CZ10 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ10 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ10 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ10 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ10 | cPVVG | Existing | Fans | 163371.81 | 0
CZ10 | cPVVG | Existing | Pumps | 0 | 0
CZ10 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ10 | cPVVG | Existing | Humidification | 0 | 0
CZ10 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ10 | cPVVG | Existing | Water Systems | 0 | 240777.35
CZ10 | cPVVG | Existing | Refrigeration | 0 | 0
CZ10 | cPVVG | Existing | Generators | 0 | 0
CZ10 | cPVVG | Existing | Total End Uses | 896975.19 | 446410.3
CZ11 | cPVVG | Existing | Heating | 0 | 148540.59
CZ11 | cPVVG | Existing | Cooling | 252785.37 | 0
CZ11 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ11 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ11 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ11 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ11 | cPVVG | Existing | Fans | 180775.43 | 0
CZ11 | cPVVG | Existing | Pumps | 0 | 0
CZ11 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ11 | cPVVG | Existing | Humidification | 0 | 0
CZ11 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ11 | cPVVG | Existing | Water Systems | 0 | 245693.03
CZ11 | cPVVG | Existing | Refrigeration | 0 | 0
CZ11 | cPVVG | Existing | Generators | 0 | 0
CZ11 | cPVVG | Existing | Total End Uses | 930502.55 | 539935.57
CZ12 | cPVVG | Existing | Heating | 0 | 129210.97
CZ12 | cPVVG | Existing | Cooling | 212564.28 | 0
CZ12 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ12 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ12 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ12 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ12 | cPVVG | Existing | Fans | 163257.51 | 0
CZ12 | cPVVG | Existing | Pumps | 0 | 0
CZ12 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ12 | cPVVG | Existing | Humidification | 0 | 0
CZ12 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ12 | cPVVG | Existing | Water Systems | 0 | 253151.21
CZ12 | cPVVG | Existing | Refrigeration | 0 | 0
CZ12 | cPVVG | Existing | Generators | 0 | 0
CZ12 | cPVVG | Existing | Total End Uses | 872763.54 | 528064.12
CZ13 | cPVVG | Existing | Heating | 0 | 102584.28
CZ13 | cPVVG | Existing | Cooling | 284130.33 | 0
CZ13 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ13 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ13 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ13 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ13 | cPVVG | Existing | Fans | 184907.99 | 0
CZ13 | cPVVG | Existing | Pumps | 0 | 0
CZ13 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ13 | cPVVG | Existing | Humidification | 0 | 0
CZ13 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ13 | cPVVG | Existing | Water Systems | 0 | 238454.76
CZ13 | cPVVG | Existing | Refrigeration | 0 | 0
CZ13 | cPVVG | Existing | Generators | 0 | 0
CZ13 | cPVVG | Existing | Total End Uses | 965980.07 | 486741
CZ14 | cPVVG | Existing | Heating | 0 | 63411.57
CZ14 | cPVVG | Existing | Cooling | 349207.19 | 0
CZ14 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ14 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ14 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ14 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ14 | cPVVG | Existing | Fans | 207034.22 | 0
CZ14 | cPVVG | Existing | Pumps | 0 | 0
CZ14 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ14 | cPVVG | Existing | Humidification | 0 | 0
CZ14 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ14 | cPVVG | Existing | Water Systems | 0 | 225864.05
CZ14 | cPVVG | Existing | Refrigeration | 0 | 0
CZ14 | cPVVG | Existing | Generators | 0 | 0
CZ14 | cPVVG | Existing | Total End Uses | 1053183.16 | 434977.56
CZ15 | cPVVG | Existing | Heating | 0 | 21952.87
CZ15 | cPVVG | Existing | Cooling | 475036.82 | 0
CZ15 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ15 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ15 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ15 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ15 | cPVVG | Existing | Fans | 217407.33 | 0
CZ15 | cPVVG | Existing | Pumps | 0 | 0
CZ15 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ15 | cPVVG | Existing | Humidification | 0 | 0
CZ15 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ15 | cPVVG | Existing | Water Systems | 0 | 200438.34
CZ15 | cPVVG | Existing | Refrigeration | 0 | 0
CZ15 | cPVVG | Existing | Generators | 0 | 0
CZ15 | cPVVG | Existing | Total End Uses | 1189385.9 | 368093.15
CZ16 | cPVVG | Existing | Heating | 0 | 196126.91
CZ16 | cPVVG | Existing | Cooling | 224758.58 | 0
CZ16 | cPVVG | Existing | Interior Lighting | 216717.02 | 0
CZ16 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ16 | cPVVG | Existing | Interior Equipment | 280224.73 | 145701.95
CZ16 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ16 | cPVVG | Existing | Fans | 195675.12 | 0
CZ16 | cPVVG | Existing | Pumps | 0 | 0
CZ16 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ16 | cPVVG | Existing | Humidification | 0 | 0
CZ16 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ16 | cPVVG | Existing | Water Systems | 0 | 267247.63
CZ16 | cPVVG | Existing | Refrigeration | 0 | 0
CZ16 | cPVVG | Existing | Generators | 0 | 0
CZ16 | cPVVG | Existing | Total End Uses | 917375.45 | 609076.48
CZ01 | cPVVG | New Construction | Heating | 0 | 293689.35
CZ01 | cPVVG | New Construction | Cooling | 23754.59 | 0
CZ01 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ01 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ01 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ01 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ01 | cPVVG | New Construction | Fans | 86768.22 | 0
CZ01 | cPVVG | New Construction | Pumps | 0 | 0
CZ01 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ01 | cPVVG | New Construction | Humidification | 0 | 0
CZ01 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ01 | cPVVG | New Construction | Water Systems | 0 | 297224.9
CZ01 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ01 | cPVVG | New Construction | Generators | 0 | 0
CZ01 | cPVVG | New Construction | Total End Uses | 494145.9 | 736616.2
CZ02 | cPVVG | New Construction | Heating | 0 | 156137.8
CZ02 | cPVVG | New Construction | Cooling | 87415.06 | 0
CZ02 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ02 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ02 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ02 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ02 | cPVVG | New Construction | Fans | 100346.84 | 0
CZ02 | cPVVG | New Construction | Pumps | 0 | 0
CZ02 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ02 | cPVVG | New Construction | Humidification | 0 | 0
CZ02 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ02 | cPVVG | New Construction | Water Systems | 0 | 272650.03
CZ02 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ02 | cPVVG | New Construction | Generators | 0 | 0
CZ02 | cPVVG | New Construction | Total End Uses | 571384.99 | 574489.77
CZ03 | cPVVG | New Construction | Heating | 0 | 115161.48
CZ03 | cPVVG | New Construction | Cooling | 61867.47 | 0
CZ03 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ03 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ03 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ03 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ03 | cPVVG | New Construction | Fans | 95303.06 | 0
CZ03 | cPVVG | New Construction | Pumps | 0 | 0
CZ03 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ03 | cPVVG | New Construction | Humidification | 0 | 0
CZ03 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ03 | cPVVG | New Construction | Water Systems | 0 | 271843.84
CZ03 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ03 | cPVVG | New Construction | Generators | 0 | 0
CZ03 | cPVVG | New Construction | Total End Uses | 540793.63 | 532707.27
CZ04 | cPVVG | New Construction | Heating | 0 | 96998.5
CZ04 | cPVVG | New Construction | Cooling | 102396.42 | 0
CZ04 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ04 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ04 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ04 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ04 | cPVVG | New Construction | Fans | 102472.52 | 0
CZ04 | cPVVG | New Construction | Pumps | 0 | 0
CZ04 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ04 | cPVVG | New Construction | Humidification | 0 | 0
CZ04 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ04 | cPVVG | New Construction | Water Systems | 0 | 262199.12
CZ04 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ04 | cPVVG | New Construction | Generators | 0 | 0
CZ04 | cPVVG | New Construction | Total End Uses | 588492.03 | 504899.56
CZ05 | cPVVG | New Construction | Heating | 0 | 108223
CZ05 | cPVVG | New Construction | Cooling | 72808.61 | 0
CZ05 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ05 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ05 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ05 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ05 | cPVVG | New Construction | Fans | 97192.01 | 0
CZ05 | cPVVG | New Construction | Pumps | 0 | 0
CZ05 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ05 | cPVVG | New Construction | Humidification | 0 | 0
CZ05 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ05 | cPVVG | New Construction | Water Systems | 0 | 271857.39
CZ05 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ05 | cPVVG | New Construction | Generators | 0 | 0
CZ05 | cPVVG | New Construction | Total End Uses | 553623.71 | 525782.33
CZ06 | cPVVG | New Construction | Heating | 0 | 34256.67
CZ06 | cPVVG | New Construction | Cooling | 112460.58 | 0
CZ06 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ06 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ06 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ06 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ06 | cPVVG | New Construction | Fans | 108684.22 | 0
CZ06 | cPVVG | New Construction | Pumps | 0 | 0
CZ06 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ06 | cPVVG | New Construction | Humidification | 0 | 0
CZ06 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ06 | cPVVG | New Construction | Water Systems | 0 | 250274.67
CZ06 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ06 | cPVVG | New Construction | Generators | 0 | 0
CZ06 | cPVVG | New Construction | Total End Uses | 604767.9 | 430233.29
CZ07 | cPVVG | New Construction | Heating | 0 | 32658.44
CZ07 | cPVVG | New Construction | Cooling | 119439.65 | 0
CZ07 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ07 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ07 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ07 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ07 | cPVVG | New Construction | Fans | 107763.02 | 0
CZ07 | cPVVG | New Construction | Pumps | 0 | 0
CZ07 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ07 | cPVVG | New Construction | Humidification | 0 | 0
CZ07 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ07 | cPVVG | New Construction | Water Systems | 0 | 246947.42
CZ07 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ07 | cPVVG | New Construction | Generators | 0 | 0
CZ07 | cPVVG | New Construction | Total End Uses | 610825.76 | 425307.81
CZ08 | cPVVG | New Construction | Heating | 0 | 44392.87
CZ08 | cPVVG | New Construction | Cooling | 137307.09 | 0
CZ08 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ08 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ08 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ08 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ08 | cPVVG | New Construction | Fans | 111960.52 | 0
CZ08 | cPVVG | New Construction | Pumps | 0 | 0
CZ08 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ08 | cPVVG | New Construction | Humidification | 0 | 0
CZ08 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ08 | cPVVG | New Construction | Water Systems | 0 | 246551.79
CZ08 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ08 | cPVVG | New Construction | Generators | 0 | 0
CZ08 | cPVVG | New Construction | Total End Uses | 632890.7 | 436646.61
CZ09 | cPVVG | New Construction | Heating | 0 | 30919.46
CZ09 | cPVVG | New Construction | Cooling | 148864.81 | 0
CZ09 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ09 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ09 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ09 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ09 | cPVVG | New Construction | Fans | 111644.88 | 0
CZ09 | cPVVG | New Construction | Pumps | 0 | 0
CZ09 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ09 | cPVVG | New Construction | Humidification | 0 | 0
CZ09 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ09 | cPVVG | New Construction | Water Systems | 0 | 243139.23
CZ09 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ09 | cPVVG | New Construction | Generators | 0 | 0
CZ09 | cPVVG | New Construction | Total End Uses | 644132.79 | 419760.64
CZ10 | cPVVG | New Construction | Heating | 0 | 68933.23
CZ10 | cPVVG | New Construction | Cooling | 186543.88 | 0
CZ10 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ10 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ10 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ10 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ10 | cPVVG | New Construction | Fans | 119014.05 | 0
CZ10 | cPVVG | New Construction | Pumps | 0 | 0
CZ10 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ10 | cPVVG | New Construction | Humidification | 0 | 0
CZ10 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ10 | cPVVG | New Construction | Water Systems | 0 | 240452.65
CZ10 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ10 | cPVVG | New Construction | Generators | 0 | 0
CZ10 | cPVVG | New Construction | Total End Uses | 689181.03 | 455087.82
CZ11 | cPVVG | New Construction | Heating | 0 | 150177.53
CZ11 | cPVVG | New Construction | Cooling | 193536.29 | 0
CZ11 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ11 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ11 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ11 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ11 | cPVVG | New Construction | Fans | 122969.09 | 0
CZ11 | cPVVG | New Construction | Pumps | 0 | 0
CZ11 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ11 | cPVVG | New Construction | Humidification | 0 | 0
CZ11 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ11 | cPVVG | New Construction | Water Systems | 0 | 245286.9
CZ11 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ11 | cPVVG | New Construction | Generators | 0 | 0
CZ11 | cPVVG | New Construction | Total End Uses | 700128.48 | 541166.37
CZ12 | cPVVG | New Construction | Heating | 0 | 133856.25
CZ12 | cPVVG | New Construction | Cooling | 163253.36 | 0
CZ12 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ12 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ12 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ12 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ12 | cPVVG | New Construction | Fans | 115079.67 | 0
CZ12 | cPVVG | New Construction | Pumps | 0 | 0
CZ12 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ12 | cPVVG | New Construction | Humidification | 0 | 0
CZ12 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ12 | cPVVG | New Construction | Water Systems | 0 | 252788.23
CZ12 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ12 | cPVVG | New Construction | Generators | 0 | 0
CZ12 | cPVVG | New Construction | Total End Uses | 661956.13 | 532346.42
CZ13 | cPVVG | New Construction | Heating | 0 | 110560.05
CZ13 | cPVVG | New Construction | Cooling | 216721.81 | 0
CZ13 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ13 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ13 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ13 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ13 | cPVVG | New Construction | Fans | 126482.84 | 0
CZ13 | cPVVG | New Construction | Pumps | 0 | 0
CZ13 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ13 | cPVVG | New Construction | Humidification | 0 | 0
CZ13 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ13 | cPVVG | New Construction | Water Systems | 0 | 238037.31
CZ13 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ13 | cPVVG | New Construction | Generators | 0 | 0
CZ13 | cPVVG | New Construction | Total End Uses | 726827.75 | 494299.3
CZ14 | cPVVG | New Construction | Heating | 0 | 73226.9
CZ14 | cPVVG | New Construction | Cooling | 271165.65 | 0
CZ14 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ14 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ14 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ14 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ14 | cPVVG | New Construction | Fans | 142720.08 | 0
CZ14 | cPVVG | New Construction | Pumps | 0 | 0
CZ14 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ14 | cPVVG | New Construction | Humidification | 0 | 0
CZ14 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ14 | cPVVG | New Construction | Water Systems | 0 | 225467.29
CZ14 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ14 | cPVVG | New Construction | Generators | 0 | 0
CZ14 | cPVVG | New Construction | Total End Uses | 797508.82 | 444396.13
CZ15 | cPVVG | New Construction | Heating | 0 | 28113.09
CZ15 | cPVVG | New Construction | Cooling | 368817.63 | 0
CZ15 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ15 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ15 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ15 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ15 | cPVVG | New Construction | Fans | 150642.3 | 0
CZ15 | cPVVG | New Construction | Pumps | 0 | 0
CZ15 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ15 | cPVVG | New Construction | Humidification | 0 | 0
CZ15 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ15 | cPVVG | New Construction | Water Systems | 0 | 200001.72
CZ15 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ15 | cPVVG | New Construction | Generators | 0 | 0
CZ15 | cPVVG | New Construction | Total End Uses | 903083.02 | 373816.75
CZ16 | cPVVG | New Construction | Heating | 0 | 195145.71
CZ16 | cPVVG | New Construction | Cooling | 176725.27 | 0
CZ16 | cPVVG | New Construction | Interior Lighting | 103398.36 | 0
CZ16 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ16 | cPVVG | New Construction | Interior Equipment | 280224.73 | 145701.95
CZ16 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ16 | cPVVG | New Construction | Fans | 137467.09 | 0
CZ16 | cPVVG | New Construction | Pumps | 0 | 0
CZ16 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ16 | cPVVG | New Construction | Humidification | 0 | 0
CZ16 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ16 | cPVVG | New Construction | Water Systems | 0 | 266810.86
CZ16 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ16 | cPVVG | New Construction | Generators | 0 | 0
CZ16 | cPVVG | New Construction | Total End Uses | 697815.45 | 607658.51

## Raw_endusebreakdownannual (hidden)
Vintage | Climate Zone | HVAC System | End Use | Electricity [kBtu] | Natural Gas [kBtu]
Existing | CZ01 | cAVVG | Heating | 0 | 303496.96
Existing | CZ01 | cAVVG | Cooling | 31162.39 | 0
Existing | CZ01 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ01 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ01 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ01 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ01 | cAVVG | Fans | 132265.77 | 0
Existing | CZ01 | cAVVG | Pumps | 559.71 | 0
Existing | CZ01 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ01 | cAVVG | Humidification | 0 | 0
Existing | CZ01 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ01 | cAVVG | Water Systems | 0 | 297531.38
Existing | CZ01 | cAVVG | Refrigeration | 0 | 0
Existing | CZ01 | cAVVG | Generators | 0 | 0
Existing | CZ01 | cAVVG | Total End Uses | 660929.61 | 746730.28
Existing | CZ02 | cAVVG | Heating | 0 | 180733.3
Existing | CZ02 | cAVVG | Cooling | 146394.15 | 0
Existing | CZ02 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ02 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ02 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ02 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ02 | cAVVG | Fans | 172938.16 | 0
Existing | CZ02 | cAVVG | Pumps | 3712.65 | 0
Existing | CZ02 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ02 | cAVVG | Humidification | 0 | 0
Existing | CZ02 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ02 | cAVVG | Water Systems | 0 | 273034.24
Existing | CZ02 | cAVVG | Refrigeration | 0 | 0
Existing | CZ02 | cAVVG | Generators | 0 | 0
Existing | CZ02 | cAVVG | Total End Uses | 819986.71 | 599469.48
Existing | CZ03 | cAVVG | Heating | 0 | 122305.83
Existing | CZ03 | cAVVG | Cooling | 101239.93 | 0
Existing | CZ03 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ03 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ03 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ03 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ03 | cAVVG | Fans | 131750.06 | 0
Existing | CZ03 | cAVVG | Pumps | 3001.37 | 0
Existing | CZ03 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ03 | cAVVG | Humidification | 0 | 0
Existing | CZ03 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ03 | cAVVG | Water Systems | 0 | 272203.9
Existing | CZ03 | cAVVG | Refrigeration | 0 | 0
Existing | CZ03 | cAVVG | Generators | 0 | 0
Existing | CZ03 | cAVVG | Total End Uses | 732933.11 | 540211.67
Existing | CZ04 | cAVVG | Heating | 0 | 114318.22
Existing | CZ04 | cAVVG | Cooling | 171867.77 | 0
Existing | CZ04 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ04 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ04 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ04 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ04 | cAVVG | Fans | 149141.1 | 0
Existing | CZ04 | cAVVG | Pumps | 4253.79 | 0
Existing | CZ04 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ04 | cAVVG | Humidification | 0 | 0
Existing | CZ04 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ04 | cAVVG | Water Systems | 0 | 262537.11
Existing | CZ04 | cAVVG | Refrigeration | 0 | 0
Existing | CZ04 | cAVVG | Generators | 0 | 0
Existing | CZ04 | cAVVG | Total End Uses | 822204.41 | 522557.28
Existing | CZ05 | cAVVG | Heating | 0 | 120049.64
Existing | CZ05 | cAVVG | Cooling | 117311.44 | 0
Existing | CZ05 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ05 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ05 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ05 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ05 | cAVVG | Fans | 129430.87 | 0
Existing | CZ05 | cAVVG | Pumps | 3566.04 | 0
Existing | CZ05 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ05 | cAVVG | Humidification | 0 | 0
Existing | CZ05 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ05 | cAVVG | Water Systems | 0 | 272214.06
Existing | CZ05 | cAVVG | Refrigeration | 0 | 0
Existing | CZ05 | cAVVG | Generators | 0 | 0
Existing | CZ05 | cAVVG | Total End Uses | 747250.1 | 537965.65
Existing | CZ06 | cAVVG | Heating | 0 | 38872.94
Existing | CZ06 | cAVVG | Cooling | 196185.64 | 0
Existing | CZ06 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ06 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ06 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ06 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ06 | cAVVG | Fans | 154517.95 | 0
Existing | CZ06 | cAVVG | Pumps | 6783.72 | 0
Existing | CZ06 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ06 | cAVVG | Humidification | 0 | 0
Existing | CZ06 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ06 | cAVVG | Water Systems | 0 | 250729.96
Existing | CZ06 | cAVVG | Refrigeration | 0 | 0
Existing | CZ06 | cAVVG | Generators | 0 | 0
Existing | CZ06 | cAVVG | Total End Uses | 854429.06 | 435304.85
Existing | CZ07 | cAVVG | Heating | 0 | 43302.27
Existing | CZ07 | cAVVG | Cooling | 213546.19 | 0
Existing | CZ07 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ07 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ07 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ07 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ07 | cAVVG | Fans | 155271.11 | 0
Existing | CZ07 | cAVVG | Pumps | 5951.33 | 0
Existing | CZ07 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ07 | cAVVG | Humidification | 0 | 0
Existing | CZ07 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ07 | cAVVG | Water Systems | 0 | 247338.69
Existing | CZ07 | cAVVG | Refrigeration | 0 | 0
Existing | CZ07 | cAVVG | Generators | 0 | 0
Existing | CZ07 | cAVVG | Total End Uses | 871710.39 | 436342.91
Existing | CZ08 | cAVVG | Heating | 0 | 55953.74
Existing | CZ08 | cAVVG | Cooling | 239947.54 | 0
Existing | CZ08 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ08 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ08 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ08 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ08 | cAVVG | Fans | 160200.06 | 0
Existing | CZ08 | cAVVG | Pumps | 6216.29 | 0
Existing | CZ08 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ08 | cAVVG | Humidification | 0 | 0
Existing | CZ08 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ08 | cAVVG | Water Systems | 0 | 246936.36
Existing | CZ08 | cAVVG | Refrigeration | 0 | 0
Existing | CZ08 | cAVVG | Generators | 0 | 0
Existing | CZ08 | cAVVG | Total End Uses | 903305.64 | 448592.05
Existing | CZ09 | cAVVG | Heating | 0 | 48492.74
Existing | CZ09 | cAVVG | Cooling | 271118.13 | 0
Existing | CZ09 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ09 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ09 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ09 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ09 | cAVVG | Fans | 180555.92 | 0
Existing | CZ09 | cAVVG | Pumps | 6618.83 | 0
Existing | CZ09 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ09 | cAVVG | Humidification | 0 | 0
Existing | CZ09 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ09 | cAVVG | Water Systems | 0 | 243521.92
Existing | CZ09 | cAVVG | Refrigeration | 0 | 0
Existing | CZ09 | cAVVG | Generators | 0 | 0
Existing | CZ09 | cAVVG | Total End Uses | 955234.63 | 437716.6
Existing | CZ10 | cAVVG | Heating | 0 | 91122.13
Existing | CZ10 | cAVVG | Cooling | 307385.46 | 0
Existing | CZ10 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ10 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ10 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ10 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ10 | cAVVG | Fans | 180172 | 0
Existing | CZ10 | cAVVG | Pumps | 6343.29 | 0
Existing | CZ10 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ10 | cAVVG | Humidification | 0 | 0
Existing | CZ10 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ10 | cAVVG | Water Systems | 0 | 240765.45
Existing | CZ10 | cAVVG | Refrigeration | 0 | 0
Existing | CZ10 | cAVVG | Generators | 0 | 0
Existing | CZ10 | cAVVG | Total End Uses | 990842.51 | 477589.53
Existing | CZ11 | cAVVG | Heating | 0 | 193991.3
Existing | CZ11 | cAVVG | Cooling | 323146.19 | 0
Existing | CZ11 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ11 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ11 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ11 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ11 | cAVVG | Fans | 200886.95 | 0
Existing | CZ11 | cAVVG | Pumps | 6109.65 | 0
Existing | CZ11 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ11 | cAVVG | Humidification | 0 | 0
Existing | CZ11 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ11 | cAVVG | Water Systems | 0 | 245678.21
Existing | CZ11 | cAVVG | Refrigeration | 0 | 0
Existing | CZ11 | cAVVG | Generators | 0 | 0
Existing | CZ11 | cAVVG | Total End Uses | 1027084.54 | 585371.45
Existing | CZ12 | cAVVG | Heating | 0 | 158825.05
Existing | CZ12 | cAVVG | Cooling | 274680.38 | 0
Existing | CZ12 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ12 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ12 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ12 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ12 | cAVVG | Fans | 204054.9 | 0
Existing | CZ12 | cAVVG | Pumps | 5849.97 | 0
Existing | CZ12 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ12 | cAVVG | Humidification | 0 | 0
Existing | CZ12 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ12 | cAVVG | Water Systems | 0 | 253125.34
Existing | CZ12 | cAVVG | Refrigeration | 0 | 0
Existing | CZ12 | cAVVG | Generators | 0 | 0
Existing | CZ12 | cAVVG | Total End Uses | 981527 | 557652.33
Existing | CZ13 | cAVVG | Heating | 0 | 137620.04
Existing | CZ13 | cAVVG | Cooling | 361932.82 | 0
Existing | CZ13 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ13 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ13 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ13 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ13 | cAVVG | Fans | 213020.18 | 0
Existing | CZ13 | cAVVG | Pumps | 7168.29 | 0
Existing | CZ13 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ13 | cAVVG | Humidification | 0 | 0
Existing | CZ13 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ13 | cAVVG | Water Systems | 0 | 238453.06
Existing | CZ13 | cAVVG | Refrigeration | 0 | 0
Existing | CZ13 | cAVVG | Generators | 0 | 0
Existing | CZ13 | cAVVG | Total End Uses | 1079063.04 | 521775.05
Existing | CZ14 | cAVVG | Heating | 0 | 104167.94
Existing | CZ14 | cAVVG | Cooling | 437490.84 | 0
Existing | CZ14 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ14 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ14 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ14 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ14 | cAVVG | Fans | 227132.76 | 0
Existing | CZ14 | cAVVG | Pumps | 6863.92 | 0
Existing | CZ14 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ14 | cAVVG | Humidification | 0 | 0
Existing | CZ14 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ14 | cAVVG | Water Systems | 0 | 225878.82
Existing | CZ14 | cAVVG | Refrigeration | 0 | 0
Existing | CZ14 | cAVVG | Generators | 0 | 0
Existing | CZ14 | cAVVG | Total End Uses | 1168429.27 | 475748.71
Existing | CZ15 | cAVVG | Heating | 0 | 52382.54
Existing | CZ15 | cAVVG | Cooling | 623702.82 | 0
Existing | CZ15 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ15 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ15 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ15 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ15 | cAVVG | Fans | 237678.99 | 0
Existing | CZ15 | cAVVG | Pumps | 10090.41 | 0
Existing | CZ15 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ15 | cAVVG | Humidification | 0 | 0
Existing | CZ15 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ15 | cAVVG | Water Systems | 0 | 200455.5
Existing | CZ15 | cAVVG | Refrigeration | 0 | 0
Existing | CZ15 | cAVVG | Generators | 0 | 0
Existing | CZ15 | cAVVG | Total End Uses | 1368413.97 | 398539.98
Existing | CZ16 | cAVVG | Heating | 0 | 235439.61
Existing | CZ16 | cAVVG | Cooling | 277046.46 | 0
Existing | CZ16 | cAVVG | Interior Lighting | 216717.02 | 0
Existing | CZ16 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ16 | cAVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ16 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ16 | cAVVG | Fans | 230774.5 | 0
Existing | CZ16 | cAVVG | Pumps | 6240.56 | 0
Existing | CZ16 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ16 | cAVVG | Humidification | 0 | 0
Existing | CZ16 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ16 | cAVVG | Water Systems | 0 | 267220.64
Existing | CZ16 | cAVVG | Refrigeration | 0 | 0
Existing | CZ16 | cAVVG | Generators | 0 | 0
Existing | CZ16 | cAVVG | Total End Uses | 1011003.27 | 648362.2
New Construction | CZ01 | cAVVG | Heating | 0 | 313791.1
New Construction | CZ01 | cAVVG | Cooling | 27402.13 | 0
New Construction | CZ01 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ01 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ01 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ01 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ01 | cAVVG | Fans | 121794.95 | 0
New Construction | CZ01 | cAVVG | Pumps | 500.43 | 0
New Construction | CZ01 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ01 | cAVVG | Humidification | 0 | 0
New Construction | CZ01 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ01 | cAVVG | Water Systems | 0 | 297261.09
New Construction | CZ01 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ01 | cAVVG | Generators | 0 | 0
New Construction | CZ01 | cAVVG | Total End Uses | 533320.61 | 756754.14
New Construction | CZ02 | cAVVG | Heating | 0 | 184521.17
New Construction | CZ02 | cAVVG | Cooling | 116908.95 | 0
New Construction | CZ02 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ02 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ02 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ02 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ02 | cAVVG | Fans | 141101.95 | 0
New Construction | CZ02 | cAVVG | Pumps | 2764.66 | 0
New Construction | CZ02 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ02 | cAVVG | Humidification | 0 | 0
New Construction | CZ02 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ02 | cAVVG | Water Systems | 0 | 272692.87
New Construction | CZ02 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ02 | cAVVG | Generators | 0 | 0
New Construction | CZ02 | cAVVG | Total End Uses | 644398.64 | 602915.99
New Construction | CZ03 | cAVVG | Heating | 0 | 129913.56
New Construction | CZ03 | cAVVG | Cooling | 82325.2 | 0
New Construction | CZ03 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ03 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ03 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ03 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ03 | cAVVG | Fans | 112100.05 | 0
New Construction | CZ03 | cAVVG | Pumps | 2319.6 | 0
New Construction | CZ03 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ03 | cAVVG | Humidification | 0 | 0
New Construction | CZ03 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ03 | cAVVG | Water Systems | 0 | 271787.89
New Construction | CZ03 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ03 | cAVVG | Generators | 0 | 0
New Construction | CZ03 | cAVVG | Total End Uses | 580367.95 | 547403.4
New Construction | CZ04 | cAVVG | Heating | 0 | 115810.85
New Construction | CZ04 | cAVVG | Cooling | 133099.57 | 0
New Construction | CZ04 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ04 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ04 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ04 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ04 | cAVVG | Fans | 121590.51 | 0
New Construction | CZ04 | cAVVG | Pumps | 3070.63 | 0
New Construction | CZ04 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ04 | cAVVG | Humidification | 0 | 0
New Construction | CZ04 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ04 | cAVVG | Water Systems | 0 | 262195.43
New Construction | CZ04 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ04 | cAVVG | Generators | 0 | 0
New Construction | CZ04 | cAVVG | Total End Uses | 641383.81 | 523708.23
New Construction | CZ05 | cAVVG | Heating | 0 | 129392.39
New Construction | CZ05 | cAVVG | Cooling | 94224.84 | 0
New Construction | CZ05 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ05 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ05 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ05 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ05 | cAVVG | Fans | 108853.93 | 0
New Construction | CZ05 | cAVVG | Pumps | 2763.68 | 0
New Construction | CZ05 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ05 | cAVVG | Humidification | 0 | 0
New Construction | CZ05 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ05 | cAVVG | Water Systems | 0 | 271875.46
New Construction | CZ05 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ05 | cAVVG | Generators | 0 | 0
New Construction | CZ05 | cAVVG | Total End Uses | 589465.54 | 546969.8
New Construction | CZ06 | cAVVG | Heating | 0 | 51417.29
New Construction | CZ06 | cAVVG | Cooling | 155515.31 | 0
New Construction | CZ06 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ06 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ06 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ06 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ06 | cAVVG | Fans | 126013.47 | 0
New Construction | CZ06 | cAVVG | Pumps | 5244.61 | 0
New Construction | CZ06 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ06 | cAVVG | Humidification | 0 | 0
New Construction | CZ06 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ06 | cAVVG | Water Systems | 0 | 250295.23
New Construction | CZ06 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ06 | cAVVG | Generators | 0 | 0
New Construction | CZ06 | cAVVG | Total End Uses | 670396.48 | 447414.47
New Construction | CZ07 | cAVVG | Heating | 0 | 55689.2
New Construction | CZ07 | cAVVG | Cooling | 169026.68 | 0
New Construction | CZ07 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ07 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ07 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ07 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ07 | cAVVG | Fans | 128241.94 | 0
New Construction | CZ07 | cAVVG | Pumps | 4427.72 | 0
New Construction | CZ07 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ07 | cAVVG | Humidification | 0 | 0
New Construction | CZ07 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ07 | cAVVG | Water Systems | 0 | 247014.52
New Construction | CZ07 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ07 | cAVVG | Generators | 0 | 0
New Construction | CZ07 | cAVVG | Total End Uses | 685319.43 | 448405.66
New Construction | CZ08 | cAVVG | Heating | 0 | 66073.28
New Construction | CZ08 | cAVVG | Cooling | 187936.59 | 0
New Construction | CZ08 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ08 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ08 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ08 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ08 | cAVVG | Fans | 129920.18 | 0
New Construction | CZ08 | cAVVG | Pumps | 4500.85 | 0
New Construction | CZ08 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ08 | cAVVG | Humidification | 0 | 0
New Construction | CZ08 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ08 | cAVVG | Water Systems | 0 | 246519.46
New Construction | CZ08 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ08 | cAVVG | Generators | 0 | 0
New Construction | CZ08 | cAVVG | Total End Uses | 705980.71 | 458294.68
New Construction | CZ09 | cAVVG | Heating | 0 | 55878.7
New Construction | CZ09 | cAVVG | Cooling | 200406.81 | 0
New Construction | CZ09 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ09 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ09 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ09 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ09 | cAVVG | Fans | 136176.08 | 0
New Construction | CZ09 | cAVVG | Pumps | 4427.31 | 0
New Construction | CZ09 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ09 | cAVVG | Humidification | 0 | 0
New Construction | CZ09 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ09 | cAVVG | Water Systems | 0 | 243182.03
New Construction | CZ09 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ09 | cAVVG | Generators | 0 | 0
New Construction | CZ09 | cAVVG | Total End Uses | 724633.29 | 444762.67
New Construction | CZ10 | cAVVG | Heating | 0 | 90234.72
New Construction | CZ10 | cAVVG | Cooling | 243905.65 | 0
New Construction | CZ10 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ10 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ10 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ10 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ10 | cAVVG | Fans | 139469.11 | 0
New Construction | CZ10 | cAVVG | Pumps | 4529.32 | 0
New Construction | CZ10 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ10 | cAVVG | Humidification | 0 | 0
New Construction | CZ10 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ10 | cAVVG | Water Systems | 0 | 240406.01
New Construction | CZ10 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ10 | cAVVG | Generators | 0 | 0
New Construction | CZ10 | cAVVG | Total End Uses | 771527.18 | 476342.68
New Construction | CZ11 | cAVVG | Heating | 0 | 168450.71
New Construction | CZ11 | cAVVG | Cooling | 249145.35 | 0
New Construction | CZ11 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ11 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ11 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ11 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ11 | cAVVG | Fans | 149419.27 | 0
New Construction | CZ11 | cAVVG | Pumps | 4005.45 | 0
New Construction | CZ11 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ11 | cAVVG | Humidification | 0 | 0
New Construction | CZ11 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ11 | cAVVG | Water Systems | 0 | 245396.42
New Construction | CZ11 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ11 | cAVVG | Generators | 0 | 0
New Construction | CZ11 | cAVVG | Total End Uses | 786193.17 | 559549.08
New Construction | CZ12 | cAVVG | Heating | 0 | 158419.48
New Construction | CZ12 | cAVVG | Cooling | 214062.05 | 0
New Construction | CZ12 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ12 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ12 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ12 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ12 | cAVVG | Fans | 156697.53 | 0
New Construction | CZ12 | cAVVG | Pumps | 4136.08 | 0
New Construction | CZ12 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ12 | cAVVG | Humidification | 0 | 0
New Construction | CZ12 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ12 | cAVVG | Water Systems | 0 | 252695.35
New Construction | CZ12 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ12 | cAVVG | Generators | 0 | 0
New Construction | CZ12 | cAVVG | Total End Uses | 758518.76 | 556816.78
New Construction | CZ13 | cAVVG | Heating | 0 | 128291.8
New Construction | CZ13 | cAVVG | Cooling | 278061.5 | 0
New Construction | CZ13 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ13 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ13 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ13 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ13 | cAVVG | Fans | 157428.4 | 0
New Construction | CZ13 | cAVVG | Pumps | 4732.85 | 0
New Construction | CZ13 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ13 | cAVVG | Humidification | 0 | 0
New Construction | CZ13 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ13 | cAVVG | Water Systems | 0 | 238116.62
New Construction | CZ13 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ13 | cAVVG | Generators | 0 | 0
New Construction | CZ13 | cAVVG | Total End Uses | 823845.85 | 512110.36
New Construction | CZ14 | cAVVG | Heating | 0 | 98450.48
New Construction | CZ14 | cAVVG | Cooling | 341489.42 | 0
New Construction | CZ14 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ14 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ14 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ14 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ14 | cAVVG | Fans | 165120.09 | 0
New Construction | CZ14 | cAVVG | Pumps | 4437.84 | 0
New Construction | CZ14 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ14 | cAVVG | Humidification | 0 | 0
New Construction | CZ14 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ14 | cAVVG | Water Systems | 0 | 225551.13
New Construction | CZ14 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ14 | cAVVG | Generators | 0 | 0
New Construction | CZ14 | cAVVG | Total End Uses | 894670.45 | 469703.56
New Construction | CZ15 | cAVVG | Heating | 0 | 60045.45
New Construction | CZ15 | cAVVG | Cooling | 494669.72 | 0
New Construction | CZ15 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ15 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ15 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ15 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ15 | cAVVG | Fans | 178131.74 | 0
New Construction | CZ15 | cAVVG | Pumps | 6736.05 | 0
New Construction | CZ15 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ15 | cAVVG | Humidification | 0 | 0
New Construction | CZ15 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ15 | cAVVG | Water Systems | 0 | 200099.32
New Construction | CZ15 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ15 | cAVVG | Generators | 0 | 0
New Construction | CZ15 | cAVVG | Total End Uses | 1063160.6 | 405846.71
New Construction | CZ16 | cAVVG | Heating | 0 | 220578.32
New Construction | CZ16 | cAVVG | Cooling | 218343.78 | 0
New Construction | CZ16 | cAVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ16 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ16 | cAVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ16 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ16 | cAVVG | Fans | 178244.48 | 0
New Construction | CZ16 | cAVVG | Pumps | 4413.77 | 0
New Construction | CZ16 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ16 | cAVVG | Humidification | 0 | 0
New Construction | CZ16 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ16 | cAVVG | Water Systems | 0 | 266918.67
New Construction | CZ16 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ16 | cAVVG | Generators | 0 | 0
New Construction | CZ16 | cAVVG | Total End Uses | 784625.12 | 633198.93
Existing | CZ01 | cDXGF | Heating | 0 | 183329.06
Existing | CZ01 | cDXGF | Cooling | 27363.16 | 0
Existing | CZ01 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ01 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ01 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXGF | Fans | 245806.77 | 0
Existing | CZ01 | cDXGF | Pumps | 0 | 0
Existing | CZ01 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ01 | cDXGF | Humidification | 0 | 0
Existing | CZ01 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ01 | cDXGF | Water Systems | 0 | 297524.36
Existing | CZ01 | cDXGF | Refrigeration | 0 | 0
Existing | CZ01 | cDXGF | Generators | 0 | 0
Existing | CZ01 | cDXGF | Total End Uses | 770111.68 | 626555.36
Existing | CZ02 | cDXGF | Heating | 0 | 101000.78
Existing | CZ02 | cDXGF | Cooling | 115331.88 | 0
Existing | CZ02 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ02 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ02 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXGF | Fans | 277304.94 | 0
Existing | CZ02 | cDXGF | Pumps | 0 | 0
Existing | CZ02 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ02 | cDXGF | Humidification | 0 | 0
Existing | CZ02 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ02 | cDXGF | Water Systems | 0 | 273013.46
Existing | CZ02 | cDXGF | Refrigeration | 0 | 0
Existing | CZ02 | cDXGF | Generators | 0 | 0
Existing | CZ02 | cDXGF | Total End Uses | 889578.57 | 519716.18
Existing | CZ03 | cDXGF | Heating | 0 | 59152.61
Existing | CZ03 | cDXGF | Cooling | 78928.82 | 0
Existing | CZ03 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ03 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ03 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXGF | Fans | 265024.82 | 0
Existing | CZ03 | cDXGF | Pumps | 0 | 0
Existing | CZ03 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ03 | cDXGF | Humidification | 0 | 0
Existing | CZ03 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ03 | cDXGF | Water Systems | 0 | 272138.93
Existing | CZ03 | cDXGF | Refrigeration | 0 | 0
Existing | CZ03 | cDXGF | Generators | 0 | 0
Existing | CZ03 | cDXGF | Total End Uses | 840895.39 | 476993.48
Existing | CZ04 | cDXGF | Heating | 0 | 52049.29
Existing | CZ04 | cDXGF | Cooling | 138187.61 | 0
Existing | CZ04 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ04 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ04 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXGF | Fans | 279566.05 | 0
Existing | CZ04 | cDXGF | Pumps | 0 | 0
Existing | CZ04 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ04 | cDXGF | Humidification | 0 | 0
Existing | CZ04 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ04 | cDXGF | Water Systems | 0 | 262527.05
Existing | CZ04 | cDXGF | Refrigeration | 0 | 0
Existing | CZ04 | cDXGF | Generators | 0 | 0
Existing | CZ04 | cDXGF | Total End Uses | 914695.41 | 460278.28
Existing | CZ05 | cDXGF | Heating | 0 | 53531.18
Existing | CZ05 | cDXGF | Cooling | 95501.65 | 0
Existing | CZ05 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ05 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ05 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXGF | Fans | 263023.74 | 0
Existing | CZ05 | cDXGF | Pumps | 0 | 0
Existing | CZ05 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ05 | cDXGF | Humidification | 0 | 0
Existing | CZ05 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ05 | cDXGF | Water Systems | 0 | 272209.89
Existing | CZ05 | cDXGF | Refrigeration | 0 | 0
Existing | CZ05 | cDXGF | Generators | 0 | 0
Existing | CZ05 | cDXGF | Total End Uses | 855467.14 | 471443.02
Existing | CZ06 | cDXGF | Heating | 0 | 11495.75
Existing | CZ06 | cDXGF | Cooling | 149358.86 | 0
Existing | CZ06 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ06 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ06 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXGF | Fans | 276226.02 | 0
Existing | CZ06 | cDXGF | Pumps | 0 | 0
Existing | CZ06 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ06 | cDXGF | Humidification | 0 | 0
Existing | CZ06 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ06 | cDXGF | Water Systems | 0 | 250734.03
Existing | CZ06 | cDXGF | Refrigeration | 0 | 0
Existing | CZ06 | cDXGF | Generators | 0 | 0
Existing | CZ06 | cDXGF | Total End Uses | 922526.64 | 407931.73
Existing | CZ07 | cDXGF | Heating | 0 | 11252.79
Existing | CZ07 | cDXGF | Cooling | 163438.53 | 0
Existing | CZ07 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ07 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ07 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXGF | Fans | 273440.9 | 0
Existing | CZ07 | cDXGF | Pumps | 0 | 0
Existing | CZ07 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ07 | cDXGF | Humidification | 0 | 0
Existing | CZ07 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ07 | cDXGF | Water Systems | 0 | 247317.93
Existing | CZ07 | cDXGF | Refrigeration | 0 | 0
Existing | CZ07 | cDXGF | Generators | 0 | 0
Existing | CZ07 | cDXGF | Total End Uses | 933821.18 | 404272.67
Existing | CZ08 | cDXGF | Heating | 0 | 17199.37
Existing | CZ08 | cDXGF | Cooling | 184673.4 | 0
Existing | CZ08 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ08 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ08 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXGF | Fans | 287124.2 | 0
Existing | CZ08 | cDXGF | Pumps | 0 | 0
Existing | CZ08 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ08 | cDXGF | Humidification | 0 | 0
Existing | CZ08 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ08 | cDXGF | Water Systems | 0 | 246912.73
Existing | CZ08 | cDXGF | Refrigeration | 0 | 0
Existing | CZ08 | cDXGF | Generators | 0 | 0
Existing | CZ08 | cDXGF | Total End Uses | 968739.35 | 409814.04
Existing | CZ09 | cDXGF | Heating | 0 | 12536.35
Existing | CZ09 | cDXGF | Cooling | 211373.37 | 0
Existing | CZ09 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ09 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ09 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXGF | Fans | 302536.47 | 0
Existing | CZ09 | cDXGF | Pumps | 0 | 0
Existing | CZ09 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ09 | cDXGF | Humidification | 0 | 0
Existing | CZ09 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ09 | cDXGF | Water Systems | 0 | 243529.23
Existing | CZ09 | cDXGF | Refrigeration | 0 | 0
Existing | CZ09 | cDXGF | Generators | 0 | 0
Existing | CZ09 | cDXGF | Total End Uses | 1010851.59 | 401767.53
Existing | CZ10 | cDXGF | Heating | 0 | 38913.97
Existing | CZ10 | cDXGF | Cooling | 246493.87 | 0
Existing | CZ10 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ10 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ10 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXGF | Fans | 296708.72 | 0
Existing | CZ10 | cDXGF | Pumps | 0 | 0
Existing | CZ10 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ10 | cDXGF | Humidification | 0 | 0
Existing | CZ10 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ10 | cDXGF | Water Systems | 0 | 240759.86
Existing | CZ10 | cDXGF | Refrigeration | 0 | 0
Existing | CZ10 | cDXGF | Generators | 0 | 0
Existing | CZ10 | cDXGF | Total End Uses | 1040144.33 | 425375.78
Existing | CZ11 | cDXGF | Heating | 0 | 100122.02
Existing | CZ11 | cDXGF | Cooling | 264994.18 | 0
Existing | CZ11 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ11 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ11 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXGF | Fans | 330097.07 | 0
Existing | CZ11 | cDXGF | Pumps | 0 | 0
Existing | CZ11 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ11 | cDXGF | Humidification | 0 | 0
Existing | CZ11 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ11 | cDXGF | Water Systems | 0 | 245697.89
Existing | CZ11 | cDXGF | Refrigeration | 0 | 0
Existing | CZ11 | cDXGF | Generators | 0 | 0
Existing | CZ11 | cDXGF | Total End Uses | 1092032.99 | 491521.85
Existing | CZ12 | cDXGF | Heating | 0 | 87843.02
Existing | CZ12 | cDXGF | Cooling | 221182.33 | 0
Existing | CZ12 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ12 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ12 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXGF | Fans | 302087.35 | 0
Existing | CZ12 | cDXGF | Pumps | 0 | 0
Existing | CZ12 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ12 | cDXGF | Humidification | 0 | 0
Existing | CZ12 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ12 | cDXGF | Water Systems | 0 | 253134.19
Existing | CZ12 | cDXGF | Refrigeration | 0 | 0
Existing | CZ12 | cDXGF | Generators | 0 | 0
Existing | CZ12 | cDXGF | Total End Uses | 1020211.44 | 486679.15
Existing | CZ13 | cDXGF | Heating | 0 | 67537.43
Existing | CZ13 | cDXGF | Cooling | 296837.83 | 0
Existing | CZ13 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ13 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ13 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXGF | Fans | 331348.01 | 0
Existing | CZ13 | cDXGF | Pumps | 0 | 0
Existing | CZ13 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ13 | cDXGF | Humidification | 0 | 0
Existing | CZ13 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ13 | cDXGF | Water Systems | 0 | 238470.23
Existing | CZ13 | cDXGF | Refrigeration | 0 | 0
Existing | CZ13 | cDXGF | Generators | 0 | 0
Existing | CZ13 | cDXGF | Total End Uses | 1125127.59 | 451709.61
Existing | CZ14 | cDXGF | Heating | 0 | 38459.61
Existing | CZ14 | cDXGF | Cooling | 368345.53 | 0
Existing | CZ14 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ14 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ14 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXGF | Fans | 359323.42 | 0
Existing | CZ14 | cDXGF | Pumps | 0 | 0
Existing | CZ14 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ14 | cDXGF | Humidification | 0 | 0
Existing | CZ14 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ14 | cDXGF | Water Systems | 0 | 225854.31
Existing | CZ14 | cDXGF | Refrigeration | 0 | 0
Existing | CZ14 | cDXGF | Generators | 0 | 0
Existing | CZ14 | cDXGF | Total End Uses | 1224610.7 | 410015.87
Existing | CZ15 | cDXGF | Heating | 0 | 12987.48
Existing | CZ15 | cDXGF | Cooling | 496598.43 | 0
Existing | CZ15 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ15 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ15 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXGF | Fans | 352015.98 | 0
Existing | CZ15 | cDXGF | Pumps | 0 | 0
Existing | CZ15 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ15 | cDXGF | Humidification | 0 | 0
Existing | CZ15 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ15 | cDXGF | Water Systems | 0 | 200448.52
Existing | CZ15 | cDXGF | Refrigeration | 0 | 0
Existing | CZ15 | cDXGF | Generators | 0 | 0
Existing | CZ15 | cDXGF | Total End Uses | 1345556.15 | 359137.94
Existing | CZ16 | cDXGF | Heating | 0 | 134687.72
Existing | CZ16 | cDXGF | Cooling | 236288.98 | 0
Existing | CZ16 | cDXGF | Interior Lighting | 216717.02 | 0
Existing | CZ16 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXGF | Interior Equipment | 280224.73 | 145701.95
Existing | CZ16 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXGF | Fans | 356851.28 | 0
Existing | CZ16 | cDXGF | Pumps | 0 | 0
Existing | CZ16 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ16 | cDXGF | Humidification | 0 | 0
Existing | CZ16 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ16 | cDXGF | Water Systems | 0 | 267234.98
Existing | CZ16 | cDXGF | Refrigeration | 0 | 0
Existing | CZ16 | cDXGF | Generators | 0 | 0
Existing | CZ16 | cDXGF | Total End Uses | 1090082.01 | 547624.65
New Construction | CZ01 | cDXGF | Heating | 0 | 226364.85
New Construction | CZ01 | cDXGF | Cooling | 23205.7 | 0
New Construction | CZ01 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ01 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ01 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXGF | Fans | 179619.22 | 0
New Construction | CZ01 | cDXGF | Pumps | 0 | 0
New Construction | CZ01 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXGF | Humidification | 0 | 0
New Construction | CZ01 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXGF | Water Systems | 0 | 297212.87
New Construction | CZ01 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ01 | cDXGF | Generators | 0 | 0
New Construction | CZ01 | cDXGF | Total End Uses | 586448.02 | 669279.67
New Construction | CZ02 | cDXGF | Heating | 0 | 117853.73
New Construction | CZ02 | cDXGF | Cooling | 89025.02 | 0
New Construction | CZ02 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ02 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ02 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXGF | Fans | 193831.09 | 0
New Construction | CZ02 | cDXGF | Pumps | 0 | 0
New Construction | CZ02 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXGF | Humidification | 0 | 0
New Construction | CZ02 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXGF | Water Systems | 0 | 272654.36
New Construction | CZ02 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ02 | cDXGF | Generators | 0 | 0
New Construction | CZ02 | cDXGF | Total End Uses | 666479.2 | 536210.03
New Construction | CZ03 | cDXGF | Heating | 0 | 81293.47
New Construction | CZ03 | cDXGF | Cooling | 60772.63 | 0
New Construction | CZ03 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ03 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ03 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXGF | Fans | 191555.54 | 0
New Construction | CZ03 | cDXGF | Pumps | 0 | 0
New Construction | CZ03 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXGF | Humidification | 0 | 0
New Construction | CZ03 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXGF | Water Systems | 0 | 271844.96
New Construction | CZ03 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ03 | cDXGF | Generators | 0 | 0
New Construction | CZ03 | cDXGF | Total End Uses | 635951.26 | 498840.38
New Construction | CZ04 | cDXGF | Heating | 0 | 68341.48
New Construction | CZ04 | cDXGF | Cooling | 104335.57 | 0
New Construction | CZ04 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ04 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ04 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXGF | Fans | 194616.78 | 0
New Construction | CZ04 | cDXGF | Pumps | 0 | 0
New Construction | CZ04 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXGF | Humidification | 0 | 0
New Construction | CZ04 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXGF | Water Systems | 0 | 262159.09
New Construction | CZ04 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ04 | cDXGF | Generators | 0 | 0
New Construction | CZ04 | cDXGF | Total End Uses | 682575.44 | 476202.52
New Construction | CZ05 | cDXGF | Heating | 0 | 77200.72
New Construction | CZ05 | cDXGF | Cooling | 73237.29 | 0
New Construction | CZ05 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ05 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ05 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXGF | Fans | 190214.1 | 0
New Construction | CZ05 | cDXGF | Pumps | 0 | 0
New Construction | CZ05 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXGF | Humidification | 0 | 0
New Construction | CZ05 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXGF | Water Systems | 0 | 271784.29
New Construction | CZ05 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ05 | cDXGF | Generators | 0 | 0
New Construction | CZ05 | cDXGF | Total End Uses | 647074.48 | 494686.96
New Construction | CZ06 | cDXGF | Heating | 0 | 19705.72
New Construction | CZ06 | cDXGF | Cooling | 113356.42 | 0
New Construction | CZ06 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ06 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ06 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXGF | Fans | 202893.35 | 0
New Construction | CZ06 | cDXGF | Pumps | 0 | 0
New Construction | CZ06 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXGF | Humidification | 0 | 0
New Construction | CZ06 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXGF | Water Systems | 0 | 250336.84
New Construction | CZ06 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ06 | cDXGF | Generators | 0 | 0
New Construction | CZ06 | cDXGF | Total End Uses | 699872.86 | 415744.51
New Construction | CZ07 | cDXGF | Heating | 0 | 19143.84
New Construction | CZ07 | cDXGF | Cooling | 123003.1 | 0
New Construction | CZ07 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ07 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ07 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXGF | Fans | 201239.5 | 0
New Construction | CZ07 | cDXGF | Pumps | 0 | 0
New Construction | CZ07 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXGF | Humidification | 0 | 0
New Construction | CZ07 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXGF | Water Systems | 0 | 246870.04
New Construction | CZ07 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ07 | cDXGF | Generators | 0 | 0
New Construction | CZ07 | cDXGF | Total End Uses | 707865.69 | 411715.83
New Construction | CZ08 | cDXGF | Heating | 0 | 27425.19
New Construction | CZ08 | cDXGF | Cooling | 140126.84 | 0
New Construction | CZ08 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ08 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ08 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXGF | Fans | 207311.03 | 0
New Construction | CZ08 | cDXGF | Pumps | 0 | 0
New Construction | CZ08 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXGF | Humidification | 0 | 0
New Construction | CZ08 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXGF | Water Systems | 0 | 246564.08
New Construction | CZ08 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ08 | cDXGF | Generators | 0 | 0
New Construction | CZ08 | cDXGF | Total End Uses | 731060.97 | 419691.21
New Construction | CZ09 | cDXGF | Heating | 0 | 18353.46
New Construction | CZ09 | cDXGF | Cooling | 153268.16 | 0
New Construction | CZ09 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ09 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ09 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXGF | Fans | 199179.97 | 0
New Construction | CZ09 | cDXGF | Pumps | 0 | 0
New Construction | CZ09 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXGF | Humidification | 0 | 0
New Construction | CZ09 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXGF | Water Systems | 0 | 243189.54
New Construction | CZ09 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ09 | cDXGF | Generators | 0 | 0
New Construction | CZ09 | cDXGF | Total End Uses | 736071.22 | 407244.94
New Construction | CZ10 | cDXGF | Heating | 0 | 48982.39
New Construction | CZ10 | cDXGF | Cooling | 192399.8 | 0
New Construction | CZ10 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ10 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ10 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXGF | Fans | 207988.49 | 0
New Construction | CZ10 | cDXGF | Pumps | 0 | 0
New Construction | CZ10 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXGF | Humidification | 0 | 0
New Construction | CZ10 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXGF | Water Systems | 0 | 240475.85
New Construction | CZ10 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ10 | cDXGF | Generators | 0 | 0
New Construction | CZ10 | cDXGF | Total End Uses | 784011.39 | 435160.18
New Construction | CZ11 | cDXGF | Heating | 0 | 112965.5
New Construction | CZ11 | cDXGF | Cooling | 199407.23 | 0
New Construction | CZ11 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ11 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ11 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXGF | Fans | 212366.73 | 0
New Construction | CZ11 | cDXGF | Pumps | 0 | 0
New Construction | CZ11 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXGF | Humidification | 0 | 0
New Construction | CZ11 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXGF | Water Systems | 0 | 245381.41
New Construction | CZ11 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ11 | cDXGF | Generators | 0 | 0
New Construction | CZ11 | cDXGF | Total End Uses | 795397.05 | 504048.85
New Construction | CZ12 | cDXGF | Heating | 0 | 101870.26
New Construction | CZ12 | cDXGF | Cooling | 167918.96 | 0
New Construction | CZ12 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ12 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ12 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXGF | Fans | 202817.55 | 0
New Construction | CZ12 | cDXGF | Pumps | 0 | 0
New Construction | CZ12 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXGF | Humidification | 0 | 0
New Construction | CZ12 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXGF | Water Systems | 0 | 252800.08
New Construction | CZ12 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ12 | cDXGF | Generators | 0 | 0
New Construction | CZ12 | cDXGF | Total End Uses | 754359.6 | 500372.29
New Construction | CZ13 | cDXGF | Heating | 0 | 81981.33
New Construction | CZ13 | cDXGF | Cooling | 222994.45 | 0
New Construction | CZ13 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ13 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ13 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXGF | Fans | 214485.98 | 0
New Construction | CZ13 | cDXGF | Pumps | 0 | 0
New Construction | CZ13 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXGF | Humidification | 0 | 0
New Construction | CZ13 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXGF | Water Systems | 0 | 238130.54
New Construction | CZ13 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ13 | cDXGF | Generators | 0 | 0
New Construction | CZ13 | cDXGF | Total End Uses | 821103.53 | 465813.81
New Construction | CZ14 | cDXGF | Heating | 0 | 50127.85
New Construction | CZ14 | cDXGF | Cooling | 280410.1 | 0
New Construction | CZ14 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ14 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ14 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXGF | Fans | 233007.91 | 0
New Construction | CZ14 | cDXGF | Pumps | 0 | 0
New Construction | CZ14 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXGF | Humidification | 0 | 0
New Construction | CZ14 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXGF | Water Systems | 0 | 225423.32
New Construction | CZ14 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ14 | cDXGF | Generators | 0 | 0
New Construction | CZ14 | cDXGF | Total End Uses | 897041.11 | 421253.12
New Construction | CZ15 | cDXGF | Heating | 0 | 18622.11
New Construction | CZ15 | cDXGF | Cooling | 378910.18 | 0
New Construction | CZ15 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ15 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ15 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXGF | Fans | 223765.39 | 0
New Construction | CZ15 | cDXGF | Pumps | 0 | 0
New Construction | CZ15 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXGF | Humidification | 0 | 0
New Construction | CZ15 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXGF | Water Systems | 0 | 200021.39
New Construction | CZ15 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ15 | cDXGF | Generators | 0 | 0
New Construction | CZ15 | cDXGF | Total End Uses | 986298.67 | 364345.45
New Construction | CZ16 | cDXGF | Heating | 0 | 148215.47
New Construction | CZ16 | cDXGF | Cooling | 183689.15 | 0
New Construction | CZ16 | cDXGF | Interior Lighting | 103398.36 | 0
New Construction | CZ16 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXGF | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ16 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXGF | Fans | 241472.87 | 0
New Construction | CZ16 | cDXGF | Pumps | 0 | 0
New Construction | CZ16 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXGF | Humidification | 0 | 0
New Construction | CZ16 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXGF | Water Systems | 0 | 266916
New Construction | CZ16 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ16 | cDXGF | Generators | 0 | 0
New Construction | CZ16 | cDXGF | Total End Uses | 808785.11 | 560833.42
Existing | CZ01 | cDXHP | Heating | 44631.38 | 0
Existing | CZ01 | cDXHP | Cooling | 27038.77 | 0
Existing | CZ01 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ01 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ01 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXHP | Fans | 245806.77 | 0
Existing | CZ01 | cDXHP | Pumps | 0 | 0
Existing | CZ01 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ01 | cDXHP | Humidification | 0 | 0
Existing | CZ01 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ01 | cDXHP | Water Systems | 0 | 297524.36
Existing | CZ01 | cDXHP | Refrigeration | 0 | 0
Existing | CZ01 | cDXHP | Generators | 0 | 0
Existing | CZ01 | cDXHP | Total End Uses | 814418.68 | 443226.31
Existing | CZ02 | cDXHP | Heating | 27094.82 | 0.04
Existing | CZ02 | cDXHP | Cooling | 114229.54 | 0
Existing | CZ02 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ02 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ02 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXHP | Fans | 277303.51 | 0
Existing | CZ02 | cDXHP | Pumps | 0 | 0
Existing | CZ02 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ02 | cDXHP | Humidification | 0 | 0
Existing | CZ02 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ02 | cDXHP | Water Systems | 0 | 273000.47
Existing | CZ02 | cDXHP | Refrigeration | 0 | 0
Existing | CZ02 | cDXHP | Generators | 0 | 0
Existing | CZ02 | cDXHP | Total End Uses | 915569.62 | 418702.45
Existing | CZ03 | cDXHP | Heating | 14500.13 | 0
Existing | CZ03 | cDXHP | Cooling | 78125.16 | 0
Existing | CZ03 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ03 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ03 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXHP | Fans | 265024.82 | 0
Existing | CZ03 | cDXHP | Pumps | 0 | 0
Existing | CZ03 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ03 | cDXHP | Humidification | 0 | 0
Existing | CZ03 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ03 | cDXHP | Water Systems | 0 | 272138.93
Existing | CZ03 | cDXHP | Refrigeration | 0 | 0
Existing | CZ03 | cDXHP | Generators | 0 | 0
Existing | CZ03 | cDXHP | Total End Uses | 854591.86 | 417840.87
Existing | CZ04 | cDXHP | Heating | 12827.58 | 0
Existing | CZ04 | cDXHP | Cooling | 137542.78 | 0
Existing | CZ04 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ04 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ04 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXHP | Fans | 279566.05 | 0
Existing | CZ04 | cDXHP | Pumps | 0 | 0
Existing | CZ04 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ04 | cDXHP | Humidification | 0 | 0
Existing | CZ04 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ04 | cDXHP | Water Systems | 0 | 262527.87
Existing | CZ04 | cDXHP | Refrigeration | 0 | 0
Existing | CZ04 | cDXHP | Generators | 0 | 0
Existing | CZ04 | cDXHP | Total End Uses | 926878.16 | 408229.82
Existing | CZ05 | cDXHP | Heating | 13671.13 | 0
Existing | CZ05 | cDXHP | Cooling | 94701.54 | 0
Existing | CZ05 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ05 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ05 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXHP | Fans | 263023.74 | 0
Existing | CZ05 | cDXHP | Pumps | 0 | 0
Existing | CZ05 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ05 | cDXHP | Humidification | 0 | 0
Existing | CZ05 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ05 | cDXHP | Water Systems | 0 | 272204.85
Existing | CZ05 | cDXHP | Refrigeration | 0 | 0
Existing | CZ05 | cDXHP | Generators | 0 | 0
Existing | CZ05 | cDXHP | Total End Uses | 868338.17 | 417906.79
Existing | CZ06 | cDXHP | Heating | 2719.91 | 0
Existing | CZ06 | cDXHP | Cooling | 144377.56 | 0
Existing | CZ06 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ06 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ06 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXHP | Fans | 276226.02 | 0
Existing | CZ06 | cDXHP | Pumps | 0 | 0
Existing | CZ06 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ06 | cDXHP | Humidification | 0 | 0
Existing | CZ06 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ06 | cDXHP | Water Systems | 0 | 250745.84
Existing | CZ06 | cDXHP | Refrigeration | 0 | 0
Existing | CZ06 | cDXHP | Generators | 0 | 0
Existing | CZ06 | cDXHP | Total End Uses | 920265.24 | 396447.79
Existing | CZ07 | cDXHP | Heating | 2669.83 | 0
Existing | CZ07 | cDXHP | Cooling | 160076.18 | 0
Existing | CZ07 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ07 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ07 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXHP | Fans | 273440.9 | 0
Existing | CZ07 | cDXHP | Pumps | 0 | 0
Existing | CZ07 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ07 | cDXHP | Humidification | 0 | 0
Existing | CZ07 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ07 | cDXHP | Water Systems | 0 | 247318.2
Existing | CZ07 | cDXHP | Refrigeration | 0 | 0
Existing | CZ07 | cDXHP | Generators | 0 | 0
Existing | CZ07 | cDXHP | Total End Uses | 933128.67 | 393020.15
Existing | CZ08 | cDXHP | Heating | 4133.78 | 0
Existing | CZ08 | cDXHP | Cooling | 182844.87 | 0
Existing | CZ08 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ08 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ08 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXHP | Fans | 287124.2 | 0
Existing | CZ08 | cDXHP | Pumps | 0 | 0
Existing | CZ08 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ08 | cDXHP | Humidification | 0 | 0
Existing | CZ08 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ08 | cDXHP | Water Systems | 0 | 246912.73
Existing | CZ08 | cDXHP | Refrigeration | 0 | 0
Existing | CZ08 | cDXHP | Generators | 0 | 0
Existing | CZ08 | cDXHP | Total End Uses | 971044.6 | 392614.68
Existing | CZ09 | cDXHP | Heating | 2997.08 | 0
Existing | CZ09 | cDXHP | Cooling | 208953.08 | 0
Existing | CZ09 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ09 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ09 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXHP | Fans | 302536.47 | 0
Existing | CZ09 | cDXHP | Pumps | 0 | 0
Existing | CZ09 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ09 | cDXHP | Humidification | 0 | 0
Existing | CZ09 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ09 | cDXHP | Water Systems | 0 | 243529.4
Existing | CZ09 | cDXHP | Refrigeration | 0 | 0
Existing | CZ09 | cDXHP | Generators | 0 | 0
Existing | CZ09 | cDXHP | Total End Uses | 1011428.38 | 389231.34
Existing | CZ10 | cDXHP | Heating | 10695.66 | 0
Existing | CZ10 | cDXHP | Cooling | 246251.14 | 0
Existing | CZ10 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ10 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ10 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXHP | Fans | 296708.71 | 0
Existing | CZ10 | cDXHP | Pumps | 0 | 0
Existing | CZ10 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ10 | cDXHP | Humidification | 0 | 0
Existing | CZ10 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ10 | cDXHP | Water Systems | 0 | 240788.34
Existing | CZ10 | cDXHP | Refrigeration | 0 | 0
Existing | CZ10 | cDXHP | Generators | 0 | 0
Existing | CZ10 | cDXHP | Total End Uses | 1050597.26 | 386490.28
Existing | CZ11 | cDXHP | Heating | 26313.73 | 0
Existing | CZ11 | cDXHP | Cooling | 265690.5 | 0
Existing | CZ11 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ11 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ11 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXHP | Fans | 330089.87 | 0
Existing | CZ11 | cDXHP | Pumps | 0 | 0
Existing | CZ11 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ11 | cDXHP | Humidification | 0 | 0
Existing | CZ11 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ11 | cDXHP | Water Systems | 0 | 245706.43
Existing | CZ11 | cDXHP | Refrigeration | 0 | 0
Existing | CZ11 | cDXHP | Generators | 0 | 0
Existing | CZ11 | cDXHP | Total End Uses | 1119035.85 | 391408.37
Existing | CZ12 | cDXHP | Heating | 23317.01 | 0
Existing | CZ12 | cDXHP | Cooling | 221141.24 | 0
Existing | CZ12 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ12 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ12 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXHP | Fans | 302089.7 | 0
Existing | CZ12 | cDXHP | Pumps | 0 | 0
Existing | CZ12 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ12 | cDXHP | Humidification | 0 | 0
Existing | CZ12 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ12 | cDXHP | Water Systems | 0 | 253125.38
Existing | CZ12 | cDXHP | Refrigeration | 0 | 0
Existing | CZ12 | cDXHP | Generators | 0 | 0
Existing | CZ12 | cDXHP | Total End Uses | 1043489.7 | 398827.32
Existing | CZ13 | cDXHP | Heating | 17676.08 | 0
Existing | CZ13 | cDXHP | Cooling | 296926.95 | 0
Existing | CZ13 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ13 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ13 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXHP | Fans | 331348.01 | 0
Existing | CZ13 | cDXHP | Pumps | 0 | 0
Existing | CZ13 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ13 | cDXHP | Humidification | 0 | 0
Existing | CZ13 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ13 | cDXHP | Water Systems | 0 | 238461.54
Existing | CZ13 | cDXHP | Refrigeration | 0 | 0
Existing | CZ13 | cDXHP | Generators | 0 | 0
Existing | CZ13 | cDXHP | Total End Uses | 1142892.79 | 384163.48
Existing | CZ14 | cDXHP | Heating | 10530.56 | 0
Existing | CZ14 | cDXHP | Cooling | 369087.65 | 0
Existing | CZ14 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ14 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ14 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXHP | Fans | 359315.8 | 0
Existing | CZ14 | cDXHP | Pumps | 0 | 0
Existing | CZ14 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ14 | cDXHP | Humidification | 0 | 0
Existing | CZ14 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ14 | cDXHP | Water Systems | 0 | 225836.94
Existing | CZ14 | cDXHP | Refrigeration | 0 | 0
Existing | CZ14 | cDXHP | Generators | 0 | 0
Existing | CZ14 | cDXHP | Total End Uses | 1235875.76 | 371538.89
Existing | CZ15 | cDXHP | Heating | 3356.86 | 0
Existing | CZ15 | cDXHP | Cooling | 496523.66 | 0
Existing | CZ15 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ15 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ15 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXHP | Fans | 352015.98 | 0
Existing | CZ15 | cDXHP | Pumps | 0 | 0
Existing | CZ15 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ15 | cDXHP | Humidification | 0 | 0
Existing | CZ15 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ15 | cDXHP | Water Systems | 0 | 200448.52
Existing | CZ15 | cDXHP | Refrigeration | 0 | 0
Existing | CZ15 | cDXHP | Generators | 0 | 0
Existing | CZ15 | cDXHP | Total End Uses | 1348838.25 | 346150.46
Existing | CZ16 | cDXHP | Heating | 43537.54 | 30.01
Existing | CZ16 | cDXHP | Cooling | 238255.71 | 0
Existing | CZ16 | cDXHP | Interior Lighting | 216717.02 | 0
Existing | CZ16 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXHP | Interior Equipment | 280224.73 | 145701.95
Existing | CZ16 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXHP | Fans | 356852.91 | 0
Existing | CZ16 | cDXHP | Pumps | 0 | 0
Existing | CZ16 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ16 | cDXHP | Humidification | 0 | 0
Existing | CZ16 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ16 | cDXHP | Water Systems | 0 | 267250.89
Existing | CZ16 | cDXHP | Refrigeration | 0 | 0
Existing | CZ16 | cDXHP | Generators | 0 | 0
Existing | CZ16 | cDXHP | Total End Uses | 1135587.91 | 412982.85
New Construction | CZ01 | cDXHP | Heating | 54305.65 | 0
New Construction | CZ01 | cDXHP | Cooling | 22887.5 | 0
New Construction | CZ01 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ01 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ01 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXHP | Fans | 179619.22 | 0
New Construction | CZ01 | cDXHP | Pumps | 0 | 0
New Construction | CZ01 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXHP | Humidification | 0 | 0
New Construction | CZ01 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXHP | Water Systems | 0 | 297212.87
New Construction | CZ01 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ01 | cDXHP | Generators | 0 | 0
New Construction | CZ01 | cDXHP | Total End Uses | 640435.46 | 442914.82
New Construction | CZ02 | cDXHP | Heating | 30228.92 | 0
New Construction | CZ02 | cDXHP | Cooling | 88305.48 | 0
New Construction | CZ02 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ02 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ02 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXHP | Fans | 193822.41 | 0
New Construction | CZ02 | cDXHP | Pumps | 0 | 0
New Construction | CZ02 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXHP | Humidification | 0 | 0
New Construction | CZ02 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXHP | Water Systems | 0 | 272670.82
New Construction | CZ02 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ02 | cDXHP | Generators | 0 | 0
New Construction | CZ02 | cDXHP | Total End Uses | 695979.9 | 418372.77
New Construction | CZ03 | cDXHP | Heating | 19498.3 | 0
New Construction | CZ03 | cDXHP | Cooling | 60275.46 | 0
New Construction | CZ03 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ03 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ03 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXHP | Fans | 191555.54 | 0
New Construction | CZ03 | cDXHP | Pumps | 0 | 0
New Construction | CZ03 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXHP | Humidification | 0 | 0
New Construction | CZ03 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXHP | Water Systems | 0 | 271809.23
New Construction | CZ03 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ03 | cDXHP | Generators | 0 | 0
New Construction | CZ03 | cDXHP | Total End Uses | 654952.39 | 417511.18
New Construction | CZ04 | cDXHP | Heating | 16491.32 | 0
New Construction | CZ04 | cDXHP | Cooling | 104064.38 | 0
New Construction | CZ04 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ04 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ04 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXHP | Fans | 194616.78 | 0
New Construction | CZ04 | cDXHP | Pumps | 0 | 0
New Construction | CZ04 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXHP | Humidification | 0 | 0
New Construction | CZ04 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXHP | Water Systems | 0 | 262142.1
New Construction | CZ04 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ04 | cDXHP | Generators | 0 | 0
New Construction | CZ04 | cDXHP | Total End Uses | 698795.58 | 407844.04
New Construction | CZ05 | cDXHP | Heating | 18971.81 | 0
New Construction | CZ05 | cDXHP | Cooling | 72765.31 | 0
New Construction | CZ05 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ05 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ05 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXHP | Fans | 190214.1 | 0
New Construction | CZ05 | cDXHP | Pumps | 0 | 0
New Construction | CZ05 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXHP | Humidification | 0 | 0
New Construction | CZ05 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXHP | Water Systems | 0 | 271709.01
New Construction | CZ05 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ05 | cDXHP | Generators | 0 | 0
New Construction | CZ05 | cDXHP | Total End Uses | 665574.31 | 417410.96
New Construction | CZ06 | cDXHP | Heating | 4606.7 | 0
New Construction | CZ06 | cDXHP | Cooling | 109340.32 | 0
New Construction | CZ06 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ06 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ06 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXHP | Fans | 202893.35 | 0
New Construction | CZ06 | cDXHP | Pumps | 0 | 0
New Construction | CZ06 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXHP | Humidification | 0 | 0
New Construction | CZ06 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXHP | Water Systems | 0 | 250299.39
New Construction | CZ06 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ06 | cDXHP | Generators | 0 | 0
New Construction | CZ06 | cDXHP | Total End Uses | 700463.46 | 396001.34
New Construction | CZ07 | cDXHP | Heating | 4478.83 | 0
New Construction | CZ07 | cDXHP | Cooling | 120555.99 | 0
New Construction | CZ07 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ07 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ07 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXHP | Fans | 201239.5 | 0
New Construction | CZ07 | cDXHP | Pumps | 0 | 0
New Construction | CZ07 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXHP | Humidification | 0 | 0
New Construction | CZ07 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXHP | Water Systems | 0 | 246887.02
New Construction | CZ07 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ07 | cDXHP | Generators | 0 | 0
New Construction | CZ07 | cDXHP | Total End Uses | 709897.41 | 392588.97
New Construction | CZ08 | cDXHP | Heating | 6491.73 | 0
New Construction | CZ08 | cDXHP | Cooling | 139138.28 | 0
New Construction | CZ08 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ08 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ08 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXHP | Fans | 207311.03 | 0
New Construction | CZ08 | cDXHP | Pumps | 0 | 0
New Construction | CZ08 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXHP | Humidification | 0 | 0
New Construction | CZ08 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXHP | Water Systems | 0 | 246564.08
New Construction | CZ08 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ08 | cDXHP | Generators | 0 | 0
New Construction | CZ08 | cDXHP | Total End Uses | 736564.14 | 392266.02
New Construction | CZ09 | cDXHP | Heating | 4334.53 | 0
New Construction | CZ09 | cDXHP | Cooling | 151892.35 | 0
New Construction | CZ09 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ09 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ09 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXHP | Fans | 199179.97 | 0
New Construction | CZ09 | cDXHP | Pumps | 0 | 0
New Construction | CZ09 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXHP | Humidification | 0 | 0
New Construction | CZ09 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXHP | Water Systems | 0 | 243189.33
New Construction | CZ09 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ09 | cDXHP | Generators | 0 | 0
New Construction | CZ09 | cDXHP | Total End Uses | 739029.94 | 388891.27
New Construction | CZ10 | cDXHP | Heating | 12821.24 | 0
New Construction | CZ10 | cDXHP | Cooling | 192715.7 | 0
New Construction | CZ10 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ10 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ10 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXHP | Fans | 207977.14 | 0
New Construction | CZ10 | cDXHP | Pumps | 0 | 0
New Construction | CZ10 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXHP | Humidification | 0 | 0
New Construction | CZ10 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXHP | Water Systems | 0 | 240509.93
New Construction | CZ10 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ10 | cDXHP | Generators | 0 | 0
New Construction | CZ10 | cDXHP | Total End Uses | 797137.17 | 386211.87
New Construction | CZ11 | cDXHP | Heating | 28851.88 | 0
New Construction | CZ11 | cDXHP | Cooling | 200810.6 | 0
New Construction | CZ11 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ11 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ11 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXHP | Fans | 212326.95 | 0
New Construction | CZ11 | cDXHP | Pumps | 0 | 0
New Construction | CZ11 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXHP | Humidification | 0 | 0
New Construction | CZ11 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXHP | Water Systems | 0 | 245369.54
New Construction | CZ11 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ11 | cDXHP | Generators | 0 | 0
New Construction | CZ11 | cDXHP | Total End Uses | 825612.52 | 391071.49
New Construction | CZ12 | cDXHP | Heating | 26050.52 | 0
New Construction | CZ12 | cDXHP | Cooling | 168662.61 | 0
New Construction | CZ12 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ12 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ12 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXHP | Fans | 202824.52 | 0
New Construction | CZ12 | cDXHP | Pumps | 0 | 0
New Construction | CZ12 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXHP | Humidification | 0 | 0
New Construction | CZ12 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXHP | Water Systems | 0 | 252723.44
New Construction | CZ12 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ12 | cDXHP | Generators | 0 | 0
New Construction | CZ12 | cDXHP | Total End Uses | 781160.75 | 398425.39
New Construction | CZ13 | cDXHP | Heating | 20779.27 | 0
New Construction | CZ13 | cDXHP | Cooling | 223712.64 | 0
New Construction | CZ13 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ13 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ13 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXHP | Fans | 214472.03 | 0
New Construction | CZ13 | cDXHP | Pumps | 0 | 0
New Construction | CZ13 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXHP | Humidification | 0 | 0
New Construction | CZ13 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXHP | Water Systems | 0 | 238160.37
New Construction | CZ13 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ13 | cDXHP | Generators | 0 | 0
New Construction | CZ13 | cDXHP | Total End Uses | 842587.04 | 383862.31
New Construction | CZ14 | cDXHP | Heating | 13138.49 | 0
New Construction | CZ14 | cDXHP | Cooling | 281720.49 | 0
New Construction | CZ14 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ14 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ14 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXHP | Fans | 232973.32 | 0
New Construction | CZ14 | cDXHP | Pumps | 0 | 0
New Construction | CZ14 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXHP | Humidification | 0 | 0
New Construction | CZ14 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXHP | Water Systems | 0 | 225423.23
New Construction | CZ14 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ14 | cDXHP | Generators | 0 | 0
New Construction | CZ14 | cDXHP | Total End Uses | 911455.39 | 371125.18
New Construction | CZ15 | cDXHP | Heating | 4667.98 | 0
New Construction | CZ15 | cDXHP | Cooling | 379508.15 | 0
New Construction | CZ15 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ15 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ15 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXHP | Fans | 223727.89 | 0
New Construction | CZ15 | cDXHP | Pumps | 0 | 0
New Construction | CZ15 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXHP | Humidification | 0 | 0
New Construction | CZ15 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXHP | Water Systems | 0 | 200031.37
New Construction | CZ15 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ15 | cDXHP | Generators | 0 | 0
New Construction | CZ15 | cDXHP | Total End Uses | 991527.12 | 345733.32
New Construction | CZ16 | cDXHP | Heating | 45040.65 | 2.82
New Construction | CZ16 | cDXHP | Cooling | 184793.97 | 0
New Construction | CZ16 | cDXHP | Interior Lighting | 103398.36 | 0
New Construction | CZ16 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXHP | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ16 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXHP | Fans | 241506.09 | 0
New Construction | CZ16 | cDXHP | Pumps | 0 | 0
New Construction | CZ16 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXHP | Humidification | 0 | 0
New Construction | CZ16 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXHP | Water Systems | 0 | 266818.75
New Construction | CZ16 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ16 | cDXHP | Generators | 0 | 0
New Construction | CZ16 | cDXHP | Total End Uses | 854963.8 | 412523.51
Existing | CZ01 | cDXOH | Heating | 0 | 0
Existing | CZ01 | cDXOH | Cooling | 26365.43 | 0
Existing | CZ01 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ01 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ01 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXOH | Fans | 247711.04 | 0
Existing | CZ01 | cDXOH | Pumps | 0 | 0
Existing | CZ01 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ01 | cDXOH | Humidification | 0 | 0
Existing | CZ01 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ01 | cDXOH | Water Systems | 0 | 297561.96
Existing | CZ01 | cDXOH | Refrigeration | 0 | 0
Existing | CZ01 | cDXOH | Generators | 0 | 0
Existing | CZ01 | cDXOH | Total End Uses | 771018.23 | 443263.9
Existing | CZ02 | cDXOH | Heating | 0 | 0.03
Existing | CZ02 | cDXOH | Cooling | 114239.72 | 0
Existing | CZ02 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ02 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ02 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXOH | Fans | 278147.74 | 0
Existing | CZ02 | cDXOH | Pumps | 0 | 0
Existing | CZ02 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ02 | cDXOH | Humidification | 0 | 0
Existing | CZ02 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ02 | cDXOH | Water Systems | 0 | 273016.7
Existing | CZ02 | cDXOH | Refrigeration | 0 | 0
Existing | CZ02 | cDXOH | Generators | 0 | 0
Existing | CZ02 | cDXOH | Total End Uses | 889329.21 | 418718.67
Existing | CZ03 | cDXOH | Heating | 0 | 0
Existing | CZ03 | cDXOH | Cooling | 78440.21 | 0
Existing | CZ03 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ03 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ03 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXOH | Fans | 265146.6 | 0
Existing | CZ03 | cDXOH | Pumps | 0 | 0
Existing | CZ03 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ03 | cDXOH | Humidification | 0 | 0
Existing | CZ03 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ03 | cDXOH | Water Systems | 0 | 272177.94
Existing | CZ03 | cDXOH | Refrigeration | 0 | 0
Existing | CZ03 | cDXOH | Generators | 0 | 0
Existing | CZ03 | cDXOH | Total End Uses | 840528.57 | 417879.89
Existing | CZ04 | cDXOH | Heating | 0 | 0
Existing | CZ04 | cDXOH | Cooling | 137624.53 | 0
Existing | CZ04 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ04 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ04 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXOH | Fans | 279587.76 | 0
Existing | CZ04 | cDXOH | Pumps | 0 | 0
Existing | CZ04 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ04 | cDXOH | Humidification | 0 | 0
Existing | CZ04 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ04 | cDXOH | Water Systems | 0 | 262555.9
Existing | CZ04 | cDXOH | Refrigeration | 0 | 0
Existing | CZ04 | cDXOH | Generators | 0 | 0
Existing | CZ04 | cDXOH | Total End Uses | 914154.04 | 408257.84
Existing | CZ05 | cDXOH | Heating | 0 | 0
Existing | CZ05 | cDXOH | Cooling | 94679.28 | 0
Existing | CZ05 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ05 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ05 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXOH | Fans | 263071.13 | 0
Existing | CZ05 | cDXOH | Pumps | 0 | 0
Existing | CZ05 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ05 | cDXOH | Humidification | 0 | 0
Existing | CZ05 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ05 | cDXOH | Water Systems | 0 | 272191.34
Existing | CZ05 | cDXOH | Refrigeration | 0 | 0
Existing | CZ05 | cDXOH | Generators | 0 | 0
Existing | CZ05 | cDXOH | Total End Uses | 854692.16 | 417893.29
Existing | CZ06 | cDXOH | Heating | 0 | 0
Existing | CZ06 | cDXOH | Cooling | 149195.03 | 0
Existing | CZ06 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ06 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ06 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXOH | Fans | 276168.04 | 0
Existing | CZ06 | cDXOH | Pumps | 0 | 0
Existing | CZ06 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ06 | cDXOH | Humidification | 0 | 0
Existing | CZ06 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ06 | cDXOH | Water Systems | 0 | 250745.82
Existing | CZ06 | cDXOH | Refrigeration | 0 | 0
Existing | CZ06 | cDXOH | Generators | 0 | 0
Existing | CZ06 | cDXOH | Total End Uses | 922304.81 | 396447.77
Existing | CZ07 | cDXOH | Heating | 0 | 0
Existing | CZ07 | cDXOH | Cooling | 163282.43 | 0
Existing | CZ07 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ07 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ07 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXOH | Fans | 273420.65 | 0
Existing | CZ07 | cDXOH | Pumps | 0 | 0
Existing | CZ07 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ07 | cDXOH | Humidification | 0 | 0
Existing | CZ07 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ07 | cDXOH | Water Systems | 0 | 247316.18
Existing | CZ07 | cDXOH | Refrigeration | 0 | 0
Existing | CZ07 | cDXOH | Generators | 0 | 0
Existing | CZ07 | cDXOH | Total End Uses | 933644.84 | 393018.13
Existing | CZ08 | cDXOH | Heating | 0 | 0
Existing | CZ08 | cDXOH | Cooling | 184389.76 | 0
Existing | CZ08 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ08 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ08 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXOH | Fans | 287091.25 | 0
Existing | CZ08 | cDXOH | Pumps | 0 | 0
Existing | CZ08 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ08 | cDXOH | Humidification | 0 | 0
Existing | CZ08 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ08 | cDXOH | Water Systems | 0 | 246920.58
Existing | CZ08 | cDXOH | Refrigeration | 0 | 0
Existing | CZ08 | cDXOH | Generators | 0 | 0
Existing | CZ08 | cDXOH | Total End Uses | 968422.76 | 392622.52
Existing | CZ09 | cDXOH | Heating | 0 | 0
Existing | CZ09 | cDXOH | Cooling | 211146.69 | 0
Existing | CZ09 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ09 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ09 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXOH | Fans | 302472.24 | 0
Existing | CZ09 | cDXOH | Pumps | 0 | 0
Existing | CZ09 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ09 | cDXOH | Humidification | 0 | 0
Existing | CZ09 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ09 | cDXOH | Water Systems | 0 | 243513.6
Existing | CZ09 | cDXOH | Refrigeration | 0 | 0
Existing | CZ09 | cDXOH | Generators | 0 | 0
Existing | CZ09 | cDXOH | Total End Uses | 1010560.67 | 389215.55
Existing | CZ10 | cDXOH | Heating | 0 | 0
Existing | CZ10 | cDXOH | Cooling | 245723.02 | 0
Existing | CZ10 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ10 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ10 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXOH | Fans | 296646.68 | 0
Existing | CZ10 | cDXOH | Pumps | 0 | 0
Existing | CZ10 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ10 | cDXOH | Humidification | 0 | 0
Existing | CZ10 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ10 | cDXOH | Water Systems | 0 | 240746.05
Existing | CZ10 | cDXOH | Refrigeration | 0 | 0
Existing | CZ10 | cDXOH | Generators | 0 | 0
Existing | CZ10 | cDXOH | Total End Uses | 1039311.45 | 386448
Existing | CZ11 | cDXOH | Heating | 0 | 0
Existing | CZ11 | cDXOH | Cooling | 264116.46 | 0
Existing | CZ11 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ11 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ11 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXOH | Fans | 331830.13 | 0
Existing | CZ11 | cDXOH | Pumps | 0 | 0
Existing | CZ11 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ11 | cDXOH | Humidification | 0 | 0
Existing | CZ11 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ11 | cDXOH | Water Systems | 0 | 245701.6
Existing | CZ11 | cDXOH | Refrigeration | 0 | 0
Existing | CZ11 | cDXOH | Generators | 0 | 0
Existing | CZ11 | cDXOH | Total End Uses | 1092888.34 | 391403.55
Existing | CZ12 | cDXOH | Heating | 0 | 0
Existing | CZ12 | cDXOH | Cooling | 220337.8 | 0
Existing | CZ12 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ12 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ12 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXOH | Fans | 303694.03 | 0
Existing | CZ12 | cDXOH | Pumps | 0 | 0
Existing | CZ12 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ12 | cDXOH | Humidification | 0 | 0
Existing | CZ12 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ12 | cDXOH | Water Systems | 0 | 253126.69
Existing | CZ12 | cDXOH | Refrigeration | 0 | 0
Existing | CZ12 | cDXOH | Generators | 0 | 0
Existing | CZ12 | cDXOH | Total End Uses | 1020973.58 | 398828.63
Existing | CZ13 | cDXOH | Heating | 0 | 0
Existing | CZ13 | cDXOH | Cooling | 296279.02 | 0
Existing | CZ13 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ13 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ13 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXOH | Fans | 332430.45 | 0
Existing | CZ13 | cDXOH | Pumps | 0 | 0
Existing | CZ13 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ13 | cDXOH | Humidification | 0 | 0
Existing | CZ13 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ13 | cDXOH | Water Systems | 0 | 238456.43
Existing | CZ13 | cDXOH | Refrigeration | 0 | 0
Existing | CZ13 | cDXOH | Generators | 0 | 0
Existing | CZ13 | cDXOH | Total End Uses | 1125651.22 | 384158.38
Existing | CZ14 | cDXOH | Heating | 0 | 0
Existing | CZ14 | cDXOH | Cooling | 367787.5 | 0
Existing | CZ14 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ14 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ14 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXOH | Fans | 359492.08 | 0
Existing | CZ14 | cDXOH | Pumps | 0 | 0
Existing | CZ14 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ14 | cDXOH | Humidification | 0 | 0
Existing | CZ14 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ14 | cDXOH | Water Systems | 0 | 225863.27
Existing | CZ14 | cDXOH | Refrigeration | 0 | 0
Existing | CZ14 | cDXOH | Generators | 0 | 0
Existing | CZ14 | cDXOH | Total End Uses | 1224221.34 | 371565.22
Existing | CZ15 | cDXOH | Heating | 0 | 0
Existing | CZ15 | cDXOH | Cooling | 496200.02 | 0
Existing | CZ15 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ15 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ15 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXOH | Fans | 351951.4 | 0
Existing | CZ15 | cDXOH | Pumps | 0 | 0
Existing | CZ15 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ15 | cDXOH | Humidification | 0 | 0
Existing | CZ15 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ15 | cDXOH | Water Systems | 0 | 200447.14
Existing | CZ15 | cDXOH | Refrigeration | 0 | 0
Existing | CZ15 | cDXOH | Generators | 0 | 0
Existing | CZ15 | cDXOH | Total End Uses | 1345093.16 | 346149.09
Existing | CZ16 | cDXOH | Heating | 0 | 35.56
Existing | CZ16 | cDXOH | Cooling | 234696.43 | 0
Existing | CZ16 | cDXOH | Interior Lighting | 216717.02 | 0
Existing | CZ16 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXOH | Interior Equipment | 280224.73 | 145701.95
Existing | CZ16 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXOH | Fans | 363430.95 | 0
Existing | CZ16 | cDXOH | Pumps | 0 | 0
Existing | CZ16 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ16 | cDXOH | Humidification | 0 | 0
Existing | CZ16 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ16 | cDXOH | Water Systems | 0 | 267250.68
Existing | CZ16 | cDXOH | Refrigeration | 0 | 0
Existing | CZ16 | cDXOH | Generators | 0 | 0
Existing | CZ16 | cDXOH | Total End Uses | 1095069.13 | 412988.18
New Construction | CZ01 | cDXOH | Heating | 0 | 0
New Construction | CZ01 | cDXOH | Cooling | 21486.5 | 0
New Construction | CZ01 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ01 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ01 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXOH | Fans | 180862.48 | 0
New Construction | CZ01 | cDXOH | Pumps | 0 | 0
New Construction | CZ01 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXOH | Humidification | 0 | 0
New Construction | CZ01 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXOH | Water Systems | 0 | 297299.76
New Construction | CZ01 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ01 | cDXOH | Generators | 0 | 0
New Construction | CZ01 | cDXOH | Total End Uses | 585972.07 | 443001.7
New Construction | CZ02 | cDXOH | Heating | 0 | 0
New Construction | CZ02 | cDXOH | Cooling | 86269.06 | 0
New Construction | CZ02 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ02 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ02 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXOH | Fans | 194421.44 | 0
New Construction | CZ02 | cDXOH | Pumps | 0 | 0
New Construction | CZ02 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXOH | Humidification | 0 | 0
New Construction | CZ02 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXOH | Water Systems | 0 | 272725.66
New Construction | CZ02 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ02 | cDXOH | Generators | 0 | 0
New Construction | CZ02 | cDXOH | Total End Uses | 664313.6 | 418427.61
New Construction | CZ03 | cDXOH | Heating | 0 | 0
New Construction | CZ03 | cDXOH | Cooling | 59349.39 | 0
New Construction | CZ03 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ03 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ03 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXOH | Fans | 191673.9 | 0
New Construction | CZ03 | cDXOH | Pumps | 0 | 0
New Construction | CZ03 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXOH | Humidification | 0 | 0
New Construction | CZ03 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXOH | Water Systems | 0 | 271858.33
New Construction | CZ03 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ03 | cDXOH | Generators | 0 | 0
New Construction | CZ03 | cDXOH | Total End Uses | 634646.39 | 417560.28
New Construction | CZ04 | cDXOH | Heating | 0 | 0
New Construction | CZ04 | cDXOH | Cooling | 102697.3 | 0
New Construction | CZ04 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ04 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ04 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXOH | Fans | 194607.99 | 0
New Construction | CZ04 | cDXOH | Pumps | 0 | 0
New Construction | CZ04 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXOH | Humidification | 0 | 0
New Construction | CZ04 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXOH | Water Systems | 0 | 262176.88
New Construction | CZ04 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ04 | cDXOH | Generators | 0 | 0
New Construction | CZ04 | cDXOH | Total End Uses | 680928.38 | 407878.83
New Construction | CZ05 | cDXOH | Heating | 0 | 0
New Construction | CZ05 | cDXOH | Cooling | 70850.54 | 0
New Construction | CZ05 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ05 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ05 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXOH | Fans | 190277.85 | 0
New Construction | CZ05 | cDXOH | Pumps | 0 | 0
New Construction | CZ05 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXOH | Humidification | 0 | 0
New Construction | CZ05 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXOH | Water Systems | 0 | 271742.92
New Construction | CZ05 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ05 | cDXOH | Generators | 0 | 0
New Construction | CZ05 | cDXOH | Total End Uses | 644751.48 | 417444.86
New Construction | CZ06 | cDXOH | Heating | 0 | 0
New Construction | CZ06 | cDXOH | Cooling | 112894.6 | 0
New Construction | CZ06 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ06 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ06 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXOH | Fans | 202891.49 | 0
New Construction | CZ06 | cDXOH | Pumps | 0 | 0
New Construction | CZ06 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXOH | Humidification | 0 | 0
New Construction | CZ06 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXOH | Water Systems | 0 | 250349.56
New Construction | CZ06 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ06 | cDXOH | Generators | 0 | 0
New Construction | CZ06 | cDXOH | Total End Uses | 699409.18 | 396051.51
New Construction | CZ07 | cDXOH | Heating | 0 | 0
New Construction | CZ07 | cDXOH | Cooling | 122564 | 0
New Construction | CZ07 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ07 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ07 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXOH | Fans | 201239.43 | 0
New Construction | CZ07 | cDXOH | Pumps | 0 | 0
New Construction | CZ07 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXOH | Humidification | 0 | 0
New Construction | CZ07 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXOH | Water Systems | 0 | 246959.32
New Construction | CZ07 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ07 | cDXOH | Generators | 0 | 0
New Construction | CZ07 | cDXOH | Total End Uses | 707426.53 | 392661.27
New Construction | CZ08 | cDXOH | Heating | 0 | 0
New Construction | CZ08 | cDXOH | Cooling | 139356.42 | 0
New Construction | CZ08 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ08 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ08 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXOH | Fans | 207314.48 | 0
New Construction | CZ08 | cDXOH | Pumps | 0 | 0
New Construction | CZ08 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXOH | Humidification | 0 | 0
New Construction | CZ08 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXOH | Water Systems | 0 | 246590.49
New Construction | CZ08 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ08 | cDXOH | Generators | 0 | 0
New Construction | CZ08 | cDXOH | Total End Uses | 730294 | 392292.44
New Construction | CZ09 | cDXOH | Heating | 0 | 0
New Construction | CZ09 | cDXOH | Cooling | 152538.7 | 0
New Construction | CZ09 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ09 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ09 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXOH | Fans | 199180.12 | 0
New Construction | CZ09 | cDXOH | Pumps | 0 | 0
New Construction | CZ09 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXOH | Humidification | 0 | 0
New Construction | CZ09 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXOH | Water Systems | 0 | 243050.67
New Construction | CZ09 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ09 | cDXOH | Generators | 0 | 0
New Construction | CZ09 | cDXOH | Total End Uses | 735341.91 | 388752.62
New Construction | CZ10 | cDXOH | Heating | 0 | 0
New Construction | CZ10 | cDXOH | Cooling | 190546.21 | 0
New Construction | CZ10 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ10 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ10 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXOH | Fans | 208031.38 | 0
New Construction | CZ10 | cDXOH | Pumps | 0 | 0
New Construction | CZ10 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXOH | Humidification | 0 | 0
New Construction | CZ10 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXOH | Water Systems | 0 | 240314.23
New Construction | CZ10 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ10 | cDXOH | Generators | 0 | 0
New Construction | CZ10 | cDXOH | Total End Uses | 782200.69 | 386016.18
New Construction | CZ11 | cDXOH | Heating | 0 | 0
New Construction | CZ11 | cDXOH | Cooling | 197454.29 | 0
New Construction | CZ11 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ11 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ11 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXOH | Fans | 213429.32 | 0
New Construction | CZ11 | cDXOH | Pumps | 0 | 0
New Construction | CZ11 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXOH | Humidification | 0 | 0
New Construction | CZ11 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXOH | Water Systems | 0 | 245323.13
New Construction | CZ11 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ11 | cDXOH | Generators | 0 | 0
New Construction | CZ11 | cDXOH | Total End Uses | 794506.71 | 391025.07
New Construction | CZ12 | cDXOH | Heating | 0 | 0
New Construction | CZ12 | cDXOH | Cooling | 165841.51 | 0
New Construction | CZ12 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ12 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ12 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXOH | Fans | 203618.39 | 0
New Construction | CZ12 | cDXOH | Pumps | 0 | 0
New Construction | CZ12 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXOH | Humidification | 0 | 0
New Construction | CZ12 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXOH | Water Systems | 0 | 252760.46
New Construction | CZ12 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ12 | cDXOH | Generators | 0 | 0
New Construction | CZ12 | cDXOH | Total End Uses | 753082.99 | 398462.41
New Construction | CZ13 | cDXOH | Heating | 0 | 0
New Construction | CZ13 | cDXOH | Cooling | 221470.24 | 0
New Construction | CZ13 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ13 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ13 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXOH | Fans | 215214.34 | 0
New Construction | CZ13 | cDXOH | Pumps | 0 | 0
New Construction | CZ13 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXOH | Humidification | 0 | 0
New Construction | CZ13 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXOH | Water Systems | 0 | 237997.8
New Construction | CZ13 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ13 | cDXOH | Generators | 0 | 0
New Construction | CZ13 | cDXOH | Total End Uses | 820307.67 | 383699.75
New Construction | CZ14 | cDXOH | Heating | 0 | 0
New Construction | CZ14 | cDXOH | Cooling | 278953.25 | 0
New Construction | CZ14 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ14 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ14 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXOH | Fans | 233142.03 | 0
New Construction | CZ14 | cDXOH | Pumps | 0 | 0
New Construction | CZ14 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXOH | Humidification | 0 | 0
New Construction | CZ14 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXOH | Water Systems | 0 | 225445.27
New Construction | CZ14 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ14 | cDXOH | Generators | 0 | 0
New Construction | CZ14 | cDXOH | Total End Uses | 895718.37 | 371147.21
New Construction | CZ15 | cDXOH | Heating | 0 | 0
New Construction | CZ15 | cDXOH | Cooling | 377648.16 | 0
New Construction | CZ15 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ15 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ15 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXOH | Fans | 223760.43 | 0
New Construction | CZ15 | cDXOH | Pumps | 0 | 0
New Construction | CZ15 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXOH | Humidification | 0 | 0
New Construction | CZ15 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXOH | Water Systems | 0 | 200051.49
New Construction | CZ15 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ15 | cDXOH | Generators | 0 | 0
New Construction | CZ15 | cDXOH | Total End Uses | 985031.69 | 345753.43
New Construction | CZ16 | cDXOH | Heating | 0 | 2.83
New Construction | CZ16 | cDXOH | Cooling | 180357.65 | 0
New Construction | CZ16 | cDXOH | Interior Lighting | 103398.36 | 0
New Construction | CZ16 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXOH | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ16 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXOH | Fans | 246026.24 | 0
New Construction | CZ16 | cDXOH | Pumps | 0 | 0
New Construction | CZ16 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXOH | Humidification | 0 | 0
New Construction | CZ16 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXOH | Water Systems | 0 | 266969.5
New Construction | CZ16 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ16 | cDXOH | Generators | 0 | 0
New Construction | CZ16 | cDXOH | Total End Uses | 810006.98 | 412674.28
Existing | CZ01 | cPVVG | Heating | 0 | 268532.33
Existing | CZ01 | cPVVG | Cooling | 28110.16 | 0
Existing | CZ01 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ01 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ01 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ01 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ01 | cPVVG | Fans | 109813.65 | 0
Existing | CZ01 | cPVVG | Pumps | 0 | 0
Existing | CZ01 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ01 | cPVVG | Humidification | 0 | 0
Existing | CZ01 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ01 | cPVVG | Water Systems | 0 | 297521.34
Existing | CZ01 | cPVVG | Refrigeration | 0 | 0
Existing | CZ01 | cPVVG | Generators | 0 | 0
Existing | CZ01 | cPVVG | Total End Uses | 634865.56 | 711755.62
Existing | CZ02 | cPVVG | Heating | 0 | 148496.79
Existing | CZ02 | cPVVG | Cooling | 112545.13 | 0
Existing | CZ02 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ02 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ02 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ02 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ02 | cPVVG | Fans | 138605.08 | 0
Existing | CZ02 | cPVVG | Pumps | 0 | 0
Existing | CZ02 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ02 | cPVVG | Humidification | 0 | 0
Existing | CZ02 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ02 | cPVVG | Water Systems | 0 | 273002.76
Existing | CZ02 | cPVVG | Refrigeration | 0 | 0
Existing | CZ02 | cPVVG | Generators | 0 | 0
Existing | CZ02 | cPVVG | Total End Uses | 748091.97 | 567201.5
Existing | CZ03 | cPVVG | Heating | 0 | 94810.78
Existing | CZ03 | cPVVG | Cooling | 81160.9 | 0
Existing | CZ03 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ03 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ03 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ03 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ03 | cPVVG | Fans | 128019.28 | 0
Existing | CZ03 | cPVVG | Pumps | 0 | 0
Existing | CZ03 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ03 | cPVVG | Humidification | 0 | 0
Existing | CZ03 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ03 | cPVVG | Water Systems | 0 | 272187.2
Existing | CZ03 | cPVVG | Refrigeration | 0 | 0
Existing | CZ03 | cPVVG | Generators | 0 | 0
Existing | CZ03 | cPVVG | Total End Uses | 706121.93 | 512699.92
Existing | CZ04 | cPVVG | Heating | 0 | 84162.43
Existing | CZ04 | cPVVG | Cooling | 134964.23 | 0
Existing | CZ04 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ04 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ04 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ04 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ04 | cPVVG | Fans | 143093.82 | 0
Existing | CZ04 | cPVVG | Pumps | 0 | 0
Existing | CZ04 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ04 | cPVVG | Humidification | 0 | 0
Existing | CZ04 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ04 | cPVVG | Water Systems | 0 | 262542.14
Existing | CZ04 | cPVVG | Refrigeration | 0 | 0
Existing | CZ04 | cPVVG | Generators | 0 | 0
Existing | CZ04 | cPVVG | Total End Uses | 774999.8 | 492406.51
Existing | CZ05 | cPVVG | Heating | 0 | 84369.59
Existing | CZ05 | cPVVG | Cooling | 95802.44 | 0
Existing | CZ05 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ05 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ05 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ05 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ05 | cPVVG | Fans | 131739.39 | 0
Existing | CZ05 | cPVVG | Pumps | 0 | 0
Existing | CZ05 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ05 | cPVVG | Humidification | 0 | 0
Existing | CZ05 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ05 | cPVVG | Water Systems | 0 | 272213.51
Existing | CZ05 | cPVVG | Refrigeration | 0 | 0
Existing | CZ05 | cPVVG | Generators | 0 | 0
Existing | CZ05 | cPVVG | Total End Uses | 724483.58 | 502285.05
Existing | CZ06 | cPVVG | Heating | 0 | 22373.79
Existing | CZ06 | cPVVG | Cooling | 150100.68 | 0
Existing | CZ06 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ06 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ06 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ06 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ06 | cPVVG | Fans | 147508.66 | 0
Existing | CZ06 | cPVVG | Pumps | 0 | 0
Existing | CZ06 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ06 | cPVVG | Humidification | 0 | 0
Existing | CZ06 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ06 | cPVVG | Water Systems | 0 | 250746.44
Existing | CZ06 | cPVVG | Refrigeration | 0 | 0
Existing | CZ06 | cPVVG | Generators | 0 | 0
Existing | CZ06 | cPVVG | Total End Uses | 794551.09 | 418822.18
Existing | CZ07 | cPVVG | Heating | 0 | 21651.03
Existing | CZ07 | cPVVG | Cooling | 159408.78 | 0
Existing | CZ07 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ07 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ07 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ07 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ07 | cPVVG | Fans | 146413.04 | 0
Existing | CZ07 | cPVVG | Pumps | 0 | 0
Existing | CZ07 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ07 | cPVVG | Humidification | 0 | 0
Existing | CZ07 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ07 | cPVVG | Water Systems | 0 | 247355.35
Existing | CZ07 | cPVVG | Refrigeration | 0 | 0
Existing | CZ07 | cPVVG | Generators | 0 | 0
Existing | CZ07 | cPVVG | Total End Uses | 802763.57 | 414708.33
Existing | CZ08 | cPVVG | Heating | 0 | 30793.21
Existing | CZ08 | cPVVG | Cooling | 180286.94 | 0
Existing | CZ08 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ08 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ08 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ08 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ08 | cPVVG | Fans | 153680.06 | 0
Existing | CZ08 | cPVVG | Pumps | 0 | 0
Existing | CZ08 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ08 | cPVVG | Humidification | 0 | 0
Existing | CZ08 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ08 | cPVVG | Water Systems | 0 | 246943.28
Existing | CZ08 | cPVVG | Refrigeration | 0 | 0
Existing | CZ08 | cPVVG | Generators | 0 | 0
Existing | CZ08 | cPVVG | Total End Uses | 830908.75 | 423438.43
Existing | CZ09 | cPVVG | Heating | 0 | 24291.81
Existing | CZ09 | cPVVG | Cooling | 203467.57 | 0
Existing | CZ09 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ09 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ09 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ09 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ09 | cPVVG | Fans | 165330.13 | 0
Existing | CZ09 | cPVVG | Pumps | 0 | 0
Existing | CZ09 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ09 | cPVVG | Humidification | 0 | 0
Existing | CZ09 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ09 | cPVVG | Water Systems | 0 | 243516.87
Existing | CZ09 | cPVVG | Refrigeration | 0 | 0
Existing | CZ09 | cPVVG | Generators | 0 | 0
Existing | CZ09 | cPVVG | Total End Uses | 865739.45 | 413510.63
Existing | CZ10 | cPVVG | Heating | 0 | 59931.01
Existing | CZ10 | cPVVG | Cooling | 236661.63 | 0
Existing | CZ10 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ10 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ10 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ10 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ10 | cPVVG | Fans | 163371.81 | 0
Existing | CZ10 | cPVVG | Pumps | 0 | 0
Existing | CZ10 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ10 | cPVVG | Humidification | 0 | 0
Existing | CZ10 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ10 | cPVVG | Water Systems | 0 | 240777.35
Existing | CZ10 | cPVVG | Refrigeration | 0 | 0
Existing | CZ10 | cPVVG | Generators | 0 | 0
Existing | CZ10 | cPVVG | Total End Uses | 896975.19 | 446410.3
Existing | CZ11 | cPVVG | Heating | 0 | 148540.59
Existing | CZ11 | cPVVG | Cooling | 252785.37 | 0
Existing | CZ11 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ11 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ11 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ11 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ11 | cPVVG | Fans | 180775.43 | 0
Existing | CZ11 | cPVVG | Pumps | 0 | 0
Existing | CZ11 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ11 | cPVVG | Humidification | 0 | 0
Existing | CZ11 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ11 | cPVVG | Water Systems | 0 | 245693.03
Existing | CZ11 | cPVVG | Refrigeration | 0 | 0
Existing | CZ11 | cPVVG | Generators | 0 | 0
Existing | CZ11 | cPVVG | Total End Uses | 930502.55 | 539935.57
Existing | CZ12 | cPVVG | Heating | 0 | 129210.97
Existing | CZ12 | cPVVG | Cooling | 212564.28 | 0
Existing | CZ12 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ12 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ12 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ12 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ12 | cPVVG | Fans | 163257.51 | 0
Existing | CZ12 | cPVVG | Pumps | 0 | 0
Existing | CZ12 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ12 | cPVVG | Humidification | 0 | 0
Existing | CZ12 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ12 | cPVVG | Water Systems | 0 | 253151.21
Existing | CZ12 | cPVVG | Refrigeration | 0 | 0
Existing | CZ12 | cPVVG | Generators | 0 | 0
Existing | CZ12 | cPVVG | Total End Uses | 872763.54 | 528064.12
Existing | CZ13 | cPVVG | Heating | 0 | 102584.28
Existing | CZ13 | cPVVG | Cooling | 284130.33 | 0
Existing | CZ13 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ13 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ13 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ13 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ13 | cPVVG | Fans | 184907.99 | 0
Existing | CZ13 | cPVVG | Pumps | 0 | 0
Existing | CZ13 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ13 | cPVVG | Humidification | 0 | 0
Existing | CZ13 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ13 | cPVVG | Water Systems | 0 | 238454.76
Existing | CZ13 | cPVVG | Refrigeration | 0 | 0
Existing | CZ13 | cPVVG | Generators | 0 | 0
Existing | CZ13 | cPVVG | Total End Uses | 965980.07 | 486741
Existing | CZ14 | cPVVG | Heating | 0 | 63411.57
Existing | CZ14 | cPVVG | Cooling | 349207.19 | 0
Existing | CZ14 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ14 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ14 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ14 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ14 | cPVVG | Fans | 207034.22 | 0
Existing | CZ14 | cPVVG | Pumps | 0 | 0
Existing | CZ14 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ14 | cPVVG | Humidification | 0 | 0
Existing | CZ14 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ14 | cPVVG | Water Systems | 0 | 225864.05
Existing | CZ14 | cPVVG | Refrigeration | 0 | 0
Existing | CZ14 | cPVVG | Generators | 0 | 0
Existing | CZ14 | cPVVG | Total End Uses | 1053183.16 | 434977.56
Existing | CZ15 | cPVVG | Heating | 0 | 21952.87
Existing | CZ15 | cPVVG | Cooling | 475036.82 | 0
Existing | CZ15 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ15 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ15 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ15 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ15 | cPVVG | Fans | 217407.33 | 0
Existing | CZ15 | cPVVG | Pumps | 0 | 0
Existing | CZ15 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ15 | cPVVG | Humidification | 0 | 0
Existing | CZ15 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ15 | cPVVG | Water Systems | 0 | 200438.34
Existing | CZ15 | cPVVG | Refrigeration | 0 | 0
Existing | CZ15 | cPVVG | Generators | 0 | 0
Existing | CZ15 | cPVVG | Total End Uses | 1189385.9 | 368093.15
Existing | CZ16 | cPVVG | Heating | 0 | 196126.91
Existing | CZ16 | cPVVG | Cooling | 224758.58 | 0
Existing | CZ16 | cPVVG | Interior Lighting | 216717.02 | 0
Existing | CZ16 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ16 | cPVVG | Interior Equipment | 280224.73 | 145701.95
Existing | CZ16 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ16 | cPVVG | Fans | 195675.12 | 0
Existing | CZ16 | cPVVG | Pumps | 0 | 0
Existing | CZ16 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ16 | cPVVG | Humidification | 0 | 0
Existing | CZ16 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ16 | cPVVG | Water Systems | 0 | 267247.63
Existing | CZ16 | cPVVG | Refrigeration | 0 | 0
Existing | CZ16 | cPVVG | Generators | 0 | 0
Existing | CZ16 | cPVVG | Total End Uses | 917375.45 | 609076.48
New Construction | CZ01 | cPVVG | Heating | 0 | 293689.35
New Construction | CZ01 | cPVVG | Cooling | 23754.59 | 0
New Construction | CZ01 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ01 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ01 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ01 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ01 | cPVVG | Fans | 86768.22 | 0
New Construction | CZ01 | cPVVG | Pumps | 0 | 0
New Construction | CZ01 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ01 | cPVVG | Humidification | 0 | 0
New Construction | CZ01 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ01 | cPVVG | Water Systems | 0 | 297224.9
New Construction | CZ01 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ01 | cPVVG | Generators | 0 | 0
New Construction | CZ01 | cPVVG | Total End Uses | 494145.9 | 736616.2
New Construction | CZ02 | cPVVG | Heating | 0 | 156137.8
New Construction | CZ02 | cPVVG | Cooling | 87415.06 | 0
New Construction | CZ02 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ02 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ02 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ02 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ02 | cPVVG | Fans | 100346.84 | 0
New Construction | CZ02 | cPVVG | Pumps | 0 | 0
New Construction | CZ02 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ02 | cPVVG | Humidification | 0 | 0
New Construction | CZ02 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ02 | cPVVG | Water Systems | 0 | 272650.03
New Construction | CZ02 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ02 | cPVVG | Generators | 0 | 0
New Construction | CZ02 | cPVVG | Total End Uses | 571384.99 | 574489.77
New Construction | CZ03 | cPVVG | Heating | 0 | 115161.48
New Construction | CZ03 | cPVVG | Cooling | 61867.47 | 0
New Construction | CZ03 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ03 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ03 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ03 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ03 | cPVVG | Fans | 95303.06 | 0
New Construction | CZ03 | cPVVG | Pumps | 0 | 0
New Construction | CZ03 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ03 | cPVVG | Humidification | 0 | 0
New Construction | CZ03 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ03 | cPVVG | Water Systems | 0 | 271843.84
New Construction | CZ03 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ03 | cPVVG | Generators | 0 | 0
New Construction | CZ03 | cPVVG | Total End Uses | 540793.63 | 532707.27
New Construction | CZ04 | cPVVG | Heating | 0 | 96998.5
New Construction | CZ04 | cPVVG | Cooling | 102396.42 | 0
New Construction | CZ04 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ04 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ04 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ04 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ04 | cPVVG | Fans | 102472.52 | 0
New Construction | CZ04 | cPVVG | Pumps | 0 | 0
New Construction | CZ04 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ04 | cPVVG | Humidification | 0 | 0
New Construction | CZ04 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ04 | cPVVG | Water Systems | 0 | 262199.12
New Construction | CZ04 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ04 | cPVVG | Generators | 0 | 0
New Construction | CZ04 | cPVVG | Total End Uses | 588492.03 | 504899.56
New Construction | CZ05 | cPVVG | Heating | 0 | 108223
New Construction | CZ05 | cPVVG | Cooling | 72808.61 | 0
New Construction | CZ05 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ05 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ05 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ05 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ05 | cPVVG | Fans | 97192.01 | 0
New Construction | CZ05 | cPVVG | Pumps | 0 | 0
New Construction | CZ05 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ05 | cPVVG | Humidification | 0 | 0
New Construction | CZ05 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ05 | cPVVG | Water Systems | 0 | 271857.39
New Construction | CZ05 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ05 | cPVVG | Generators | 0 | 0
New Construction | CZ05 | cPVVG | Total End Uses | 553623.71 | 525782.33
New Construction | CZ06 | cPVVG | Heating | 0 | 34256.67
New Construction | CZ06 | cPVVG | Cooling | 112460.58 | 0
New Construction | CZ06 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ06 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ06 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ06 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ06 | cPVVG | Fans | 108684.22 | 0
New Construction | CZ06 | cPVVG | Pumps | 0 | 0
New Construction | CZ06 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ06 | cPVVG | Humidification | 0 | 0
New Construction | CZ06 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ06 | cPVVG | Water Systems | 0 | 250274.67
New Construction | CZ06 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ06 | cPVVG | Generators | 0 | 0
New Construction | CZ06 | cPVVG | Total End Uses | 604767.9 | 430233.29
New Construction | CZ07 | cPVVG | Heating | 0 | 32658.44
New Construction | CZ07 | cPVVG | Cooling | 119439.65 | 0
New Construction | CZ07 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ07 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ07 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ07 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ07 | cPVVG | Fans | 107763.02 | 0
New Construction | CZ07 | cPVVG | Pumps | 0 | 0
New Construction | CZ07 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ07 | cPVVG | Humidification | 0 | 0
New Construction | CZ07 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ07 | cPVVG | Water Systems | 0 | 246947.42
New Construction | CZ07 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ07 | cPVVG | Generators | 0 | 0
New Construction | CZ07 | cPVVG | Total End Uses | 610825.76 | 425307.81
New Construction | CZ08 | cPVVG | Heating | 0 | 44392.87
New Construction | CZ08 | cPVVG | Cooling | 137307.09 | 0
New Construction | CZ08 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ08 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ08 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ08 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ08 | cPVVG | Fans | 111960.52 | 0
New Construction | CZ08 | cPVVG | Pumps | 0 | 0
New Construction | CZ08 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ08 | cPVVG | Humidification | 0 | 0
New Construction | CZ08 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ08 | cPVVG | Water Systems | 0 | 246551.79
New Construction | CZ08 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ08 | cPVVG | Generators | 0 | 0
New Construction | CZ08 | cPVVG | Total End Uses | 632890.7 | 436646.61
New Construction | CZ09 | cPVVG | Heating | 0 | 30919.46
New Construction | CZ09 | cPVVG | Cooling | 148864.81 | 0
New Construction | CZ09 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ09 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ09 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ09 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ09 | cPVVG | Fans | 111644.88 | 0
New Construction | CZ09 | cPVVG | Pumps | 0 | 0
New Construction | CZ09 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ09 | cPVVG | Humidification | 0 | 0
New Construction | CZ09 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ09 | cPVVG | Water Systems | 0 | 243139.23
New Construction | CZ09 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ09 | cPVVG | Generators | 0 | 0
New Construction | CZ09 | cPVVG | Total End Uses | 644132.79 | 419760.64
New Construction | CZ10 | cPVVG | Heating | 0 | 68933.23
New Construction | CZ10 | cPVVG | Cooling | 186543.88 | 0
New Construction | CZ10 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ10 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ10 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ10 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ10 | cPVVG | Fans | 119014.05 | 0
New Construction | CZ10 | cPVVG | Pumps | 0 | 0
New Construction | CZ10 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ10 | cPVVG | Humidification | 0 | 0
New Construction | CZ10 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ10 | cPVVG | Water Systems | 0 | 240452.65
New Construction | CZ10 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ10 | cPVVG | Generators | 0 | 0
New Construction | CZ10 | cPVVG | Total End Uses | 689181.03 | 455087.82
New Construction | CZ11 | cPVVG | Heating | 0 | 150177.53
New Construction | CZ11 | cPVVG | Cooling | 193536.29 | 0
New Construction | CZ11 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ11 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ11 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ11 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ11 | cPVVG | Fans | 122969.09 | 0
New Construction | CZ11 | cPVVG | Pumps | 0 | 0
New Construction | CZ11 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ11 | cPVVG | Humidification | 0 | 0
New Construction | CZ11 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ11 | cPVVG | Water Systems | 0 | 245286.9
New Construction | CZ11 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ11 | cPVVG | Generators | 0 | 0
New Construction | CZ11 | cPVVG | Total End Uses | 700128.48 | 541166.37
New Construction | CZ12 | cPVVG | Heating | 0 | 133856.25
New Construction | CZ12 | cPVVG | Cooling | 163253.36 | 0
New Construction | CZ12 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ12 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ12 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ12 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ12 | cPVVG | Fans | 115079.67 | 0
New Construction | CZ12 | cPVVG | Pumps | 0 | 0
New Construction | CZ12 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ12 | cPVVG | Humidification | 0 | 0
New Construction | CZ12 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ12 | cPVVG | Water Systems | 0 | 252788.23
New Construction | CZ12 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ12 | cPVVG | Generators | 0 | 0
New Construction | CZ12 | cPVVG | Total End Uses | 661956.13 | 532346.42
New Construction | CZ13 | cPVVG | Heating | 0 | 110560.05
New Construction | CZ13 | cPVVG | Cooling | 216721.81 | 0
New Construction | CZ13 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ13 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ13 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ13 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ13 | cPVVG | Fans | 126482.84 | 0
New Construction | CZ13 | cPVVG | Pumps | 0 | 0
New Construction | CZ13 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ13 | cPVVG | Humidification | 0 | 0
New Construction | CZ13 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ13 | cPVVG | Water Systems | 0 | 238037.31
New Construction | CZ13 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ13 | cPVVG | Generators | 0 | 0
New Construction | CZ13 | cPVVG | Total End Uses | 726827.75 | 494299.3
New Construction | CZ14 | cPVVG | Heating | 0 | 73226.9
New Construction | CZ14 | cPVVG | Cooling | 271165.65 | 0
New Construction | CZ14 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ14 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ14 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ14 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ14 | cPVVG | Fans | 142720.08 | 0
New Construction | CZ14 | cPVVG | Pumps | 0 | 0
New Construction | CZ14 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ14 | cPVVG | Humidification | 0 | 0
New Construction | CZ14 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ14 | cPVVG | Water Systems | 0 | 225467.29
New Construction | CZ14 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ14 | cPVVG | Generators | 0 | 0
New Construction | CZ14 | cPVVG | Total End Uses | 797508.82 | 444396.13
New Construction | CZ15 | cPVVG | Heating | 0 | 28113.09
New Construction | CZ15 | cPVVG | Cooling | 368817.63 | 0
New Construction | CZ15 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ15 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ15 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ15 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ15 | cPVVG | Fans | 150642.3 | 0
New Construction | CZ15 | cPVVG | Pumps | 0 | 0
New Construction | CZ15 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ15 | cPVVG | Humidification | 0 | 0
New Construction | CZ15 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ15 | cPVVG | Water Systems | 0 | 200001.72
New Construction | CZ15 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ15 | cPVVG | Generators | 0 | 0
New Construction | CZ15 | cPVVG | Total End Uses | 903083.02 | 373816.75
New Construction | CZ16 | cPVVG | Heating | 0 | 195145.71
New Construction | CZ16 | cPVVG | Cooling | 176725.27 | 0
New Construction | CZ16 | cPVVG | Interior Lighting | 103398.36 | 0
New Construction | CZ16 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ16 | cPVVG | Interior Equipment | 280224.73 | 145701.95
New Construction | CZ16 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ16 | cPVVG | Fans | 137467.09 | 0
New Construction | CZ16 | cPVVG | Pumps | 0 | 0
New Construction | CZ16 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ16 | cPVVG | Humidification | 0 | 0
New Construction | CZ16 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ16 | cPVVG | Water Systems | 0 | 266810.86
New Construction | CZ16 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ16 | cPVVG | Generators | 0 | 0
New Construction | CZ16 | cPVVG | Total End Uses | 697815.45 | 607658.51

## PV
PV - Education - Primary School (NA)

## EV Charger
EV Charger - Education - Primary School (NA)

## Raw_building (hidden)
Building Type | Building Category | Roof Type | Window Wall Ratio (%)
Education - Primary School | Nonresidential | Flat Roof | 20.99

## Raw_windowdimensionsillheight (hidden)
Window Name | Width [ft] | Height [ft] | Sill Height [ft]
EL1 NORTH WIN (G.NNE2.E1.W1) | 58.07 | 6 | 3
EL1 SOUTH WIN (G.SSE3.E2.W1) | 58.07 | 6 | 3
EL1 NORTH WIN (G.W4.E4.W1) | 15.72 | 6 | 3
EL1 SOUTH WIN (G.W4.E3.W1) | 15.72 | 6 | 3
EL1 WEST WIN (G.W4.E5.W1) | 58.6 | 6 | 3
EL2 EAST WIN (G.SSW1.E2.W1) | 6.46 | 6.27 | 3
EL2 SOUTH WIN (G.SSW1.E1.W1) | 21.62 | 6.27 | 3
EL2 EAST WIN (G.N2.E5.W1) | 11.81 | 6.27 | 3
EL2 NORTH WIN (G.N2.E4.W1) | 21.62 | 6.27 | 3
EL2 EAST WIN (G.E3.E7.W1) | 10.93 | 6.27 | 3

## Raw_shadinggeometry (hidden)
Shading Name | Width [ft] | Length [ft]
No Shading

## Raw_zonesummary (hidden)
Vintage | Space | Zone Name | Conditioned | Area (Excluding Plenums and CrawlSpace) (ft2) | Area (Including Plenums and CrawlSpace) (ft2) | Width (ft) | Length (ft) | Volume (ft3) | Multipliers | People (Persons/1000 ft2) | Lighting (Btu/h-ft2) | Plug Loads (Btu/h-ft2) | Outdoor Air Flow per Person (cfm/person) | Outdoor Air Flow per Zone Floor Area (cfm/ft2) | Zone Type | HVAC System Identifier | Schedule Identifier | Height (ft)
Existing | CLASSROOM G.E1 | CLASSROOM G.E1 | Yes | 5751.45 | 5751.45 | 110.86 | 51.87 | 51765.56 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
Existing | CLASSROOM G.NNE2 | CLASSROOM G.NNE2 | Yes | 3321.4 | 3321.4 | 110.86 | 29.95 | 29894.07 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
Existing | CLASSROOM G.SSE3 | CLASSROOM G.SSE3 | Yes | 3321.39 | 3321.39 | 110.86 | 29.95 | 29893.97 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
Existing | CLASSROOM G.W4 | CLASSROOM G.W4 | Yes | 3354.33 | 3354.33 | 29.99 | 111.81 | 30190.42 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
Existing | DINING G.SSW1 | DINING G.SSW1 | Yes | 3754.31 | 3754.31 | 61.25 | 61.25 | 45053.94 | 1 | 33.33 | 4.1409 | 2.5588 | 0.0 | 0.5 | Dining_fast | Main | School | 12.0006
Existing | GYMNASIUM G.N2 | GYMNASIUM G.N2 | Yes | 3747.29 | 3747.29 | 82.74 | 45.28 | 44969.62 | 1 | 33.33 | 3.3597 | 1.7058 | 0.0 | 0.5 | Gym | Main | School | 12.0006
Existing | KITCHEN G.E3 | KITCHEN G.E3 | Yes | 1750.76 | 1750.76 | 41.86 | 41.8 | 21010.09 | 1 | 2.5 | 5.6273 | 26.4716 | 0.0 | 0.15 | Kitchen | Customized | Kitchen | 12.0006
Existing | PLENUM G.E5 | PLENUM G.E5 | No | 5751.45 | 5751.45 | 110.86 | 51.87 | 17255.19 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.0001
Existing | PLENUM G.NNE6 | PLENUM G.NNE6 | No | 3321.4 | 3321.4 | 110.86 | 29.95 | 9964.69 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.0001
Existing | PLENUM G.SSE7 | PLENUM G.SSE7 | No | 3321.39 | 3321.39 | 110.86 | 29.95 | 9964.66 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.0001
Existing | PLENUM G.W8 | PLENUM G.W8 | No | 3354.33 | 3354.33 | 29.99 | 111.81 | 10063.47 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.0001
New Construction | CLASSROOM G.E1 | CLASSROOM G.E1 | Yes | 5751.45 | 5751.45 | 110.86 | 51.87 | 51765.56 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
New Construction | CLASSROOM G.NNE2 | CLASSROOM G.NNE2 | Yes | 3321.4 | 3321.4 | 110.86 | 29.95 | 29894.07 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
New Construction | CLASSROOM G.SSE3 | CLASSROOM G.SSE3 | Yes | 3321.39 | 3321.39 | 110.86 | 29.95 | 29893.97 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
New Construction | CLASSROOM G.W4 | CLASSROOM G.W4 | Yes | 3354.33 | 3354.33 | 29.99 | 111.81 | 30190.42 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
New Construction | DINING G.SSW1 | DINING G.SSW1 | Yes | 3754.31 | 3754.31 | 61.25 | 61.25 | 45053.94 | 1 | 33.33 | 1.5353 | 2.5588 | 0.0 | 0.5 | Dining_fast | Main | School | 12.0006
New Construction | GYMNASIUM G.N2 | GYMNASIUM G.N2 | Yes | 3747.29 | 3747.29 | 82.74 | 45.28 | 44969.62 | 1 | 33.33 | 1.7058 | 1.7058 | 0.0 | 0.5 | Gym | Main | School | 12.0006
New Construction | KITCHEN G.E3 | KITCHEN G.E3 | Yes | 1750.76 | 1750.76 | 41.86 | 41.8 | 21010.09 | 1 | 2.5 | 3.2411 | 26.4716 | 0.0 | 0.15 | Kitchen | Customized | Kitchen | 12.0006
New Construction | PLENUM G.E5 | PLENUM G.E5 | No | 5751.45 | 5751.45 | 110.86 | 51.87 | 17255.19 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.0001
New Construction | PLENUM G.NNE6 | PLENUM G.NNE6 | No | 3321.4 | 3321.4 | 110.86 | 29.95 | 9964.69 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.0001
New Construction | PLENUM G.SSE7 | PLENUM G.SSE7 | No | 3321.39 | 3321.39 | 110.86 | 29.95 | 9964.66 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.0001
New Construction | PLENUM G.W8 | PLENUM G.W8 | No | 3354.33 | 3354.33 | 29.99 | 111.81 | 10063.47 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.0001