## Geometry Summary (hidden)
Abbreviation | Building Type | Shape | Number of Floors | Aspect Ratio | Zone Height_1 | Zone Height_2 | Zone Height_3 | Plenum Height | Floor to Floor Height (feet) | Floor to Ceiling Height (feet)
Asm | Assembly | #VALUE! | 1 | 1 | 12.0006 | na | na | 3.0001 | 12.0006 | 15.0007
ECC | Education - Community College | #VALUE! | 3 | 5.7 | 9.0004 | 13.0006 | na | 4.0002 | 9 / 13 | 13 / 17
EPr | Education - Primary School | #VALUE! | 1 | 2 | 9.0004 | 12.0006 | na | 3.0001 | 9 / 12 | 12 / 15
ERC | Education - Relocatable Classroom | #VALUE! | 1 | 1.7 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
ESe | Education - Secondary School | #VALUE! | 2 | 2.5/1.0 | 9.0004 | 13.0006 | na | 4.0002 | 9 / 13 | 13 / 17
EUn | Education - University | #VALUE! | 4 | 2.0/15.0 | 10.0005 | 9.0004 | 14.0007 | 4.0002 | 9 / 10 / 14 | 13 / 14 / 18
Fin | Financial buildings, incl. banks | #VALUE! | 1 | 1 | 11.0005 | na | na | na | 11.0005 | 11.0005
Gro | Grocery | #VALUE! | 1 | 1 | 25.0012 | na | na | na | 25.0012 | 25.0012
Hsp | Health/Medical - Hospital | #VALUE! | 3 | 1 | 10.007 | 12.9927 | na | 2.9857 | 10 / 13 | 13 / 16
Htl | Lodging - Hotel | #VALUE! | 4 | 6.6 | 8.0004 | 10.5005 | na | 1.5001 | 8 / 11 | 10 / 12
Lib | Libraries | #VALUE! | 1 | 1 | 13.0006 | na | na | na | 13.0006 | 13.0006
MBT | Manufacturing Biotech | #VALUE! | 1 | 6 | 9.0004 | na | na | 6.0003 | 9.0004 | 15.0008
MLI | Manufacturing Light Industrial | #VALUE! | 1 | 1 | 35.0017 | na | na | na | 35.0017 | 35.0017
Mtl | Lodging - Motel | #VALUE! | 2 | 5.1 | 9.0004 | na | na | na | 9.0004 | 9.0004
Nrs | Health/Medical - Nursing Home | #VALUE! | 2 | 10.3 | 12.9986 | 9.0005 | na | 4.0055 | 9 / 13 | 13 / 17
OfL | Office - Large | #VALUE! | 3 | 1.5 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
OfS | Office - Small | #VALUE! | 2 | 1.5 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
Rel | Religious assembly buildings | #VALUE! | 1 | 2.5 | 37.5018 | 15.0007 | na | na | 38 / 15 | 38 / 15
RFF | Restaurant - Fast-Food | #VALUE! | 1 | 1 | 10.0005 | na | na | 3.0002 | 10.0005 | 13.0007
RSD | Restaurant - Sit-Down | #VALUE! | 1 | 1 | 10.0005 | na | na | 3.0001 | 10.0005 | 13.0006
Rt3 | Retail - Multistory Large | #VALUE! | 3 | 1 | 15.0007 | na | na | 5.8002 | 15.0007 | 20.8009
RtL | Retail - Single-Story Large | #VALUE! | 1 | 1 | 20.501 | na | na | na | 20.501 | 20.501
RtS | Retail - Small | #VALUE! | 1 | 1 | 10.0005 | na | na | 2.0001 | 10.0005 | 12.0006
SCn | Storage - Conditioned | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023
SUn | Storage - Unconditioned | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023
WRf | Warehouse - Refrigerated | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023

## Prototype
TRC, Updated Febuary 2026
Health/Medical - Nursing Home
Characteristic | Value
Building Type | Health/Medical - Nursing Home
Building Category | Nonresidential
Vintages | Two vintages: Existing and New Construction
Shape | #VALUE!
Total Floor Area (ft²) | 60006.49
Aspect Ratio | 10.3
Number of Floors | 2
Roof Type | Flat Roof
Gross Window to Wall Ratio (%) | 20
Shading Geometry | No Shading
Floor to Floor Height (feet) | 9 / 13
Floor to Ceiling Height (feet) | 13 / 17
Glazing Sill Height (feet) | 3

## Notes
Prototype Overview
Name | Description
Asm | Assembly
ECC | Education - Community College
EPr | Education - Primary School
ERC | Education - Relocatable Classroom
ESe | Education - Secondary School
EUn | Education - University
Fin | Financial buildings, incl. banks
Gro | Grocery
Hsp | Health/Medical - Hospital
Htl | Lodging - Hotel
Lib | Libraries
MBT | Manufacturing Biotech
MLI | Manufacturing Light Industrial
Mtl | Lodging - Motel
Nrs | Health/Medical - Nursing Home
OfL | Office - Large
OfS | Office - Small
Rel | Religious assembly buildings
RFF | Restaurant - Fast-Food
RSD | Restaurant - Sit-Down
Rt3 | Retail - Multistory Large
RtL | Retail - Single-Story Large
RtS | Retail - Small
SCn | Storage - Conditioned
SUn | Storage - Unconditioned
WRf | Warehouse - Refrigerated
Vintages
Existing | Weighted average of Title 24 requirements based on vintages from 1975 to 2022
New Construction | Title 24 2025
Run Begin Day
Begin Month | Begin Day of Month | Day of Week for Start Day
1 | 1 | Sunday
Special Days
Name | Start Date | Duration (days) | Special Day Type
New Years Day | January 1 | 1 | Holiday
Veterans Day | November 11 | 1 | Holiday
Christmas | December 25 | 1 | Holiday
Independence Day | July 4 | 1 | Holiday
MLK Day | 3rd Monday in January | 1 | Holiday
Presidents Day | 3rd Monday in February | 1 | Holiday
Memorial Day | Last Monday in May | 1 | Holiday
Labor Day | 1st Monday in September | 1 | Holiday
Columbus Day | 2nd Monday in October | 1 | Holiday
Thanksgiving | 4th Thursday in November | 1 | Holiday

## Raw_runbeginday (hidden)
Begin Month | Begin Day of Month | Day of Week for Start Day
1 | 1 | Sunday

## Raw_specialdays (hidden)
Name | Start Day | Duration | Special Day Type
New Years Day | January 1 | 1 | Holiday
Veterans Day | November 11 | 1 | Holiday
Christmas | December 25 | 1 | Holiday
Independence Day | July 4 | 1 | Holiday
MLK Day | 3rd Monday in January | 1 | Holiday
Presidents Day | 3rd Monday in February | 1 | Holiday
Memorial Day | Last Monday in May | 1 | Holiday
Labor Day | 1st Monday in September | 1 | Holiday
Columbus Day | 2nd Monday in October | 1 | Holiday
Thanksgiving | 4th Thursday in November | 1 | Holiday

## Climate Zone
Climate Zones - All Prototypes
Climate Zone | Representative City | Weather File Name
CZ01 | Eureka | CA_EUREKA_725940S_CZ2022.epw
CZ02 | Napa | CA_NAPA-CO_724955S_CZ2022.epw
CZ03 | Oakland | CA_OAKLAND-METRO-AP_724930S_CZ2022.epw
CZ04 | San Jose | CA_SAN-JOSE-IAP_724945S_CZ2022.epw
CZ05 | Santa Maria | CA_SANTA-MARIA-PUBLIC-AP_723940S_CZ2022.epw
CZ06 | Los Angeles | CA_LOS-ANGELES-IAP_722950S_CZ2022.epw
CZ07 | San Diego-Lindbergh | CA_SAN-DIEGO-LINDBERGH-FLD_722900S_CZ2022.epw
CZ08 | Long Beach-Daugherty | CA_LONG-BEACH-DAUGHERTY-FLD_722970S_CZ2022.epw
CZ09 | Los Angeles | CA_LOS-ANGELES-DOWNTOWN-USC_722874S_CZ2022.epw
CZ10 | Riverside | CA_RIVERSIDE-MUNI_722869S_CZ2022.epw
CZ11 | Red Bluff | CA_RED-BLUFF-MUNI-AP_725910S_CZ2022.epw
CZ12 | Stockton | CA_STOCKTON-METRO-AP_724920S_CZ2022.epw
CZ13 | Fresno Yosemite | CA_FRESNO-YOSEMITE-IAP_723890S_CZ2022.epw
CZ14 | Daggett Barstow | CA_DAGGETT-BARSTOW-AP_723815S_CZ2022.epw
CZ15 | El Centro | CA_EL-CENTRO-NAF_722810S_CZ2022.epw
CZ16 | Bishop | CA_BISHOP-AP_724800S_CZ2022.epw
Source: California Energy Commission, https://cecgis-caenergy.opendata.arcgis.com/datasets/CAEnergy::california-building-climate-zones/about

## Zones
Zone Summary - Health/Medical - Nursing Home
Space | Zone Name | Conditioned [Y/N] | Zone Type | HVAC System Identifier (Main/Alternative/Customized) | Schedule Identifier | Area Fraction | Area (Excluding Plenums and Crawl Space) (ft²) | Volume (ft³) | Multipliers | People (Persons/1,000 ft²) | Note
CORRIDOR EL4 CORE SPC (G.C3) | CORRIDOR EL4 CORE SPC (G.C3) | Yes | Corridor | Alternative | Health | 5.547% | 3328.42 | 29957.28 | 1 | 5
DINING EL1 WEST PERIM SPC (G.W1) | DINING EL1 WEST PERIM SPC (G.W1) | Yes | Dining_fast | Main | Office | 10.5% | 6303.51 | 81936.69 | 1 | 33.33
EL2 CORE PLNM (G.4) | EL2 CORE PLNM (G.4) | No | Plenum | - | Plenum | 0% | 0 | 15596.62 | 1 | 0
EL2 NORTH PLNM (G.4) | EL2 NORTH PLNM (G.4) | No | Plenum | - | Plenum | 0% | 0 | 22198.24 | 1 | 0
EL2 SOUTH PLNM (G.4) | EL2 SOUTH PLNM (G.4) | No | Plenum | - | Plenum | 0% | 0 | 22192.59 | 1 | 0
EL3 NORTH PLNM (G.4) | EL3 NORTH PLNM (G.4) | No | Plenum | - | Plenum | 0% | 0 | 8880.6 | 1 | 0
EL3 SOUTH PLNM (G.4) | EL3 SOUTH PLNM (G.4) | No | Plenum | - | Plenum | 0% | 0 | 8890.59 | 1 | 0
EL3 WEST PLNM (G.4) | EL3 WEST PLNM (G.4) | No | Plenum | - | Plenum | 0% | 0 | 6251.26 | 1 | 0
EL4 CORE PLNM (G.4) | EL4 CORE PLNM (G.4) | No | Plenum | - | Plenum | 0% | 0 | 13314.35 | 1 | 0
EL4 NORTH PLNM (G.4) | EL4 NORTH PLNM (G.4) | No | Plenum | - | Plenum | 0% | 0 | 53411.42 | 1 | 0
EL4 SOUTH PLNM (G.4) | EL4 SOUTH PLNM (G.4) | No | Plenum | - | Plenum | 0% | 0 | 53301.05 | 1 | 0
KITCHEN EL1 EAST PERIM SPC (G.E2) | KITCHEN EL1 EAST PERIM SPC (G.E2) | Yes | Kitchen | Customized | Kitchen | 4.503% | 2701.87 | 35120.65 | 1 | 2.5
OFFICE EL2 CORE SPC (G.C1) | OFFICE EL2 CORE SPC (G.C1) | Yes | Office | Main | Office | 6.492% | 3895.75 | 35057.54 | 1 | 5
OFFICE EL2 NORTH PERIM SPC (G.N3) | OFFICE EL2 NORTH PERIM SPC (G.N3) | Yes | Office | Main | Office | 9.248% | 5549.46 | 49947.45 | 1 | 5
OFFICE EL2 SOUTH PERIM SPC (G.S2) | OFFICE EL2 SOUTH PERIM SPC (G.S2) | Yes | Office | Main | Office | 9.248% | 5549.38 | 49946.82 | 1 | 5
OFFICE EL3 NORTH PERIM SPC (G.N3) | OFFICE EL3 NORTH PERIM SPC (G.N3) | Yes | Office | Main | Office | 3.704% | 2222.58 | 20003.95 | 1 | 5
OFFICE EL3 SOUTH PERIM SPC (G.S2) | OFFICE EL3 SOUTH PERIM SPC (G.S2) | Yes | Office | Main | Office | 3.704% | 2222.55 | 20003.91 | 1 | 5
OFFICE EL3 WEST PERIM SPC (G.W1) | OFFICE EL3 WEST PERIM SPC (G.W1) | Yes | Office | Main | Office | 2.6% | 1560.27 | 14043.21 | 1 | 5
PATIENT EL4 NORTH PERIM SPC (G.N1) | PATIENT EL4 NORTH PERIM SPC (G.N1) | Yes | Health_patient | Alternative | Health | 22.24% | 13348.11 | 120193.7 | 1 | 5
PATIENTROOM EL4 SOUTH PERIM SPC (G.S2) | PATIENTROOM EL4 SOUTH PERIM SPC (G.S2) | Yes | Health_patient | Alternative | Health | 22.21% | 13324.59 | 119927.36 | 1 | 5
Total (20 Space) | Total (20 Space) | Total (11 Conditioned zones, 9 Unconditioned Zones) |  |  |  |  | 60006.49

## Envelope
Envelope - Health/Medical - Nursing Home
Element | Prototype | Assembly Type | Construction | Unit | Vintage | Selected T24 | Note | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Health/Medical - Nursing Home | - | Stucco+Wall Continuous Insulation+Gypsum 5/8in | U-value IP | Existing | Weighted average |  | 0.118 | 0.109 | 0.119 | 0.107 | 0.116 | 0.118 | 0.112 | 0.117 | 0.11 | 0.091 | 0.103 | 0.103 | 0.102 | 0.097 | 0.086 | 0.098
External Wall | Health/Medical - Nursing Home | - | Stucco+Wall Continuous Insulation+Gypsum 5/8in | U-value IP | New Construction | 2025 |  | 0.084 | 0.055 | 0.112 | 0.055 | 0.103 | 0.112 | 0.112 | 0.103 | 0.055 | 0.055 | 0.044 | 0.055 | 0.055 | 0.055 | 0.039 | 0.055
Roof | Health/Medical - Nursing Home | - | Roof Membrane+Roof Continuous Insulation+Metal Decking | U-value IP | Existing | Weighted average |  | 0.067 | 0.066 | 0.067 | 0.065 | 0.067 | 0.074 | 0.073 | 0.073 | 0.07 | 0.061 | 0.063 | 0.063 | 0.063 | 0.061 | 0.059 | 0.061
Roof | Health/Medical - Nursing Home | - | Roof Membrane+Roof Continuous Insulation+Metal Decking | U-value IP | New Construction | 2025 |  | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.048 | 0.048 | 0.048 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | Health/Medical - Nursing Home | - | Theoretical Glazing | U-value IP | Existing | Weighted average |  | 1.024 | 1.078 | 1.131 | 1.108 | 1.109 | 1.115 | 1.075 | 1.114 | 1.112 | 0.875 | 0.942 | 0.94 | 0.929 | 0.886 | 0.831 | 0.885
Windows | Health/Medical - Nursing Home | - | Theoretical Glazing | U-value IP | New Construction | 2025 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
Windows | Health/Medical - Nursing Home | - | Theoretical Glazing | SHGC | Existing | Weighted average |  | 0.70708 | 0.70715 | 0.73753 | 0.71836 | 0.75308 | 0.7254 | 0.72673 | 0.7241 | 0.72365 | 0.5734 | 0.64366 | 0.64394 | 0.6358 | 0.60724 | 0.57129 | 0.62767
Windows | Health/Medical - Nursing Home | - | Theoretical Glazing | SHGC | New Construction | 2025 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Windows | Health/Medical - Nursing Home | - | Theoretical Glazing | Visible Transmittance | Existing | Weighted average |  | 0.26089 | 0.26141 | 0.26004 | 0.26231 | 0.26223 | 0.26197 | 0.26576 | 0.26213 | 0.26228 | 0.27816 | 0.26665 | 0.26607 | 0.26793 | 0.27125 | 0.27583 | 0.27139
Windows | Health/Medical - Nursing Home | - | Theoretical Glazing | Visible Transmittance | New Construction | 2025 |  | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
Infiltration - Health/Medical - Nursing Home
|  |  |  | Element | Unit | Vintage | Note | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
|  |  |  | Infiltration Rate | CFM/ft2 | Existing | Infiltration rate is flow rate per exterior surface area at 10 mph wind speed, modeled proportionally to wind speed. | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801
[6 empty] | New Construction |  | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801

## Raw_envelope (hidden)
Climate Zone | Vintage | Exterior Roof Layers | Roof U-Value [Btu/h-ft2-F] | Exterior Wall Layers | Wall U-Value [Btu/h-ft2-F] | Exterior Window Layers | Window U-Value [Btu/h-ft2-F] | Window SHGC | Window VT
CZ01 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.067 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.118 | Theoretical Glazing | 1.024 | 0.70708 | 0.26089
CZ02 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.066 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.109 | Theoretical Glazing | 1.078 | 0.70715 | 0.26141
CZ03 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.067 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.119 | Theoretical Glazing | 1.131 | 0.73753 | 0.26004
CZ04 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.107 | Theoretical Glazing | 1.108 | 0.71836 | 0.26231
CZ05 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.067 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.116 | Theoretical Glazing | 1.109 | 0.75308 | 0.26223
CZ06 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.074 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.118 | Theoretical Glazing | 1.115 | 0.7254 | 0.26197
CZ07 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.073 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.112 | Theoretical Glazing | 1.075 | 0.72673 | 0.26576
CZ08 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.073 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.117 | Theoretical Glazing | 1.114 | 0.7241 | 0.26213
CZ09 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.07 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.11 | Theoretical Glazing | 1.112 | 0.72365 | 0.26228
CZ10 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.091 | Theoretical Glazing | 0.875 | 0.5734 | 0.27816
CZ11 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.063 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.103 | Theoretical Glazing | 0.942 | 0.64366 | 0.26665
CZ12 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.063 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.103 | Theoretical Glazing | 0.94 | 0.64394 | 0.26607
CZ13 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.063 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.102 | Theoretical Glazing | 0.929 | 0.6358 | 0.26793
CZ14 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.097 | Theoretical Glazing | 0.886 | 0.60724 | 0.27125
CZ15 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.059 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.086 | Theoretical Glazing | 0.831 | 0.57129 | 0.27583
CZ16 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.098 | Theoretical Glazing | 0.885 | 0.62767 | 0.27139
CZ01 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.084 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ02 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ03 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.112 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ04 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ05 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.103 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ06 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.048 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.112 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ07 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.048 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.112 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ08 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.048 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.103 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ09 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ10 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ11 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.044 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ12 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ13 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ14 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ15 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.039 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ16 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.055 | Theoretical Glazing | 0.36 | 0.25 | 0.42

## Raw_infiltrationcfmft (hidden)
Vintage | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Existing | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801
New Construction | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801

## Thermostat
Thermostat Setpoints - Health/Medical - Nursing Home | [18 empty] | Zone Type
Schedule Identifier | Setpoint | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Notes | Health
Health | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Kitchen
Health | Heating Setback (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Office
Health | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Health | Cooling Setback (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Kitchen | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Office | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Office | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Office | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Office | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Raw_thermostatsetpoints (hidden)
Climate Zone | Schedule Identifier | Heating Setpoint (F) | Heating Setback (F) | Cooling Setpoint (F) | Cooling Setback (F)
CZ01 | Health | 70 | 70 | 75 | 75
CZ01 | Kitchen | 70 | 60 | 75 | 85
CZ01 | Office | 70 | 60 | 75 | 85
CZ02 | Health | 70 | 70 | 75 | 75
CZ02 | Kitchen | 70 | 60 | 75 | 85
CZ02 | Office | 70 | 60 | 75 | 85
CZ03 | Health | 70 | 70 | 75 | 75
CZ03 | Kitchen | 70 | 60 | 75 | 85
CZ03 | Office | 70 | 60 | 75 | 85
CZ04 | Health | 70 | 70 | 75 | 75
CZ04 | Kitchen | 70 | 60 | 75 | 85
CZ04 | Office | 70 | 60 | 75 | 85
CZ05 | Health | 70 | 70 | 75 | 75
CZ05 | Kitchen | 70 | 60 | 75 | 85
CZ05 | Office | 70 | 60 | 75 | 85
CZ06 | Health | 70 | 70 | 75 | 75
CZ06 | Kitchen | 70 | 60 | 75 | 85
CZ06 | Office | 70 | 60 | 75 | 85
CZ07 | Health | 70 | 70 | 75 | 75
CZ07 | Kitchen | 70 | 60 | 75 | 85
CZ07 | Office | 70 | 60 | 75 | 85
CZ08 | Health | 70 | 70 | 75 | 75
CZ08 | Kitchen | 70 | 60 | 75 | 85
CZ08 | Office | 70 | 60 | 75 | 85
CZ09 | Health | 70 | 70 | 75 | 75
CZ09 | Kitchen | 70 | 60 | 75 | 85
CZ09 | Office | 70 | 60 | 75 | 85
CZ10 | Health | 70 | 70 | 75 | 75
CZ10 | Kitchen | 70 | 60 | 75 | 85
CZ10 | Office | 70 | 60 | 75 | 85
CZ11 | Health | 70 | 70 | 75 | 75
CZ11 | Kitchen | 70 | 60 | 75 | 85
CZ11 | Office | 70 | 60 | 75 | 85
CZ12 | Health | 70 | 70 | 75 | 75
CZ12 | Kitchen | 70 | 60 | 75 | 85
CZ12 | Office | 70 | 60 | 75 | 85
CZ13 | Health | 70 | 70 | 75 | 75
CZ13 | Kitchen | 70 | 60 | 75 | 85
CZ13 | Office | 70 | 60 | 75 | 85
CZ14 | Health | 70 | 70 | 75 | 75
CZ14 | Kitchen | 70 | 60 | 75 | 85
CZ14 | Office | 70 | 60 | 75 | 85
CZ15 | Health | 70 | 70 | 75 | 75
CZ15 | Kitchen | 70 | 60 | 75 | 85
CZ15 | Office | 70 | 60 | 75 | 85
CZ16 | Health | 70 | 70 | 75 | 75
CZ16 | Kitchen | 70 | 60 | 75 | 85
CZ16 | Office | 70 | 60 | 75 | 85

## HVAC System
HVAC system - Health/Medical - Nursing Home
Vintage | System Name | Category | Heating Type* | Cooling Type* | Air Distribution | Heating Efficiency | Cooling Efficiency | Note
Existing | cDXGF | Main | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.65
Existing | cDXGF | Alternative | Boiler (gas) | DX-AIR | MZ-VAV | 0.8 | 3.85
Existing | cDXGF | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
New Construction | cDXGF | Main | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.65
New Construction | cDXGF | Alternative | Boiler (gas) | DX-AIR | MZ-VAV | 0.8 | 3.85
New Construction | cDXGF | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
Existing | cDXHP | Main | DX-AIR | DX-AIR | SZ-CAV | 3.738 | 3.65
Existing | cDXHP | Alternative | Boiler (gas) | DX-AIR | MZ-VAV | 0.8 | 3.85
Existing | cDXHP | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
New Construction | cDXHP | Main | DX-AIR | DX-AIR | SZ-CAV | 3.738 | 3.65
New Construction | cDXHP | Alternative | Boiler (gas) | DX-AIR | MZ-VAV | 0.8 | 3.85
New Construction | cDXHP | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
Existing | cAVVG | Main | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Alternative | Boiler (gas) | DX-AIR | MZ-VAV | 0.805 | 3.85
Existing | cAVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
New Construction | cAVVG | Main | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Alternative | Boiler (gas) | DX-AIR | MZ-VAV | 0.805 | 3.85
New Construction | cAVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
Existing | cDXOH | Main | None | DX-AIR | SZ-CAV | - | 3.65
Existing | cDXOH | Alternative | Boiler (gas) | DX-AIR | MZ-VAV | 0.8 | 3.85
Existing | cDXOH | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
New Construction | cDXOH | Main | None | DX-AIR | SZ-CAV | - | 3.65
New Construction | cDXOH | Alternative | Boiler (gas) | DX-AIR | MZ-VAV | 0.8 | 3.85
New Construction | cDXOH | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
Existing | cPVVG | Main | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.65
Existing | cPVVG | Alternative | Boiler (gas) | DX-AIR | MZ-VAV | 0.8 | 3.85
Existing | cPVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
New Construction | cPVVG | Main | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.65
New Construction | cPVVG | Alternative | Boiler (gas) | DX-AIR | MZ-VAV | 0.8 | 3.85
New Construction | cPVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
*DX Heating and cooling COPs are calculated based on coil-only input power and exclude fan power
Fan Power - Health/Medical - Nursing Home
Vintage | System Name | HVAC System Identifier | Fan System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm | Note
Existing | cAVVG | Main | MZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cAVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cAVVG | Main | MZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cAVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXGF | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXGF | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXGF | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXGF | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXGF | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXGF | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXHP | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXHP | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXHP | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXHP | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXHP | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXHP | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXOH | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXOH | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXOH | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXOH | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXOH | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXOH | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cPVVG | Main | SZ-VAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cPVVG | Main | SZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cPVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cPVVG | Main | SZ-VAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cPVVG | Main | SZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cPVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7

## Raw_fanoverview (hidden)
Vintage | HVAC name | System type | HVAC System Identifier | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm
Existing | cAVVG | MZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cAVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cAVVG | MZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cAVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXGF | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXGF | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXGF | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXGF | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXGF | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXGF | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXHP | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXHP | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXHP | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXHP | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXHP | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXHP | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXOH | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXOH | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXOH | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXOH | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXOH | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXOH | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cPVVG | SZ-VAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cPVVG | SZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cPVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cPVVG | SZ-VAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cPVVG | SZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cPVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7

## Raw_hvac (hidden)
Vintage | System Name | HVAC System Identifier | Air Distribution | Heating Efficiency | Cooling Efficiency | Cooling Coil Type | Heating Coil Type
Existing | cAVVG | Main | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Alternative | MZ-VAV | 0.805 | 3.85 | DX-AIR | WATER
Existing | cAVVG | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cAVVG | Main | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Alternative | MZ-VAV | 0.805 | 3.85 | DX-AIR | WATER
New Construction | cAVVG | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cDXGF | Main | SZ-CAV | 0.8 | 3.65
Existing | cDXGF | Alternative | MZ-VAV | 0.8 | 3.85 | DX-AIR | WATER
Existing | cDXGF | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cDXGF | Main | SZ-CAV | 0.8 | 3.65
New Construction | cDXGF | Alternative | MZ-VAV | 0.8 | 3.85 | DX-AIR | WATER
New Construction | cDXGF | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cDXHP | Main | SZ-CAV | 3.738 | 3.65
Existing | cDXHP | Alternative | MZ-VAV | 0.8 | 3.85 | DX-AIR | WATER
Existing | cDXHP | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cDXHP | Main | SZ-CAV | 3.738 | 3.65
New Construction | cDXHP | Alternative | MZ-VAV | 0.8 | 3.85 | DX-AIR | WATER
New Construction | cDXHP | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cDXOH | Main | SZ-CAV | - | 3.65
Existing | cDXOH | Alternative | MZ-VAV | 0.8 | 3.85 | DX-AIR | WATER
Existing | cDXOH | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cDXOH | Main | SZ-CAV | - | 3.65
New Construction | cDXOH | Alternative | MZ-VAV | 0.8 | 3.85 | DX-AIR | WATER
New Construction | cDXOH | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cPVVG | Main | SZ-VAV | 0.8 | 3.65
Existing | cPVVG | Alternative | MZ-VAV | 0.8 | 3.85 | DX-AIR | WATER
Existing | cPVVG | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cPVVG | Main | SZ-VAV | 0.8 | 3.65
New Construction | cPVVG | Alternative | MZ-VAV | 0.8 | 3.85 | DX-AIR | WATER
New Construction | cPVVG | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION

## Ventilation
Outdoor Airflow Rate - Health/Medical - Nursing Home | [19 empty] | Zone Type
Zone Type | Floor area (ft²) | cfm/person | cfm/ft² | cfm | Notes | [14 empty] | Corridor
Corridor | 3328.42 | 0 | 0.15 | 499.263 | [15 empty] | Dining_fast
Dining_fast | 6303.51 | 0 | 0.5 | 3151.755 | [15 empty] | Health_patient
Health_patient | 26672.7 | 0 | 0.15 | 4000.905 | [15 empty] | Kitchen
Kitchen | 2701.87 | 0 | 0.15 | 405.2805 | [15 empty] | Office
Office | 20999.99 | 0 | 0.15 | 3149.9985
OA Controller - Health/Medical - Nursing Home
Element | Vintage | Unit | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Notes
Economizer Maximum Limit Dry-Bulb Temperature | Existing | °F | 75 | 73 | 75 | 73 | 75 | 71 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 75 | 75 | 75
| New Construction | °F | 75 | 73 | 75 | 73 | 75 | 71 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 75 | 75 | 75
Exhaust hood - Health/Medical - Nursing Home
Type of Hood | Max Exhaust Flow Rate (cfm/ft) | Hood Length (ft) | Hood Exhaust Rate (cfm) | Note
- | - | - | -

## Raw_outdoorairflowrate (hidden)
Zone Type | Floor Area (ft2) | cfm/person | cfm/ft2
Corridor | 3328.42 | 0 | 0.15
Dining_fast | 6303.51 | 0 | 0.5
Health_patient | 26672.7 | 0 | 0.15
Kitchen | 2701.87 | 0 | 0.15
Office | 20999.99 | 0 | 0.15

## Raw_oacontroller (hidden)
Climate Zone | Vintage | Economizer Maximum Limit Dry-Bulb Temperature (F)
CZ01 | Existing | 75
CZ02 | Existing | 73
CZ03 | Existing | 75
CZ04 | Existing | 73
CZ05 | Existing | 75
CZ06 | Existing | 71
CZ07 | Existing | 69
CZ08 | Existing | 71
CZ09 | Existing | 71
CZ10 | Existing | 73
CZ11 | Existing | 75
CZ12 | Existing | 75
CZ13 | Existing | 75
CZ14 | Existing | 75
CZ15 | Existing | 75
CZ16 | Existing | 75
CZ01 | New Construction | 75
CZ02 | New Construction | 73
CZ03 | New Construction | 75
CZ04 | New Construction | 73
CZ05 | New Construction | 75
CZ06 | New Construction | 71
CZ07 | New Construction | 69
CZ08 | New Construction | 71
CZ09 | New Construction | 71
CZ10 | New Construction | 73
CZ11 | New Construction | 75
CZ12 | New Construction | 75
CZ13 | New Construction | 75
CZ14 | New Construction | 75
CZ15 | New Construction | 75
CZ16 | New Construction | 75

## Water Heater
Water Heater - Health/Medical - Nursing Home
Vintage | Fuel type | Burner Efficiency | Maximum Heater Capacity (Btu/hr) | Tank Volume (gallon) | Tank Loss |  | Notes
[5 empty] | Off Cycle (W/K) | On Cycle (W/K)
Existing | Gas | 0.8 | 449473.47 | 94.26 | 1.6282 | 1.6282
New Construction | Gas | 0.8 | 449473.47 | 94.26 | 1.6282 | 1.6282
Peak Hot Water Consumption - Health/Medical - Nursing Home
Space | Floor Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Notes
CORRIDOR EL4 CORE SPC (G.C3) | 3328.42 | 5 | 0 | 0 | 0
DINING EL1 WEST PERIM SPC (G.W1) | 6303.51 | 33.33 | 7.2876 | 242.8953 | 4.0483
EL2 CORE PLNM (G.4) | 0 | 0 | 0 | 0 | 0
EL2 NORTH PLNM (G.4) | 0 | 0 | 0 | 0 | 0
EL2 SOUTH PLNM (G.4) | 0 | 0 | 0 | 0 | 0
EL3 NORTH PLNM (G.4) | 0 | 0 | 0 | 0 | 0
EL3 SOUTH PLNM (G.4) | 0 | 0 | 0 | 0 | 0
EL3 WEST PLNM (G.4) | 0 | 0 | 0 | 0 | 0
EL4 CORE PLNM (G.4) | 0 | 0 | 0 | 0 | 0
EL4 NORTH PLNM (G.4) | 0 | 0 | 0 | 0 | 0
EL4 SOUTH PLNM (G.4) | 0 | 0 | 0 | 0 | 0
KITCHEN EL1 EAST PERIM SPC (G.E2) | 2701.87 | 2.5 | 3.1234 | 7.8084 | 0.13014
OFFICE EL2 CORE SPC (G.C1) | 3895.75 | 5 | 1.4025 | 7.0123 | 0.11687
OFFICE EL2 NORTH PERIM SPC (G.N3) | 5549.46 | 5 | 1.9978 | 9.989 | 0.16648
OFFICE EL2 SOUTH PERIM SPC (G.S2) | 5549.38 | 5 | 1.9978 | 9.9889 | 0.16648
OFFICE EL3 NORTH PERIM SPC (G.N3) | 2222.58 | 5 | 0 | 0 | 0
OFFICE EL3 SOUTH PERIM SPC (G.S2) | 2222.55 | 5 | 0 | 0 | 0
OFFICE EL3 WEST PERIM SPC (G.W1) | 1560.27 | 5 | 0 | 0 | 0
PATIENT EL4 NORTH PERIM SPC (G.N1) | 13348.11 | 5 | 6.4071 | 32.0355 | 0.53392
PATIENTROOM EL4 SOUTH PERIM SPC (G.S2) | 13324.59 | 5 | 0 | 0 | 0
Total (20 Space)

## Raw_waterheater (hidden)
Vintage | Burner Efficiency | Maximum Heater Capacity (Btu/h) | Tank Volume (ft3) | Tank Loss_Off Cycle (W/K) | Tank Loss_On Cycle (W/K)
Existing | 0.8 | 449473.47 | 94.26 | 1.6282 | 1.6282
New Construction | 0.8 | 449473.47 | 94.26 | 1.6282 | 1.6282

## Raw_dhwpeakflowbyzone (hidden)
Space | Peak hot water usage (gal/hr) | Zone Name
Dining EL1 West Perim Spc (G.W1) | 242.8953 | DINING EL1 WEST PERIM SPC (G.W1)
Kitchen EL1 East Perim Spc (G.E2) | 7.8084 | KITCHEN EL1 EAST PERIM SPC (G.E2)
Office EL2 Core Spc (G.C1) | 7.0123 | OFFICE EL2 CORE SPC (G.C1)
Office EL2 North Perim Spc (G.N3) | 9.989 | OFFICE EL2 NORTH PERIM SPC (G.N3)
Office EL2 South Perim Spc (G.S2) | 9.9889 | OFFICE EL2 SOUTH PERIM SPC (G.S2)
Office EL3 North Perim Spc (G.N3) | 4.0006 | OFFICE EL2 NORTH PERIM SPC (G.N3)
Office EL3 South Perim Spc (G.S2) | 4.0006 | OFFICE EL2 SOUTH PERIM SPC (G.S2)
Office EL3 West Perim Spc (G.W1) | 2.8085 | DINING EL1 WEST PERIM SPC (G.W1)
Patient EL4 North Perim Spc (G.N1) | 32.0355 | PATIENT EL4 NORTH PERIM SPC (G.N1)
PatientRoom EL4 South Perim Spc (G.S2) | 31.979 | OFFICE EL2 SOUTH PERIM SPC (G.S2)

## Interior Lights
Interior Lighting - Health/Medical - Nursing Home
Vintage | Method | Zone type | Floor area (ft²) | Lighting Power Density (Watts/ft²) | Additional Lighting Power for Portable Lighting (Watts/ft²) | Technology | Notes
Existing | Space by space | Corridor | 3328.42 | 0.62242 | NA | NA
Existing | Space by space | Dining_fast | 6303.51 | 1.2136 | NA | NA
Existing | Space by space | Health_patient | 26672.7 | 1.302 | NA | NA
Existing | Space by space | Kitchen | 2701.87 | 1.6492 | NA | NA
Existing | Space by space | Office | 20999.99 | 1.2504 | NA | NA
New Construction | Space by space | Corridor | 3328.42 | 0.39995 | NA | NA
New Construction | Space by space | Dining_fast | 6303.51 | 0.44995 | NA | NA
New Construction | Space by space | Health_patient | 26672.7 | 0.69991 | NA | NA
New Construction | Space by space | Kitchen | 2701.87 | 0.94987 | NA | NA
New Construction | Space by space | Office | 20999.99 | 0.59992 | NA | NA

## Ext Lighting
Exterior Lighting - Health/Medical - Nursing Home
Vintage | Non-Motion Controlled Luminaires (W) | Motion-Controlled Luminaires (W) | Total (W) | Notes
Existing | NA | NA | NA
New Consturction | NA | NA | NA

## Raw_interiorlights (hidden)
Vintage | Zone Type | Floor Area (ft2) | Lighting Power Density(W/ft2)
Existing | Corridor | 3328.42 | 0.62242
Existing | Dining_fast | 6303.51 | 1.2136
Existing | Health_patient | 26672.7 | 1.302
Existing | Kitchen | 2701.87 | 1.6492
Existing | Office | 20999.99 | 1.2504
New Construction | Corridor | 3328.42 | 0.39995
New Construction | Dining_fast | 6303.51 | 0.44995
New Construction | Health_patient | 26672.7 | 0.69991
New Construction | Kitchen | 2701.87 | 0.94987
New Construction | Office | 20999.99 | 0.59992

## Equipment
Equipment - Health/Medical - Nursing Home
Zone Type | Floor Area (ft²) | Plug Load Intensity (W/ft²) | Gas Power Density (Btu/hr-ft²)
Corridor | 3328.42 | 0 | 0
Dining_fast | 6303.51 | 0.74991 | 0
Health_patient | 26672.7 | 1.4998 | 0
Kitchen | 2701.87 | 7.7581 | 17.5354
Office | 20999.99 | 1.4998 | 0
Refrigeration - Health/Medical - Nursing Home
Refrigeration System Name | Condenser Fan Power | Refrigeration System Working Fluid | Condenser Type
Elevator - Health/Medical - Nursing Home
Vintage | No. of Elevators | Cab Lighting Power Limit | Lighting Shutoff | Cab Fan Control | Fan Power Limit | Regenerative Drive Threshold | Design load (W) | Note
Existing | - | - | - | - | - | - | -
New Construction | - | - | - | - | - | - | -

## Raw_equipment (hidden)
Vintage | Zone Type | Floor Area (ft2) | Plug Load Intensity (W/ft2)
Existing | Corridor | 3328.42 | 0
Existing | Dining_fast | 6303.51 | 0.74991
Existing | Health_patient | 26672.7 | 1.4998
Existing | Kitchen | 2701.87 | 7.7581
Existing | Office | 20999.99 | 1.4998
New Construction | Corridor | 3328.42 | 0
New Construction | Dining_fast | 6303.51 | 0.74991
New Construction | Health_patient | 26672.7 | 1.4998
New Construction | Kitchen | 2701.87 | 7.7581
New Construction | Office | 20999.99 | 1.4998

## Raw_gasequipment (hidden)
Vintage | Zone Name | Gas Loads (Btu/h-ft2) | Zone Type
Existing | Kitchen EL1 East Perim Spc (G.E2) | 17.5354 | Kitchen
New Construction | Kitchen EL1 East Perim Spc (G.E2) | 17.5354 | Kitchen

## Raw_refrigerationsystem (hidden)
Vintage | Refrigeration System Name | Condenser Fan Power | Working fluid | Condenser Type
No refrigeration system was found

## Schedules
Schedule by Hour - Health/Medical - Nursing Home
Schedule Identifier | Space type | Type | Notes | Hour
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Cooling Setpoint Schedule | Health | AllDays | Cooling/Heating setpoints are in °F; others are intensity (0–100%) | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | Health | AllOtherDays |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
DHW Sch | Health | Saturdays |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
DHW Sch | Health | Weekdays |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.01 | 0.01 | 0.01
Elec Equip Sch | Health | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | Health | Saturdays |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Elec Equip Sch | Health | Weekdays |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Heating Setpoint Schedule | Health | AllDays |  | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | Health | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Health | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Health | Saturdays |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Lighting Schedule | Health | Weekdays |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.45 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
OA Schedule | Health | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | Health | Saturdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OA Schedule | Health | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Occupant Sch | Health | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Health | Saturdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Health | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
Cooling Setpoint Schedule | Kitchen | AllOtherDays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Cooling Setpoint Schedule | Kitchen | Saturdays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Cooling Setpoint Schedule | Kitchen | Weekdays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | Kitchen | AllOtherDays |  | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
DHW Sch | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
DHW Sch | Kitchen | Weekdays |  | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
Elec Equip Sch | Kitchen | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | Kitchen | AllOtherDays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Elec Equip Sch | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Elec Equip Sch | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Heating Setpoint Schedule | Kitchen | AllOtherDays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Heating Setpoint Schedule | Kitchen | Saturdays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Heating Setpoint Schedule | Kitchen | Weekdays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | Kitchen | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Kitchen | AllOtherDays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
Lighting Schedule | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Lighting Schedule | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
OA Schedule | Kitchen | AllOtherDays |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OA Schedule | Kitchen | Saturdays |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OA Schedule | Kitchen | Weekdays |  | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Occupant Sch | Kitchen | AllOtherDays |  | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Occupant Sch | Kitchen | Saturdays |  | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
Occupant Sch | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Cooling Setpoint Schedule | Office | AllOtherDays |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | Office | Saturday |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | Office | Weekdays |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | Office | AllOtherDays |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
DHW Sch | Office | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
DHW Sch | Office | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
Elec Equip Sch | Office | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | Office | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | Office | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | Office | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Heating Setpoint Schedule | Office | AllOtherDays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | Office | Saturday |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | Office | Weekdays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | Office | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Office | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Office | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Office | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OA Schedule | Office | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | Office | Saturday |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OA Schedule | Office | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Occupant Sch | Office | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Office | Saturday |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Office | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
Infiltration Schedule | Plenum | AllDays | bar: Hour 1 to Hour 24

## Schedule_Figures
Schedule Figures (linked to Schedules tab)

## Raw_schedule (hidden)
Schedule Identifier | Schedule Name | Type | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Health | Cooling Setpoint Schedule | AllDays | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Health | DHW Sch | AllOtherDays | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Health | DHW Sch | Saturdays | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Health | DHW Sch | Weekdays | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.01 | 0.01 | 0.01
Health | Elec Equip Sch | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Health | Elec Equip Sch | Saturdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Health | Elec Equip Sch | Weekdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Health | Heating Setpoint Schedule | AllDays | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Health | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Health | Lighting Schedule | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Health | Lighting Schedule | Saturdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Health | Lighting Schedule | Weekdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.45 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Health | OA Schedule | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health | OA Schedule | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Health | OA Schedule | Weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Health | Occupant Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health | Occupant Sch | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Health | Occupant Sch | Weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
Kitchen | Cooling Setpoint Schedule | AllOtherDays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | Cooling Setpoint Schedule | Saturdays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | Cooling Setpoint Schedule | Weekdays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | DHW Sch | AllOtherDays | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Kitchen | DHW Sch | Saturdays | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
Kitchen | DHW Sch | Weekdays | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
Kitchen | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Elec Equip Sch | AllOtherDays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Kitchen | Elec Equip Sch | Saturdays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Kitchen | Elec Equip Sch | Weekdays | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Kitchen | Heating Setpoint Schedule | AllOtherDays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Heating Setpoint Schedule | Saturdays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Heating Setpoint Schedule | Weekdays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Lighting Schedule | AllOtherDays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
Kitchen | Lighting Schedule | Saturdays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Kitchen | Lighting Schedule | Weekdays | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Kitchen | OA Schedule | AllOtherDays | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | OA Schedule | Saturdays | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | OA Schedule | Weekdays | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Occupant Sch | AllOtherDays | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Kitchen | Occupant Sch | Saturdays | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
Kitchen | Occupant Sch | Weekdays | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Office | Cooling Setpoint Schedule | AllOtherDays | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Office | Cooling Setpoint Schedule | Saturday | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Office | Cooling Setpoint Schedule | Weekdays | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Office | DHW Sch | AllOtherDays | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Office | DHW Sch | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
Office | DHW Sch | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
Office | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Elec Equip Sch | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Elec Equip Sch | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Elec Equip Sch | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Office | Heating Setpoint Schedule | AllOtherDays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Office | Heating Setpoint Schedule | Saturday | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Office | Heating Setpoint Schedule | Weekdays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Office | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Lighting Schedule | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Lighting Schedule | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Lighting Schedule | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Office | OA Schedule | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office | OA Schedule | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Office | OA Schedule | Weekdays | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Occupant Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Office | Occupant Sch | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
Office | Occupant Sch | Weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
Plenum | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## Energy Usage
Energy Consumption - Health/Medical - Nursing Home
Climate Zone | HVAC Type | Vintage | Total Floorspace (Excluding Plenums and Crawl Space) (ft²) | Annual Electricity Intensity (kBtu/ft²) | Annual Gas Intensity (kBtu/ft²) | Notes
CZ01 | cAVVG | Existing | 60006.49 | 32.2961 | 20.1352
CZ01 | cAVVG | New Construction | 60006.49 | 25.7755 | 19.5872
CZ01 | cDXGF | Existing | 60006.49 | 35.6069 | 17.8326
CZ01 | cDXGF | New Construction | 60006.49 | 27.8698 | 16.658
CZ01 | cDXHP | Existing | 60006.49 | 36.1536 | 15.6238
CZ01 | cDXHP | New Construction | 60006.49 | 28.5684 | 13.7841
CZ01 | cDXOH | Existing | 60006.49 | 35.6024 | 16.0552
CZ01 | cDXOH | New Construction | 60006.49 | 27.8678 | 14.3853
CZ01 | cPVVG | Existing | 60006.49 | 32.4769 | 19.0552
CZ01 | cPVVG | New Construction | 60006.49 | 25.7935 | 17.6918
CZ02 | cAVVG | Existing | 60006.49 | 36.9633 | 16.6902
CZ02 | cAVVG | New Construction | 60006.49 | 28.5598 | 15.7475
CZ02 | cDXGF | Existing | 60006.49 | 40.2611 | 15.152
CZ02 | cDXGF | New Construction | 60006.49 | 30.7715 | 13.9263
CZ02 | cDXHP | Existing | 60006.49 | 40.6417 | 13.7971
CZ02 | cDXHP | New Construction | 60006.49 | 31.2225 | 12.2557
CZ02 | cDXOH | Existing | 60006.49 | 40.2531 | 14.0598
CZ02 | cDXOH | New Construction | 60006.49 | 30.749 | 12.5839
CZ02 | cPVVG | Existing | 60006.49 | 36.8972 | 15.9542
CZ02 | cPVVG | New Construction | 60006.49 | 28.47 | 14.5959
CZ03 | cAVVG | Existing | 60006.49 | 35.5368 | 14.2106
CZ03 | cAVVG | New Construction | 60006.49 | 27.397 | 14.1978
CZ03 | cDXGF | Existing | 60006.49 | 38.8962 | 13.2415
CZ03 | cDXGF | New Construction | 60006.49 | 29.6002 | 12.9777
CZ03 | cDXHP | Existing | 60006.49 | 39.0743 | 12.4842
CZ03 | cDXHP | New Construction | 60006.49 | 29.8744 | 11.8332
CZ03 | cDXOH | Existing | 60006.49 | 38.8895 | 12.6346
CZ03 | cDXOH | New Construction | 60006.49 | 29.5901 | 12.0506
CZ03 | cPVVG | Existing | 60006.49 | 35.6668 | 13.7963
CZ03 | cPVVG | New Construction | 60006.49 | 27.3131 | 13.5258
CZ04 | cAVVG | Existing | 60006.49 | 38.1977 | 13.4526
CZ04 | cAVVG | New Construction | 60006.49 | 29.263 | 13.3338
CZ04 | cDXGF | Existing | 60006.49 | 41.3181 | 12.5555
CZ04 | cDXGF | New Construction | 60006.49 | 31.4751 | 12.1141
CZ04 | cDXHP | Existing | 60006.49 | 41.4849 | 11.9025
CZ04 | cDXHP | New Construction | 60006.49 | 31.6916 | 11.2427
CZ04 | cDXOH | Existing | 60006.49 | 41.3101 | 12.0128
CZ04 | cDXOH | New Construction | 60006.49 | 31.448 | 11.3097
CZ04 | cPVVG | Existing | 60006.49 | 37.9984 | 13.0598
CZ04 | cPVVG | New Construction | 60006.49 | 29.1743 | 12.532
CZ05 | cAVVG | Existing | 60006.49 | 36.6167 | 13.9887
CZ05 | cAVVG | New Construction | 60006.49 | 28.0117 | 14.2751
CZ05 | cDXGF | Existing | 60006.49 | 39.8931 | 13.0732
CZ05 | cDXGF | New Construction | 60006.49 | 30.2106 | 13.02
CZ05 | cDXHP | Existing | 60006.49 | 40.0788 | 12.3296
CZ05 | cDXHP | New Construction | 60006.49 | 30.5081 | 11.8376
CZ05 | cDXOH | Existing | 60006.49 | 39.8763 | 12.4185
CZ05 | cDXOH | New Construction | 60006.49 | 30.1721 | 11.9633
CZ05 | cPVVG | Existing | 60006.49 | 36.7816 | 13.5645
CZ05 | cPVVG | New Construction | 60006.49 | 27.9769 | 13.5024
CZ06 | cAVVG | Existing | 60006.49 | 40.6072 | 11.3861
CZ06 | cAVVG | New Construction | 60006.49 | 30.5467 | 11.2618
CZ06 | cDXGF | Existing | 60006.49 | 42.9324 | 11.1149
CZ06 | cDXGF | New Construction | 60006.49 | 32.1897 | 10.883
CZ06 | cDXHP | Existing | 60006.49 | 42.9002 | 11.0097
CZ06 | cDXHP | New Construction | 60006.49 | 32.1944 | 10.6548
CZ06 | cDXOH | Existing | 60006.49 | 42.9324 | 11.0163
CZ06 | cDXOH | New Construction | 60006.49 | 32.1831 | 10.6674
CZ06 | cPVVG | Existing | 60006.49 | 40.025 | 11.2612
CZ06 | cPVVG | New Construction | 60006.49 | 30.021 | 11.0357
CZ07 | cAVVG | Existing | 60006.49 | 40.6568 | 10.9926
CZ07 | cAVVG | New Construction | 60006.49 | 30.4991 | 11.3245
CZ07 | cDXGF | Existing | 60006.49 | 42.7496 | 10.7225
CZ07 | cDXGF | New Construction | 60006.49 | 32.3408 | 10.727
CZ07 | cDXHP | Existing | 60006.49 | 42.7413 | 10.6324
CZ07 | cDXHP | New Construction | 60006.49 | 32.3542 | 10.5189
CZ07 | cDXOH | Existing | 60006.49 | 42.7423 | 10.634
CZ07 | cDXOH | New Construction | 60006.49 | 32.3423 | 10.538
CZ07 | cPVVG | Existing | 60006.49 | 39.8436 | 10.8245
CZ07 | cPVVG | New Construction | 60006.49 | 30.1842 | 10.8671
CZ08 | cAVVG | Existing | 60006.49 | 41.0995 | 11.8151
CZ08 | cAVVG | New Construction | 60006.49 | 31.3489 | 11.9187
CZ08 | cDXGF | Existing | 60006.49 | 43.8782 | 11.1395
CZ08 | cDXGF | New Construction | 60006.49 | 33.3063 | 11.0698
CZ08 | cDXHP | Existing | 60006.49 | 43.9032 | 10.9476
CZ08 | cDXHP | New Construction | 60006.49 | 33.3741 | 10.723
CZ08 | cDXOH | Existing | 60006.49 | 43.8697 | 10.9619
CZ08 | cDXOH | New Construction | 60006.49 | 33.2967 | 10.7531
CZ08 | cPVVG | Existing | 60006.49 | 40.764 | 11.3188
CZ08 | cPVVG | New Construction | 60006.49 | 31.0252 | 11.2722
CZ09 | cAVVG | Existing | 60006.49 | 43.0501 | 11.387
CZ09 | cAVVG | New Construction | 60006.49 | 31.7726 | 11.4806
CZ09 | cDXGF | Existing | 60006.49 | 45.2996 | 11.0411
CZ09 | cDXGF | New Construction | 60006.49 | 33.6733 | 10.7727
CZ09 | cDXHP | Existing | 60006.49 | 45.312 | 10.9072
CZ09 | cDXHP | New Construction | 60006.49 | 33.7123 | 10.5371
CZ09 | cDXOH | Existing | 60006.49 | 45.2925 | 10.9114
CZ09 | cDXOH | New Construction | 60006.49 | 33.6596 | 10.5507
CZ09 | cPVVG | Existing | 60006.49 | 42.1186 | 11.1831
CZ09 | cPVVG | New Construction | 60006.49 | 31.4691 | 10.9267
CZ10 | cAVVG | Existing | 60006.49 | 43.6584 | 12.6051
CZ10 | cAVVG | New Construction | 60006.49 | 33.5071 | 12.4487
CZ10 | cDXGF | Existing | 60006.49 | 46.5088 | 11.4736
CZ10 | cDXGF | New Construction | 60006.49 | 35.5236 | 11.2919
CZ10 | cDXHP | Existing | 60006.49 | 46.6362 | 11.0248
CZ10 | cDXHP | New Construction | 60006.49 | 35.6909 | 10.669
CZ10 | cDXOH | Existing | 60006.49 | 46.5004 | 11.0797
CZ10 | cDXOH | New Construction | 60006.49 | 35.508 | 10.7404
CZ10 | cPVVG | Existing | 60006.49 | 43.2204 | 11.7999
CZ10 | cPVVG | New Construction | 60006.49 | 33.1432 | 11.6
CZ11 | cAVVG | Existing | 60006.49 | 44.321 | 17.1458
CZ11 | cAVVG | New Construction | 60006.49 | 33.6462 | 15.335
CZ11 | cDXGF | Existing | 60006.49 | 47.4069 | 15.1557
CZ11 | cDXGF | New Construction | 60006.49 | 35.5984 | 13.491
CZ11 | cDXHP | Existing | 60006.49 | 47.762 | 13.8779
CZ11 | cDXHP | New Construction | 60006.49 | 36.0003 | 11.9774
CZ11 | cDXOH | Existing | 60006.49 | 47.4017 | 14.1342
CZ11 | cDXOH | New Construction | 60006.49 | 35.59 | 12.3376
CZ11 | cPVVG | Existing | 60006.49 | 43.9606 | 16.0056
CZ11 | cPVVG | New Construction | 60006.49 | 33.2522 | 14.1919
CZ12 | cAVVG | Existing | 60006.49 | 41.9335 | 16.3358
CZ12 | cAVVG | New Construction | 60006.49 | 32.0763 | 15.2192
CZ12 | cDXGF | Existing | 60006.49 | 44.8842 | 14.5638
CZ12 | cDXGF | New Construction | 60006.49 | 34.0438 | 13.4813
CZ12 | cDXHP | Existing | 60006.49 | 45.24 | 13.3089
CZ12 | cDXHP | New Construction | 60006.49 | 34.4648 | 11.9389
CZ12 | cDXOH | Existing | 60006.49 | 44.8782 | 13.568
CZ12 | cDXOH | New Construction | 60006.49 | 34.041 | 12.301
CZ12 | cPVVG | Existing | 60006.49 | 41.6428 | 15.3166
CZ12 | cPVVG | New Construction | 60006.49 | 31.7537 | 14.0888
CZ13 | cAVVG | Existing | 60006.49 | 45.7532 | 15.0502
CZ13 | cAVVG | New Construction | 60006.49 | 34.6975 | 14.2798
CZ13 | cDXGF | Existing | 60006.49 | 48.4514 | 13.4357
CZ13 | cDXGF | New Construction | 60006.49 | 36.5102 | 12.6409
CZ13 | cDXHP | Existing | 60006.49 | 48.7177 | 12.4708
CZ13 | cDXHP | New Construction | 60006.49 | 36.8281 | 11.3841
CZ13 | cDXOH | Existing | 60006.49 | 48.4559 | 12.7163
CZ13 | cDXOH | New Construction | 60006.49 | 36.4986 | 11.6839
CZ13 | cPVVG | Existing | 60006.49 | 45.173 | 14.1095
CZ13 | cPVVG | New Construction | 60006.49 | 34.203 | 13.214
CZ14 | cAVVG | Existing | 60006.49 | 49.7271 | 13.068
CZ14 | cAVVG | New Construction | 60006.49 | 37.364 | 13.278
CZ14 | cDXGF | Existing | 60006.49 | 52.0395 | 12.1465
CZ14 | cDXGF | New Construction | 60006.49 | 39.2755 | 11.9967
CZ14 | cDXHP | Existing | 60006.49 | 52.2098 | 11.5515
CZ14 | cDXHP | New Construction | 60006.49 | 39.5043 | 11.1752
CZ14 | cDXOH | Existing | 60006.49 | 52.0279 | 11.6394
CZ14 | cDXOH | New Construction | 60006.49 | 39.2525 | 11.2907
CZ14 | cPVVG | Existing | 60006.49 | 48.5634 | 12.6029
CZ14 | cPVVG | New Construction | 60006.49 | 36.8716 | 12.425
CZ15 | cAVVG | Existing | 60006.49 | 55.8173 | 11.1698
CZ15 | cAVVG | New Construction | 60006.49 | 42.3134 | 11.3459
CZ15 | cDXGF | Existing | 60006.49 | 57.3168 | 10.3652
CZ15 | cDXGF | New Construction | 60006.49 | 43.0852 | 10.5608
CZ15 | cDXHP | Existing | 60006.49 | 57.3527 | 10.1611
CZ15 | cDXHP | New Construction | 60006.49 | 43.1563 | 10.2737
CZ15 | cDXOH | Existing | 60006.49 | 57.3011 | 10.1782
CZ15 | cDXOH | New Construction | 60006.49 | 43.0601 | 10.2762
CZ15 | cPVVG | Existing | 60006.49 | 54.257 | 10.4893
CZ15 | cPVVG | New Construction | 60006.49 | 41.0348 | 10.7044
CZ16 | cAVVG | Existing | 60006.49 | 43.6608 | 20.1154
CZ16 | cAVVG | New Construction | 60006.49 | 33.3549 | 18.7103
CZ16 | cDXGF | Existing | 60006.49 | 47.1086 | 18.0365
CZ16 | cDXGF | New Construction | 60006.49 | 35.8138 | 16.5624
CZ16 | cDXHP | Existing | 60006.49 | 47.8782 | 15.8883
CZ16 | cDXHP | New Construction | 60006.49 | 36.6782 | 13.9586
CZ16 | cDXOH | Existing | 60006.49 | 47.0992 | 16.2642
CZ16 | cDXOH | New Construction | 60006.49 | 35.7905 | 14.5072
CZ16 | cPVVG | Existing | 60006.49 | 43.4287 | 19.0836
CZ16 | cPVVG | New Construction | 60006.49 | 33.1673 | 17.5068

## Energy Usage_Figures
Energy Figures (from 'Energy Usage' Tab)
cAVVG ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cAVVG ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 32.2961 | 25.7755 | CZ01 | 20.1352 | 19.5872
CZ02 | 36.9633 | 28.5598 | CZ02 | 16.6902 | 15.7475
CZ03 | 35.5368 | 27.397 | CZ03 | 14.2106 | 14.1978
CZ04 | 38.1977 | 29.263 | CZ04 | 13.4526 | 13.3338
CZ05 | 36.6167 | 28.0117 | CZ05 | 13.9887 | 14.2751
CZ06 | 40.6072 | 30.5467 | CZ06 | 11.3861 | 11.2618
CZ07 | 40.6568 | 30.4991 | CZ07 | 10.9926 | 11.3245
CZ08 | 41.0995 | 31.3489 | CZ08 | 11.8151 | 11.9187
CZ09 | 43.0501 | 31.7726 | CZ09 | 11.387 | 11.4806
CZ10 | 43.6584 | 33.5071 | CZ10 | 12.6051 | 12.4487
CZ11 | 44.321 | 33.6462 | CZ11 | 17.1458 | 15.335
CZ12 | 41.9335 | 32.0763 | CZ12 | 16.3358 | 15.2192
CZ13 | 45.7532 | 34.6975 | CZ13 | 15.0502 | 14.2798
CZ14 | 49.7271 | 37.364 | CZ14 | 13.068 | 13.278
CZ15 | 55.8173 | 42.3134 | CZ15 | 11.1698 | 11.3459
CZ16 | 43.6608 | 33.3549 | CZ16 | 20.1154 | 18.7103
cDXGF ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXGF ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 35.6069 | 27.8698 | CZ01 | 17.8326 | 16.658
CZ02 | 40.2611 | 30.7715 | CZ02 | 15.152 | 13.9263
CZ03 | 38.8962 | 29.6002 | CZ03 | 13.2415 | 12.9777
CZ04 | 41.3181 | 31.4751 | CZ04 | 12.5555 | 12.1141
CZ05 | 39.8931 | 30.2106 | CZ05 | 13.0732 | 13.02
CZ06 | 42.9324 | 32.1897 | CZ06 | 11.1149 | 10.883
CZ07 | 42.7496 | 32.3408 | CZ07 | 10.7225 | 10.727
CZ08 | 43.8782 | 33.3063 | CZ08 | 11.1395 | 11.0698
CZ09 | 45.2996 | 33.6733 | CZ09 | 11.0411 | 10.7727
CZ10 | 46.5088 | 35.5236 | CZ10 | 11.4736 | 11.2919
CZ11 | 47.4069 | 35.5984 | CZ11 | 15.1557 | 13.491
CZ12 | 44.8842 | 34.0438 | CZ12 | 14.5638 | 13.4813
CZ13 | 48.4514 | 36.5102 | CZ13 | 13.4357 | 12.6409
CZ14 | 52.0395 | 39.2755 | CZ14 | 12.1465 | 11.9967
CZ15 | 57.3168 | 43.0852 | CZ15 | 10.3652 | 10.5608
CZ16 | 47.1086 | 35.8138 | CZ16 | 18.0365 | 16.5624
cDXHP ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXHP ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 36.1536 | 28.5684 | CZ01 | 15.6238 | 13.7841
CZ02 | 40.6417 | 31.2225 | CZ02 | 13.7971 | 12.2557
CZ03 | 39.0743 | 29.8744 | CZ03 | 12.4842 | 11.8332
CZ04 | 41.4849 | 31.6916 | CZ04 | 11.9025 | 11.2427
CZ05 | 40.0788 | 30.5081 | CZ05 | 12.3296 | 11.8376
CZ06 | 42.9002 | 32.1944 | CZ06 | 11.0097 | 10.6548
CZ07 | 42.7413 | 32.3542 | CZ07 | 10.6324 | 10.5189
CZ08 | 43.9032 | 33.3741 | CZ08 | 10.9476 | 10.723
CZ09 | 45.312 | 33.7123 | CZ09 | 10.9072 | 10.5371
CZ10 | 46.6362 | 35.6909 | CZ10 | 11.0248 | 10.669
CZ11 | 47.762 | 36.0003 | CZ11 | 13.8779 | 11.9774
CZ12 | 45.24 | 34.4648 | CZ12 | 13.3089 | 11.9389
CZ13 | 48.7177 | 36.8281 | CZ13 | 12.4708 | 11.3841
CZ14 | 52.2098 | 39.5043 | CZ14 | 11.5515 | 11.1752
CZ15 | 57.3527 | 43.1563 | CZ15 | 10.1611 | 10.2737
CZ16 | 47.8782 | 36.6782 | CZ16 | 15.8883 | 13.9586
cDXOH ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXOH ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 35.6024 | 27.8678 | CZ01 | 16.0552 | 14.3853
CZ02 | 40.2531 | 30.749 | CZ02 | 14.0598 | 12.5839
CZ03 | 38.8895 | 29.5901 | CZ03 | 12.6346 | 12.0506
CZ04 | 41.3101 | 31.448 | CZ04 | 12.0128 | 11.3097
CZ05 | 39.8763 | 30.1721 | CZ05 | 12.4185 | 11.9633
CZ06 | 42.9324 | 32.1831 | CZ06 | 11.0163 | 10.6674
CZ07 | 42.7423 | 32.3423 | CZ07 | 10.634 | 10.538
CZ08 | 43.8697 | 33.2967 | CZ08 | 10.9619 | 10.7531
CZ09 | 45.2925 | 33.6596 | CZ09 | 10.9114 | 10.5507
CZ10 | 46.5004 | 35.508 | CZ10 | 11.0797 | 10.7404
CZ11 | 47.4017 | 35.59 | CZ11 | 14.1342 | 12.3376
CZ12 | 44.8782 | 34.041 | CZ12 | 13.568 | 12.301
CZ13 | 48.4559 | 36.4986 | CZ13 | 12.7163 | 11.6839
CZ14 | 52.0279 | 39.2525 | CZ14 | 11.6394 | 11.2907
CZ15 | 57.3011 | 43.0601 | CZ15 | 10.1782 | 10.2762
CZ16 | 47.0992 | 35.7905 | CZ16 | 16.2642 | 14.5072
cPVVG ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cPVVG ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 32.4769 | 25.7935 | CZ01 | 19.0552 | 17.6918
CZ02 | 36.8972 | 28.47 | CZ02 | 15.9542 | 14.5959
CZ03 | 35.6668 | 27.3131 | CZ03 | 13.7963 | 13.5258
CZ04 | 37.9984 | 29.1743 | CZ04 | 13.0598 | 12.532
CZ05 | 36.7816 | 27.9769 | CZ05 | 13.5645 | 13.5024
CZ06 | 40.025 | 30.021 | CZ06 | 11.2612 | 11.0357
CZ07 | 39.8436 | 30.1842 | CZ07 | 10.8245 | 10.8671
CZ08 | 40.764 | 31.0252 | CZ08 | 11.3188 | 11.2722
CZ09 | 42.1186 | 31.4691 | CZ09 | 11.1831 | 10.9267
CZ10 | 43.2204 | 33.1432 | CZ10 | 11.7999 | 11.6
CZ11 | 43.9606 | 33.2522 | CZ11 | 16.0056 | 14.1919
CZ12 | 41.6428 | 31.7537 | CZ12 | 15.3166 | 14.0888
CZ13 | 45.173 | 34.203 | CZ13 | 14.1095 | 13.214
CZ14 | 48.5634 | 36.8716 | CZ14 | 12.6029 | 12.425
CZ15 | 54.257 | 41.0348 | CZ15 | 10.4893 | 10.7044
CZ16 | 43.4287 | 33.1673 | CZ16 | 19.0836 | 17.5068

## Raw_totalendusesannual (hidden)
Vintage | Climate Zone | HVAC System | Electricity (kBtu) | Natural Gas (kBtu)
Existing | CZ01 | cAVVG | 1937973.45 | 1208242.52
Existing | CZ02 | cAVVG | 2218040.49 | 1001521.47
Existing | CZ03 | cAVVG | 2132438.18 | 852730.29
Existing | CZ04 | cAVVG | 2292111.17 | 807240.82
Existing | CZ05 | cAVVG | 2197241.44 | 839413.8
Existing | CZ06 | cAVVG | 2436694.71 | 683240.51
Existing | CZ07 | cAVVG | 2439670.05 | 659629.25
Existing | CZ08 | cAVVG | 2466235.07 | 708981.16
Existing | CZ09 | cAVVG | 2583283.29 | 683294.85
Existing | CZ10 | cAVVG | 2619789.6 | 756386.05
Existing | CZ11 | cAVVG | 2659549.03 | 1028861.01
Existing | CZ12 | cAVVG | 2516279.9 | 980251.94
Existing | CZ13 | cAVVG | 2745486.83 | 903107.39
Existing | CZ14 | cAVVG | 2983951.37 | 784164.1
Existing | CZ15 | cAVVG | 3349402.35 | 670262.14
Existing | CZ16 | cAVVG | 2619931.51 | 1207053.82
New Construction | CZ01 | cAVVG | 1546695.71 | 1175358.76
New Construction | CZ02 | cAVVG | 1713774.44 | 944953.58
New Construction | CZ03 | cAVVG | 1643995.15 | 851958.21
New Construction | CZ04 | cAVVG | 1755969.29 | 800112.86
New Construction | CZ05 | cAVVG | 1680884.94 | 856601.49
New Construction | CZ06 | cAVVG | 1833002.95 | 675781.87
New Construction | CZ07 | cAVVG | 1830144.6 | 679543.13
New Construction | CZ08 | cAVVG | 1881136.23 | 715202.07
New Construction | CZ09 | cAVVG | 1906562.93 | 688910.93
New Construction | CZ10 | cAVVG | 2010641.37 | 747002.58
New Construction | CZ11 | cAVVG | 2018992.54 | 920199.21
New Construction | CZ12 | cAVVG | 1924787.64 | 913249.85
New Construction | CZ13 | cAVVG | 2082074.27 | 856878.72
New Construction | CZ14 | cAVVG | 2242082.84 | 796765.41
New Construction | CZ15 | cAVVG | 2539081.18 | 680828.1
New Construction | CZ16 | cAVVG | 2001508.68 | 1122739.36
Existing | CZ01 | cDXGF | 2136646.3 | 1070072.71
Existing | CZ02 | cDXGF | 2415927.04 | 909216.07
Existing | CZ03 | cDXGF | 2334021.84 | 794577.6
Existing | CZ04 | cDXGF | 2479354.48 | 753411.74
Existing | CZ05 | cDXGF | 2393847.1 | 784477.17
Existing | CZ06 | cDXGF | 2576224.39 | 666966.62
Existing | CZ07 | cDXGF | 2565254.7 | 643422.11
Existing | CZ08 | cDXGF | 2632974.29 | 668440.2
Existing | CZ09 | cDXGF | 2718269.23 | 662534.89
Existing | CZ10 | cDXGF | 2790830.9 | 688491.65
Existing | CZ11 | cDXGF | 2844723.25 | 909441.4
Existing | CZ12 | cDXGF | 2693345.38 | 873924.85
Existing | CZ13 | cDXGF | 2907398.57 | 806228.6
Existing | CZ14 | cDXGF | 3122705.9 | 728866.22
Existing | CZ15 | cDXGF | 3439380.99 | 621981.35
Existing | CZ16 | cDXGF | 2826824.21 | 1082304.41
New Construction | CZ01 | cDXGF | 1672368.44 | 999590.4
New Construction | CZ02 | cDXGF | 1846488.12 | 835667.12
New Construction | CZ03 | cDXGF | 1776202.4 | 778749.13
New Construction | CZ04 | cDXGF | 1888711.97 | 726924.38
New Construction | CZ05 | cDXGF | 1812832.37 | 781282.37
New Construction | CZ06 | cDXGF | 1931592.22 | 653050.53
New Construction | CZ07 | cDXGF | 1940655.92 | 643689.08
New Construction | CZ08 | cDXGF | 1998595.91 | 664262.62
New Construction | CZ09 | cDXGF | 2020617.96 | 646432.97
New Construction | CZ10 | cDXGF | 2131645.24 | 677586.17
New Construction | CZ11 | cDXGF | 2136132.13 | 809545.77
New Construction | CZ12 | cDXGF | 2042848.13 | 808967.28
New Construction | CZ13 | cDXGF | 2190847.13 | 758533.16
New Construction | CZ14 | cDXGF | 2356783.72 | 719882.35
New Construction | CZ15 | cDXGF | 2585389.25 | 633716.85
New Construction | CZ16 | cDXGF | 2149062.89 | 993848.63
Existing | CZ01 | cDXHP | 2169451.42 | 937526.92
Existing | CZ02 | cDXHP | 2438767.98 | 827915.76
Existing | CZ03 | cDXHP | 2344710.22 | 749132.97
Existing | CZ04 | cDXHP | 2489361.07 | 714230.2
Existing | CZ05 | cDXHP | 2404987.69 | 739858.63
Existing | CZ06 | cDXHP | 2574291.68 | 660651.18
Existing | CZ07 | cDXHP | 2564756 | 638010.18
Existing | CZ08 | cDXHP | 2634478.18 | 656924.51
Existing | CZ09 | cDXHP | 2719011.13 | 654501.03
Existing | CZ10 | cDXHP | 2798474.68 | 661559.78
Existing | CZ11 | cDXHP | 2866032.54 | 832763.09
Existing | CZ12 | cDXHP | 2714695.3 | 798619.01
Existing | CZ13 | cDXHP | 2923378.4 | 748326.56
Existing | CZ14 | cDXHP | 3132925.34 | 693164.5
Existing | CZ15 | cDXHP | 3441533.89 | 609734.89
Existing | CZ16 | cDXHP | 2873001.38 | 953398.23
New Construction | CZ01 | cDXHP | 1714290.92 | 827137.82
New Construction | CZ02 | cDXHP | 1873551.85 | 735419.16
New Construction | CZ03 | cDXHP | 1792659.16 | 710069.98
New Construction | CZ04 | cDXHP | 1901700.74 | 674636.11
New Construction | CZ05 | cDXHP | 1830683.92 | 710333.07
New Construction | CZ06 | cDXHP | 1931871.51 | 639355.78
New Construction | CZ07 | cDXHP | 1941464.07 | 631200.34
New Construction | CZ08 | cDXHP | 2002662.57 | 643448.63
New Construction | CZ09 | cDXHP | 2022954.4 | 632292.86
New Construction | CZ10 | cDXHP | 2141686.78 | 640208.43
New Construction | CZ11 | cDXHP | 2160249 | 718721.28
New Construction | CZ12 | cDXHP | 2068110.14 | 716411.55
New Construction | CZ13 | cDXHP | 2209923.97 | 683117.3
New Construction | CZ14 | cDXHP | 2370513.71 | 670584.24
New Construction | CZ15 | cDXHP | 2589659.16 | 616490.37
New Construction | CZ16 | cDXHP | 2200929.38 | 837609.54
Existing | CZ01 | cDXOH | 2136373.99 | 963416.48
Existing | CZ02 | cDXOH | 2415447.94 | 843680.7
Existing | CZ03 | cDXOH | 2333623.49 | 758160.43
Existing | CZ04 | cDXOH | 2478873.11 | 720846.56
Existing | CZ05 | cDXOH | 2392837.59 | 745190.33
Existing | CZ06 | cDXOH | 2576221.08 | 661050.56
Existing | CZ07 | cDXOH | 2564814.43 | 638106.35
Existing | CZ08 | cDXOH | 2632467.14 | 657787.8
Existing | CZ09 | cDXOH | 2717845.5 | 654755.32
Existing | CZ10 | cDXOH | 2790327.05 | 664856.54
Existing | CZ11 | cDXOH | 2844407.44 | 848142.92
Existing | CZ12 | cDXOH | 2692986 | 814166.19
Existing | CZ13 | cDXOH | 2907667.78 | 763059.74
Existing | CZ14 | cDXOH | 3122011.1 | 698436.85
Existing | CZ15 | cDXOH | 3438435.92 | 610758.91
Existing | CZ16 | cDXOH | 2826256.73 | 975958.93
New Construction | CZ01 | cDXOH | 1672248.41 | 863212.32
New Construction | CZ02 | cDXOH | 1845137.33 | 755113.43
New Construction | CZ03 | cDXOH | 1775600.81 | 723115.45
New Construction | CZ04 | cDXOH | 1887084.76 | 678655.88
New Construction | CZ05 | cDXOH | 1810520.53 | 717877.51
New Construction | CZ06 | cDXOH | 1931197.38 | 640113.05
New Construction | CZ07 | cDXOH | 1940749.74 | 632351
New Construction | CZ08 | cDXOH | 1998017.71 | 645256.4
New Construction | CZ09 | cDXOH | 2019792.21 | 633109.79
New Construction | CZ10 | cDXOH | 2130709.47 | 644493.1
New Construction | CZ11 | cDXOH | 2135631.21 | 740337.97
New Construction | CZ12 | cDXOH | 2042677.95 | 738137.66
New Construction | CZ13 | cDXOH | 2190150.77 | 701108.78
New Construction | CZ14 | cDXOH | 2355402.77 | 677516.01
New Construction | CZ15 | cDXOH | 2583882.78 | 616638.79
New Construction | CZ16 | cDXOH | 2147659.38 | 870527.51
Existing | CZ01 | cPVVG | 1948825.87 | 1143437.8
Existing | CZ02 | cPVVG | 2214072.23 | 957353.83
Existing | CZ03 | cPVVG | 2140236.54 | 827869.15
Existing | CZ04 | cPVVG | 2280153.47 | 783674.83
Existing | CZ05 | cPVVG | 2207133 | 813957.95
Existing | CZ06 | cPVVG | 2401760.52 | 675745.49
Existing | CZ07 | cPVVG | 2390876.56 | 649539.58
Existing | CZ08 | cPVVG | 2446102.29 | 679199.22
Existing | CZ09 | cPVVG | 2527387.22 | 671058.08
Existing | CZ10 | cPVVG | 2593506.57 | 708070.9
Existing | CZ11 | cPVVG | 2637921.24 | 960438.76
Existing | CZ12 | cPVVG | 2498840.51 | 919095.67
Existing | CZ13 | cPVVG | 2710673.8 | 846660.45
Existing | CZ14 | cPVVG | 2914119.58 | 756255.84
Existing | CZ15 | cPVVG | 3255774.23 | 629426.93
Existing | CZ16 | cPVVG | 2606005.37 | 1145142.04
New Construction | CZ01 | cPVVG | 1547776.35 | 1061623.47
New Construction | CZ02 | cPVVG | 1708383.66 | 875846.05
New Construction | CZ03 | cPVVG | 1638963.59 | 811634.12
New Construction | CZ04 | cPVVG | 1750649.82 | 751998.81
New Construction | CZ05 | cPVVG | 1678796.61 | 810230.97
New Construction | CZ06 | cPVVG | 1801453.67 | 662211.81
New Construction | CZ07 | cPVVG | 1811245 | 652099.11
New Construction | CZ08 | cPVVG | 1861713.71 | 676404.76
New Construction | CZ09 | cPVVG | 1888348.56 | 655673.79
New Construction | CZ10 | cPVVG | 1988809.75 | 696075.24
New Construction | CZ11 | cPVVG | 1995349.46 | 851604.18
New Construction | CZ12 | cPVVG | 1905425.73 | 845421.47
New Construction | CZ13 | cPVVG | 2052402.3 | 792922.76
New Construction | CZ14 | cPVVG | 2212536.74 | 745578.54
New Construction | CZ15 | cPVVG | 2462354.59 | 642332.44
New Construction | CZ16 | cPVVG | 1990253.68 | 1050521.11

## Energy Usage by End Use
Energy Consumption by End Use - Health/Medical - Nursing Home
Climate Zone | HVAC System | Vintage | End Use | Electricity (kBtu) | Natural Gas (kBtu) | Note
CZ01 | cAVVG | Existing | Heating | 0 | 514010.34
CZ01 | cAVVG | Existing | Cooling | 71008.63 | 0
CZ01 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ01 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ01 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ01 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ01 | cAVVG | Existing | Fans | 216053.37 | 0
CZ01 | cAVVG | Existing | Pumps | 806.93 | 0
CZ01 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ01 | cAVVG | Existing | Humidification | 0 | 0
CZ01 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ01 | cAVVG | Existing | Water Systems | 0 | 469376.41
CZ01 | cAVVG | Existing | Refrigeration | 0 | 0
CZ01 | cAVVG | Existing | Generators | 0 | 0
CZ01 | cAVVG | Existing | Total End Uses | 1937973.45 | 1208242.52
CZ02 | cAVVG | Existing | Heating | 0 | 345324.29
CZ02 | cAVVG | Existing | Cooling | 292904.16 | 0
CZ02 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ02 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ02 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ02 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ02 | cAVVG | Existing | Fans | 269720.73 | 0
CZ02 | cAVVG | Existing | Pumps | 5311.08 | 0
CZ02 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ02 | cAVVG | Existing | Humidification | 0 | 0
CZ02 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ02 | cAVVG | Existing | Water Systems | 0 | 431341.4
CZ02 | cAVVG | Existing | Refrigeration | 0 | 0
CZ02 | cAVVG | Existing | Generators | 0 | 0
CZ02 | cAVVG | Existing | Total End Uses | 2218040.49 | 1001521.47
CZ03 | cAVVG | Existing | Heating | 0 | 198227.66
CZ03 | cAVVG | Existing | Cooling | 225235.41 | 0
CZ03 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ03 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ03 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ03 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ03 | cAVVG | Existing | Fans | 252643.51 | 0
CZ03 | cAVVG | Existing | Pumps | 4454.73 | 0
CZ03 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ03 | cAVVG | Existing | Humidification | 0 | 0
CZ03 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ03 | cAVVG | Existing | Water Systems | 0 | 429646.85
CZ03 | cAVVG | Existing | Refrigeration | 0 | 0
CZ03 | cAVVG | Existing | Generators | 0 | 0
CZ03 | cAVVG | Existing | Total End Uses | 2132438.18 | 852730.29
CZ04 | cAVVG | Existing | Heating | 0 | 167479.39
CZ04 | cAVVG | Existing | Cooling | 346023.64 | 0
CZ04 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ04 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ04 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ04 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ04 | cAVVG | Existing | Fans | 289646.1 | 0
CZ04 | cAVVG | Existing | Pumps | 6336.91 | 0
CZ04 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ04 | cAVVG | Existing | Humidification | 0 | 0
CZ04 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ04 | cAVVG | Existing | Water Systems | 0 | 414905.65
CZ04 | cAVVG | Existing | Refrigeration | 0 | 0
CZ04 | cAVVG | Existing | Generators | 0 | 0
CZ04 | cAVVG | Existing | Total End Uses | 2292111.17 | 807240.82
CZ05 | cAVVG | Existing | Heating | 0 | 184878.26
CZ05 | cAVVG | Existing | Cooling | 273255.83 | 0
CZ05 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ05 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ05 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ05 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ05 | cAVVG | Existing | Fans | 269550.36 | 0
CZ05 | cAVVG | Existing | Pumps | 4330.73 | 0
CZ05 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ05 | cAVVG | Existing | Humidification | 0 | 0
CZ05 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ05 | cAVVG | Existing | Water Systems | 0 | 429679.76
CZ05 | cAVVG | Existing | Refrigeration | 0 | 0
CZ05 | cAVVG | Existing | Generators | 0 | 0
CZ05 | cAVVG | Existing | Total End Uses | 2197241.44 | 839413.8
CZ06 | cAVVG | Existing | Heating | 0 | 62553.66
CZ06 | cAVVG | Existing | Cooling | 448347.44 | 0
CZ06 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ06 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ06 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ06 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ06 | cAVVG | Existing | Fans | 329965.71 | 0
CZ06 | cAVVG | Existing | Pumps | 8277.03 | 0
CZ06 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ06 | cAVVG | Existing | Humidification | 0 | 0
CZ06 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ06 | cAVVG | Existing | Water Systems | 0 | 395831.07
CZ06 | cAVVG | Existing | Refrigeration | 0 | 0
CZ06 | cAVVG | Existing | Generators | 0 | 0
CZ06 | cAVVG | Existing | Total End Uses | 2436694.71 | 683240.51
CZ07 | cAVVG | Existing | Heating | 0 | 43953.85
CZ07 | cAVVG | Existing | Cooling | 453101.86 | 0
CZ07 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ07 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ07 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ07 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ07 | cAVVG | Existing | Fans | 327308.74 | 0
CZ07 | cAVVG | Existing | Pumps | 9154.93 | 0
CZ07 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ07 | cAVVG | Existing | Humidification | 0 | 0
CZ07 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ07 | cAVVG | Existing | Water Systems | 0 | 390819.63
CZ07 | cAVVG | Existing | Refrigeration | 0 | 0
CZ07 | cAVVG | Existing | Generators | 0 | 0
CZ07 | cAVVG | Existing | Total End Uses | 2439670.05 | 659629.25
CZ08 | cAVVG | Existing | Heating | 0 | 93877.24
CZ08 | cAVVG | Existing | Cooling | 483036.57 | 0
CZ08 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ08 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ08 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ08 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ08 | cAVVG | Existing | Fans | 326055.89 | 0
CZ08 | cAVVG | Existing | Pumps | 7038.09 | 0
CZ08 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ08 | cAVVG | Existing | Humidification | 0 | 0
CZ08 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ08 | cAVVG | Existing | Water Systems | 0 | 390248.14
CZ08 | cAVVG | Existing | Refrigeration | 0 | 0
CZ08 | cAVVG | Existing | Generators | 0 | 0
CZ08 | cAVVG | Existing | Total End Uses | 2466235.07 | 708981.16
CZ09 | cAVVG | Existing | Heating | 0 | 73602.98
CZ09 | cAVVG | Existing | Cooling | 555684.84 | 0
CZ09 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ09 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ09 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ09 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ09 | cAVVG | Existing | Fans | 367630.75 | 0
CZ09 | cAVVG | Existing | Pumps | 9863.18 | 0
CZ09 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ09 | cAVVG | Existing | Humidification | 0 | 0
CZ09 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ09 | cAVVG | Existing | Water Systems | 0 | 384836.09
CZ09 | cAVVG | Existing | Refrigeration | 0 | 0
CZ09 | cAVVG | Existing | Generators | 0 | 0
CZ09 | cAVVG | Existing | Total End Uses | 2583283.29 | 683294.85
CZ10 | cAVVG | Existing | Heating | 0 | 149781.39
CZ10 | cAVVG | Existing | Cooling | 605504.8 | 0
CZ10 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ10 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ10 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ10 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ10 | cAVVG | Existing | Fans | 357228.71 | 0
CZ10 | cAVVG | Existing | Pumps | 6951.57 | 0
CZ10 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ10 | cAVVG | Existing | Humidification | 0 | 0
CZ10 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ10 | cAVVG | Existing | Water Systems | 0 | 381748.89
CZ10 | cAVVG | Existing | Refrigeration | 0 | 0
CZ10 | cAVVG | Existing | Generators | 0 | 0
CZ10 | cAVVG | Existing | Total End Uses | 2619789.6 | 756386.05
CZ11 | cAVVG | Existing | Heating | 0 | 413763.4
CZ11 | cAVVG | Existing | Cooling | 638140.11 | 0
CZ11 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ11 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ11 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ11 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ11 | cAVVG | Existing | Fans | 364973.29 | 0
CZ11 | cAVVG | Existing | Pumps | 6331.11 | 0
CZ11 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ11 | cAVVG | Existing | Humidification | 0 | 0
CZ11 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ11 | cAVVG | Existing | Water Systems | 0 | 390241.83
CZ11 | cAVVG | Existing | Refrigeration | 0 | 0
CZ11 | cAVVG | Existing | Generators | 0 | 0
CZ11 | cAVVG | Existing | Total End Uses | 2659549.03 | 1028861.01
CZ12 | cAVVG | Existing | Heating | 0 | 354163.22
CZ12 | cAVVG | Existing | Cooling | 527187.85 | 0
CZ12 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ12 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ12 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ12 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ12 | cAVVG | Existing | Fans | 332990.67 | 0
CZ12 | cAVVG | Existing | Pumps | 5996.85 | 0
CZ12 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ12 | cAVVG | Existing | Humidification | 0 | 0
CZ12 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ12 | cAVVG | Existing | Water Systems | 0 | 401232.94
CZ12 | cAVVG | Existing | Refrigeration | 0 | 0
CZ12 | cAVVG | Existing | Generators | 0 | 0
CZ12 | cAVVG | Existing | Total End Uses | 2516279.9 | 980251.94
CZ13 | cAVVG | Existing | Heating | 0 | 299332.92
CZ13 | cAVVG | Existing | Cooling | 704741.31 | 0
CZ13 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ13 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ13 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ13 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ13 | cAVVG | Existing | Fans | 383537.81 | 0
CZ13 | cAVVG | Existing | Pumps | 7103.18 | 0
CZ13 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ13 | cAVVG | Existing | Humidification | 0 | 0
CZ13 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ13 | cAVVG | Existing | Water Systems | 0 | 378918.69
CZ13 | cAVVG | Existing | Refrigeration | 0 | 0
CZ13 | cAVVG | Existing | Generators | 0 | 0
CZ13 | cAVVG | Existing | Total End Uses | 2745486.83 | 903107.39
CZ14 | cAVVG | Existing | Heating | 0 | 199606.42
CZ14 | cAVVG | Existing | Cooling | 869420.88 | 0
CZ14 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ14 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ14 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ14 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ14 | cAVVG | Existing | Fans | 453839.61 | 0
CZ14 | cAVVG | Existing | Pumps | 10586.36 | 0
CZ14 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ14 | cAVVG | Existing | Humidification | 0 | 0
CZ14 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ14 | cAVVG | Existing | Water Systems | 0 | 359701.9
CZ14 | cAVVG | Existing | Refrigeration | 0 | 0
CZ14 | cAVVG | Existing | Generators | 0 | 0
CZ14 | cAVVG | Existing | Total End Uses | 2983951.37 | 784164.1
CZ15 | cAVVG | Existing | Heating | 0 | 126013.2
CZ15 | cAVVG | Existing | Cooling | 1214832.82 | 0
CZ15 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ15 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ15 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ15 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ15 | cAVVG | Existing | Fans | 474396.02 | 0
CZ15 | cAVVG | Existing | Pumps | 10068.99 | 0
CZ15 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ15 | cAVVG | Existing | Humidification | 0 | 0
CZ15 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ15 | cAVVG | Existing | Water Systems | 0 | 319393.16
CZ15 | cAVVG | Existing | Refrigeration | 0 | 0
CZ15 | cAVVG | Existing | Generators | 0 | 0
CZ15 | cAVVG | Existing | Total End Uses | 3349402.35 | 670262.14
CZ16 | cAVVG | Existing | Heating | 0 | 557960.29
CZ16 | cAVVG | Existing | Cooling | 547952.92 | 0
CZ16 | cAVVG | Existing | Interior Lighting | 687070.6 | 0
CZ16 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ16 | cAVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ16 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ16 | cAVVG | Existing | Fans | 415594.07 | 0
CZ16 | cAVVG | Existing | Pumps | 6280 | 0
CZ16 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ16 | cAVVG | Existing | Humidification | 0 | 0
CZ16 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ16 | cAVVG | Existing | Water Systems | 0 | 424237.74
CZ16 | cAVVG | Existing | Refrigeration | 0 | 0
CZ16 | cAVVG | Existing | Generators | 0 | 0
CZ16 | cAVVG | Existing | Total End Uses | 2619931.51 | 1207053.82
CZ01 | cAVVG | New Construction | Heating | 0 | 481355.79
CZ01 | cAVVG | New Construction | Cooling | 49179.03 | 0
CZ01 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ01 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ01 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ01 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ01 | cAVVG | New Construction | Fans | 181192.96 | 0
CZ01 | cAVVG | New Construction | Pumps | 619.92 | 0
CZ01 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ01 | cAVVG | New Construction | Humidification | 0 | 0
CZ01 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ01 | cAVVG | New Construction | Water Systems | 0 | 469147.19
CZ01 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ01 | cAVVG | New Construction | Generators | 0 | 0
CZ01 | cAVVG | New Construction | Total End Uses | 1546695.71 | 1175358.76
CZ02 | cAVVG | New Construction | Heating | 0 | 289043.58
CZ02 | cAVVG | New Construction | Cooling | 199915.31 | 0
CZ02 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ02 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ02 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ02 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ02 | cAVVG | New Construction | Fans | 195162.19 | 0
CZ02 | cAVVG | New Construction | Pumps | 2993.14 | 0
CZ02 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ02 | cAVVG | New Construction | Humidification | 0 | 0
CZ02 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ02 | cAVVG | New Construction | Water Systems | 0 | 431054.23
CZ02 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ02 | cAVVG | New Construction | Generators | 0 | 0
CZ02 | cAVVG | New Construction | Total End Uses | 1713774.44 | 944953.58
CZ03 | cAVVG | New Construction | Heating | 0 | 197660.19
CZ03 | cAVVG | New Construction | Cooling | 144394.39 | 0
CZ03 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ03 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ03 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ03 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ03 | cAVVG | New Construction | Fans | 180732.48 | 0
CZ03 | cAVVG | New Construction | Pumps | 3164.49 | 0
CZ03 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ03 | cAVVG | New Construction | Humidification | 0 | 0
CZ03 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ03 | cAVVG | New Construction | Water Systems | 0 | 429442.24
CZ03 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ03 | cAVVG | New Construction | Generators | 0 | 0
CZ03 | cAVVG | New Construction | Total End Uses | 1643995.15 | 851958.21
CZ04 | cAVVG | New Construction | Heating | 0 | 160657.83
CZ04 | cAVVG | New Construction | Cooling | 235873.63 | 0
CZ04 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ04 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ04 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ04 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ04 | cAVVG | New Construction | Fans | 201001.52 | 0
CZ04 | cAVVG | New Construction | Pumps | 3390.34 | 0
CZ04 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ04 | cAVVG | New Construction | Humidification | 0 | 0
CZ04 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ04 | cAVVG | New Construction | Water Systems | 0 | 414599.25
CZ04 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ04 | cAVVG | New Construction | Generators | 0 | 0
CZ04 | cAVVG | New Construction | Total End Uses | 1755969.29 | 800112.86
CZ05 | cAVVG | New Construction | Heating | 0 | 202273.26
CZ05 | cAVVG | New Construction | Cooling | 173312.44 | 0
CZ05 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ05 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ05 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ05 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ05 | cAVVG | New Construction | Fans | 188861.75 | 0
CZ05 | cAVVG | New Construction | Pumps | 3006.96 | 0
CZ05 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ05 | cAVVG | New Construction | Humidification | 0 | 0
CZ05 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ05 | cAVVG | New Construction | Water Systems | 0 | 429472.45
CZ05 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ05 | cAVVG | New Construction | Generators | 0 | 0
CZ05 | cAVVG | New Construction | Total End Uses | 1680884.94 | 856601.49
CZ06 | cAVVG | New Construction | Heating | 0 | 55295.47
CZ06 | cAVVG | New Construction | Cooling | 294839.46 | 0
CZ06 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ06 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ06 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ06 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ06 | cAVVG | New Construction | Fans | 216629.65 | 0
CZ06 | cAVVG | New Construction | Pumps | 5830.04 | 0
CZ06 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ06 | cAVVG | New Construction | Humidification | 0 | 0
CZ06 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ06 | cAVVG | New Construction | Water Systems | 0 | 395630.62
CZ06 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ06 | cAVVG | New Construction | Generators | 0 | 0
CZ06 | cAVVG | New Construction | Total End Uses | 1833002.95 | 675781.87
CZ07 | cAVVG | New Construction | Heating | 0 | 64160.71
CZ07 | cAVVG | New Construction | Cooling | 298920.87 | 0
CZ07 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ07 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ07 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ07 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ07 | cAVVG | New Construction | Fans | 210568.1 | 0
CZ07 | cAVVG | New Construction | Pumps | 4951.83 | 0
CZ07 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ07 | cAVVG | New Construction | Humidification | 0 | 0
CZ07 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ07 | cAVVG | New Construction | Water Systems | 0 | 390526.63
CZ07 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ07 | cAVVG | New Construction | Generators | 0 | 0
CZ07 | cAVVG | New Construction | Total End Uses | 1830144.6 | 679543.13
CZ08 | cAVVG | New Construction | Heating | 0 | 100312.34
CZ08 | cAVVG | New Construction | Cooling | 338115.76 | 0
CZ08 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ08 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ08 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ08 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ08 | cAVVG | New Construction | Fans | 222328.1 | 0
CZ08 | cAVVG | New Construction | Pumps | 4988.58 | 0
CZ08 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ08 | cAVVG | New Construction | Humidification | 0 | 0
CZ08 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ08 | cAVVG | New Construction | Water Systems | 0 | 390033.95
CZ08 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ08 | cAVVG | New Construction | Generators | 0 | 0
CZ08 | cAVVG | New Construction | Total End Uses | 1881136.23 | 715202.07
CZ09 | cAVVG | New Construction | Heating | 0 | 79506.14
CZ09 | cAVVG | New Construction | Cooling | 358445.68 | 0
CZ09 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ09 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ09 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ09 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ09 | cAVVG | New Construction | Fans | 227454.41 | 0
CZ09 | cAVVG | New Construction | Pumps | 4959.04 | 0
CZ09 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ09 | cAVVG | New Construction | Humidification | 0 | 0
CZ09 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ09 | cAVVG | New Construction | Water Systems | 0 | 384549.01
CZ09 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ09 | cAVVG | New Construction | Generators | 0 | 0
CZ09 | cAVVG | New Construction | Total End Uses | 1906562.93 | 688910.93
CZ10 | cAVVG | New Construction | Heating | 0 | 140667.3
CZ10 | cAVVG | New Construction | Cooling | 439352.91 | 0
CZ10 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ10 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ10 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ10 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ10 | cAVVG | New Construction | Fans | 250434.92 | 0
CZ10 | cAVVG | New Construction | Pumps | 5149.75 | 0
CZ10 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ10 | cAVVG | New Construction | Humidification | 0 | 0
CZ10 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ10 | cAVVG | New Construction | Water Systems | 0 | 381479.5
CZ10 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ10 | cAVVG | New Construction | Generators | 0 | 0
CZ10 | cAVVG | New Construction | Total End Uses | 2010641.37 | 747002.58
CZ11 | cAVVG | New Construction | Heating | 0 | 305432.34
CZ11 | cAVVG | New Construction | Cooling | 452129.02 | 0
CZ11 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ11 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ11 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ11 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ11 | cAVVG | New Construction | Fans | 246688.49 | 0
CZ11 | cAVVG | New Construction | Pumps | 4471.23 | 0
CZ11 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ11 | cAVVG | New Construction | Humidification | 0 | 0
CZ11 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ11 | cAVVG | New Construction | Water Systems | 0 | 389911.09
CZ11 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ11 | cAVVG | New Construction | Generators | 0 | 0
CZ11 | cAVVG | New Construction | Total End Uses | 2018992.54 | 920199.21
CZ12 | cAVVG | New Construction | Heating | 0 | 287394.5
CZ12 | cAVVG | New Construction | Cooling | 374576.91 | 0
CZ12 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ12 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ12 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ12 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ12 | cAVVG | New Construction | Fans | 230101.59 | 0
CZ12 | cAVVG | New Construction | Pumps | 4405.35 | 0
CZ12 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ12 | cAVVG | New Construction | Humidification | 0 | 0
CZ12 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ12 | cAVVG | New Construction | Water Systems | 0 | 400999.58
CZ12 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ12 | cAVVG | New Construction | Generators | 0 | 0
CZ12 | cAVVG | New Construction | Total End Uses | 1924787.64 | 913249.85
CZ13 | cAVVG | New Construction | Heating | 0 | 253291.96
CZ13 | cAVVG | New Construction | Cooling | 501835.58 | 0
CZ13 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ13 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ13 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ13 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ13 | cAVVG | New Construction | Fans | 259379.6 | 0
CZ13 | cAVVG | New Construction | Pumps | 5155.29 | 0
CZ13 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ13 | cAVVG | New Construction | Humidification | 0 | 0
CZ13 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ13 | cAVVG | New Construction | Water Systems | 0 | 378730.98
CZ13 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ13 | cAVVG | New Construction | Generators | 0 | 0
CZ13 | cAVVG | New Construction | Total End Uses | 2082074.27 | 856878.72
CZ14 | cAVVG | New Construction | Heating | 0 | 212393.73
CZ14 | cAVVG | New Construction | Cooling | 634579.55 | 0
CZ14 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ14 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ14 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ14 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ14 | cAVVG | New Construction | Fans | 286847.91 | 0
CZ14 | cAVVG | New Construction | Pumps | 4951.57 | 0
CZ14 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ14 | cAVVG | New Construction | Humidification | 0 | 0
CZ14 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ14 | cAVVG | New Construction | Water Systems | 0 | 359515.9
CZ14 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ14 | cAVVG | New Construction | Generators | 0 | 0
CZ14 | cAVVG | New Construction | Total End Uses | 2242082.84 | 796765.41
CZ15 | cAVVG | New Construction | Heating | 0 | 136880.19
CZ15 | cAVVG | New Construction | Cooling | 912344.05 | 0
CZ15 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ15 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ15 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ15 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ15 | cAVVG | New Construction | Fans | 303747.45 | 0
CZ15 | cAVVG | New Construction | Pumps | 7285.88 | 0
CZ15 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ15 | cAVVG | New Construction | Humidification | 0 | 0
CZ15 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ15 | cAVVG | New Construction | Water Systems | 0 | 319092.13
CZ15 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ15 | cAVVG | New Construction | Generators | 0 | 0
CZ15 | cAVVG | New Construction | Total End Uses | 2539081.18 | 680828.1
CZ16 | cAVVG | New Construction | Heating | 0 | 473821.89
CZ16 | cAVVG | New Construction | Cooling | 398255.34 | 0
CZ16 | cAVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ16 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ16 | cAVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ16 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ16 | cAVVG | New Construction | Fans | 282937.86 | 0
CZ16 | cAVVG | New Construction | Pumps | 4611.67 | 0
CZ16 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ16 | cAVVG | New Construction | Humidification | 0 | 0
CZ16 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ16 | cAVVG | New Construction | Water Systems | 0 | 424061.69
CZ16 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ16 | cAVVG | New Construction | Generators | 0 | 0
CZ16 | cAVVG | New Construction | Total End Uses | 2001508.68 | 1122739.36
CZ01 | cDXGF | Existing | Heating | 0 | 375841.32
CZ01 | cDXGF | Existing | Cooling | 67852.82 | 0
CZ01 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ01 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ01 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXGF | Existing | Fans | 418595.52 | 0
CZ01 | cDXGF | Existing | Pumps | 93.44 | 0
CZ01 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ01 | cDXGF | Existing | Humidification | 0 | 0
CZ01 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ01 | cDXGF | Existing | Water Systems | 0 | 469375.61
CZ01 | cDXGF | Existing | Refrigeration | 0 | 0
CZ01 | cDXGF | Existing | Generators | 0 | 0
CZ01 | cDXGF | Existing | Total End Uses | 2136646.3 | 1070072.71
CZ02 | cDXGF | Existing | Heating | 0 | 253027.43
CZ02 | cDXGF | Existing | Cooling | 266941.89 | 0
CZ02 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ02 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ02 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXGF | Existing | Fans | 498802.14 | 0
CZ02 | cDXGF | Existing | Pumps | 78.49 | 0
CZ02 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ02 | cDXGF | Existing | Humidification | 0 | 0
CZ02 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ02 | cDXGF | Existing | Water Systems | 0 | 431332.86
CZ02 | cDXGF | Existing | Refrigeration | 0 | 0
CZ02 | cDXGF | Existing | Generators | 0 | 0
CZ02 | cDXGF | Existing | Total End Uses | 2415927.04 | 909216.07
CZ03 | cDXGF | Existing | Heating | 0 | 140076.03
CZ03 | cDXGF | Existing | Cooling | 204982.04 | 0
CZ03 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ03 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ03 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXGF | Existing | Fans | 478855.83 | 0
CZ03 | cDXGF | Existing | Pumps | 79.44 | 0
CZ03 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ03 | cDXGF | Existing | Humidification | 0 | 0
CZ03 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ03 | cDXGF | Existing | Water Systems | 0 | 429645.79
CZ03 | cDXGF | Existing | Refrigeration | 0 | 0
CZ03 | cDXGF | Existing | Generators | 0 | 0
CZ03 | cDXGF | Existing | Total End Uses | 2334021.84 | 794577.6
CZ04 | cDXGF | Existing | Heating | 0 | 113655.82
CZ04 | cDXGF | Existing | Cooling | 316061.82 | 0
CZ04 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ04 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ04 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXGF | Existing | Fans | 513139.47 | 0
CZ04 | cDXGF | Existing | Pumps | 48.66 | 0
CZ04 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ04 | cDXGF | Existing | Humidification | 0 | 0
CZ04 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ04 | cDXGF | Existing | Water Systems | 0 | 414900.14
CZ04 | cDXGF | Existing | Refrigeration | 0 | 0
CZ04 | cDXGF | Existing | Generators | 0 | 0
CZ04 | cDXGF | Existing | Total End Uses | 2479354.48 | 753411.74
CZ05 | cDXGF | Existing | Heating | 0 | 129962.27
CZ05 | cDXGF | Existing | Cooling | 257990.06 | 0
CZ05 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ05 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ05 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXGF | Existing | Fans | 485634.33 | 0
CZ05 | cDXGF | Existing | Pumps | 118.18 | 0
CZ05 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ05 | cDXGF | Existing | Humidification | 0 | 0
CZ05 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ05 | cDXGF | Existing | Water Systems | 0 | 429659.13
CZ05 | cDXGF | Existing | Refrigeration | 0 | 0
CZ05 | cDXGF | Existing | Generators | 0 | 0
CZ05 | cDXGF | Existing | Total End Uses | 2393847.1 | 784477.17
CZ06 | cDXGF | Existing | Heating | 0 | 46252.54
CZ06 | cDXGF | Existing | Cooling | 408162.53 | 0
CZ06 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ06 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ06 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXGF | Existing | Fans | 517823.01 | 0
CZ06 | cDXGF | Existing | Pumps | 134.32 | 0
CZ06 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ06 | cDXGF | Existing | Humidification | 0 | 0
CZ06 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ06 | cDXGF | Existing | Water Systems | 0 | 395858.3
CZ06 | cDXGF | Existing | Refrigeration | 0 | 0
CZ06 | cDXGF | Existing | Generators | 0 | 0
CZ06 | cDXGF | Existing | Total End Uses | 2576224.39 | 666966.62
CZ07 | cDXGF | Existing | Heating | 0 | 27758.66
CZ07 | cDXGF | Existing | Cooling | 409565.7 | 0
CZ07 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ07 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ07 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXGF | Existing | Fans | 505508.63 | 0
CZ07 | cDXGF | Existing | Pumps | 75.85 | 0
CZ07 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ07 | cDXGF | Existing | Humidification | 0 | 0
CZ07 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ07 | cDXGF | Existing | Water Systems | 0 | 390807.67
CZ07 | cDXGF | Existing | Refrigeration | 0 | 0
CZ07 | cDXGF | Existing | Generators | 0 | 0
CZ07 | cDXGF | Existing | Total End Uses | 2565254.7 | 643422.11
CZ08 | cDXGF | Existing | Heating | 0 | 53363.87
CZ08 | cDXGF | Existing | Cooling | 445251.33 | 0
CZ08 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ08 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ08 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXGF | Existing | Fans | 537557.1 | 0
CZ08 | cDXGF | Existing | Pumps | 61.34 | 0
CZ08 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ08 | cDXGF | Existing | Humidification | 0 | 0
CZ08 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ08 | cDXGF | Existing | Water Systems | 0 | 390220.56
CZ08 | cDXGF | Existing | Refrigeration | 0 | 0
CZ08 | cDXGF | Existing | Generators | 0 | 0
CZ08 | cDXGF | Existing | Total End Uses | 2632974.29 | 668440.2
CZ09 | cDXGF | Existing | Heating | 0 | 52844.06
CZ09 | cDXGF | Existing | Cooling | 504532.75 | 0
CZ09 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ09 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ09 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXGF | Existing | Fans | 563565.5 | 0
CZ09 | cDXGF | Existing | Pumps | 66.46 | 0
CZ09 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ09 | cDXGF | Existing | Humidification | 0 | 0
CZ09 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ09 | cDXGF | Existing | Water Systems | 0 | 384835.05
CZ09 | cDXGF | Existing | Refrigeration | 0 | 0
CZ09 | cDXGF | Existing | Generators | 0 | 0
CZ09 | cDXGF | Existing | Total End Uses | 2718269.23 | 662534.89
CZ10 | cDXGF | Existing | Heating | 0 | 81904.47
CZ10 | cDXGF | Existing | Cooling | 570808.11 | 0
CZ10 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ10 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ10 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXGF | Existing | Fans | 569848.6 | 0
CZ10 | cDXGF | Existing | Pumps | 69.67 | 0
CZ10 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ10 | cDXGF | Existing | Humidification | 0 | 0
CZ10 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ10 | cDXGF | Existing | Water Systems | 0 | 381731.4
CZ10 | cDXGF | Existing | Refrigeration | 0 | 0
CZ10 | cDXGF | Existing | Generators | 0 | 0
CZ10 | cDXGF | Existing | Total End Uses | 2790830.9 | 688491.65
CZ11 | cDXGF | Existing | Heating | 0 | 294345.33
CZ11 | cDXGF | Existing | Cooling | 603818.82 | 0
CZ11 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ11 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ11 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXGF | Existing | Fans | 590699.1 | 0
CZ11 | cDXGF | Existing | Pumps | 100.81 | 0
CZ11 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ11 | cDXGF | Existing | Humidification | 0 | 0
CZ11 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ11 | cDXGF | Existing | Water Systems | 0 | 390240.29
CZ11 | cDXGF | Existing | Refrigeration | 0 | 0
CZ11 | cDXGF | Existing | Generators | 0 | 0
CZ11 | cDXGF | Existing | Total End Uses | 2844723.25 | 909441.4
CZ12 | cDXGF | Existing | Heating | 0 | 247857.58
CZ12 | cDXGF | Existing | Cooling | 498009.12 | 0
CZ12 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ12 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ12 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXGF | Existing | Fans | 545144.07 | 0
CZ12 | cDXGF | Existing | Pumps | 87.67 | 0
CZ12 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ12 | cDXGF | Existing | Humidification | 0 | 0
CZ12 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ12 | cDXGF | Existing | Water Systems | 0 | 401211.49
CZ12 | cDXGF | Existing | Refrigeration | 0 | 0
CZ12 | cDXGF | Existing | Generators | 0 | 0
CZ12 | cDXGF | Existing | Total End Uses | 2693345.38 | 873924.85
CZ13 | cDXGF | Existing | Heating | 0 | 202485.8
CZ13 | cDXGF | Existing | Cooling | 666381.8 | 0
CZ13 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ13 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ13 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXGF | Existing | Fans | 590828.05 | 0
CZ13 | cDXGF | Existing | Pumps | 84.19 | 0
CZ13 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ13 | cDXGF | Existing | Humidification | 0 | 0
CZ13 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ13 | cDXGF | Existing | Water Systems | 0 | 378887.03
CZ13 | cDXGF | Existing | Refrigeration | 0 | 0
CZ13 | cDXGF | Existing | Generators | 0 | 0
CZ13 | cDXGF | Existing | Total End Uses | 2907398.57 | 806228.6
CZ14 | cDXGF | Existing | Heating | 0 | 144312.25
CZ14 | cDXGF | Existing | Cooling | 821102.62 | 0
CZ14 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ14 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ14 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXGF | Existing | Fans | 651420.05 | 0
CZ14 | cDXGF | Existing | Pumps | 78.71 | 0
CZ14 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ14 | cDXGF | Existing | Humidification | 0 | 0
CZ14 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ14 | cDXGF | Existing | Water Systems | 0 | 359698.2
CZ14 | cDXGF | Existing | Refrigeration | 0 | 0
CZ14 | cDXGF | Existing | Generators | 0 | 0
CZ14 | cDXGF | Existing | Total End Uses | 3122705.9 | 728866.22
CZ15 | cDXGF | Existing | Heating | 0 | 77762.02
CZ15 | cDXGF | Existing | Cooling | 1129579.74 | 0
CZ15 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ15 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ15 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXGF | Existing | Fans | 659583.45 | 0
CZ15 | cDXGF | Existing | Pumps | 113.28 | 0
CZ15 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ15 | cDXGF | Existing | Humidification | 0 | 0
CZ15 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ15 | cDXGF | Existing | Water Systems | 0 | 319363.55
CZ15 | cDXGF | Existing | Refrigeration | 0 | 0
CZ15 | cDXGF | Existing | Generators | 0 | 0
CZ15 | cDXGF | Existing | Total End Uses | 3439380.99 | 621981.35
CZ16 | cDXGF | Existing | Heating | 0 | 433232.15
CZ16 | cDXGF | Existing | Cooling | 530549.15 | 0
CZ16 | cDXGF | Existing | Interior Lighting | 687070.6 | 0
CZ16 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXGF | Existing | Interior Equipment | 963033.93 | 224855.78
CZ16 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXGF | Existing | Fans | 646057.52 | 0
CZ16 | cDXGF | Existing | Pumps | 113.02 | 0
CZ16 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ16 | cDXGF | Existing | Humidification | 0 | 0
CZ16 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ16 | cDXGF | Existing | Water Systems | 0 | 424216.48
CZ16 | cDXGF | Existing | Refrigeration | 0 | 0
CZ16 | cDXGF | Existing | Generators | 0 | 0
CZ16 | cDXGF | Existing | Total End Uses | 2826824.21 | 1082304.41
CZ01 | cDXGF | New Construction | Heating | 0 | 305586.73
CZ01 | cDXGF | New Construction | Cooling | 46679.82 | 0
CZ01 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ01 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ01 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXGF | New Construction | Fans | 309913.98 | 0
CZ01 | cDXGF | New Construction | Pumps | 70.84 | 0
CZ01 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXGF | New Construction | Humidification | 0 | 0
CZ01 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXGF | New Construction | Water Systems | 0 | 469147.89
CZ01 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ01 | cDXGF | New Construction | Generators | 0 | 0
CZ01 | cDXGF | New Construction | Total End Uses | 1672368.44 | 999590.4
CZ02 | cDXGF | New Construction | Heating | 0 | 179680.67
CZ02 | cDXGF | New Construction | Cooling | 186599.57 | 0
CZ02 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ02 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ02 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXGF | New Construction | Fans | 344074.28 | 0
CZ02 | cDXGF | New Construction | Pumps | 110.47 | 0
CZ02 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXGF | New Construction | Humidification | 0 | 0
CZ02 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXGF | New Construction | Water Systems | 0 | 431130.67
CZ02 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ02 | cDXGF | New Construction | Generators | 0 | 0
CZ02 | cDXGF | New Construction | Total End Uses | 1846488.12 | 835667.12
CZ03 | cDXGF | New Construction | Heating | 0 | 124463.85
CZ03 | cDXGF | New Construction | Cooling | 128497.27 | 0
CZ03 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ03 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ03 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXGF | New Construction | Fans | 331924.32 | 0
CZ03 | cDXGF | New Construction | Pumps | 77.02 | 0
CZ03 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXGF | New Construction | Humidification | 0 | 0
CZ03 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXGF | New Construction | Water Systems | 0 | 429429.5
CZ03 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ03 | cDXGF | New Construction | Generators | 0 | 0
CZ03 | cDXGF | New Construction | Total End Uses | 1776202.4 | 778749.13
CZ04 | cDXGF | New Construction | Heating | 0 | 87355.12
CZ04 | cDXGF | New Construction | Cooling | 222038.45 | 0
CZ04 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ04 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ04 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXGF | New Construction | Fans | 350872.78 | 0
CZ04 | cDXGF | New Construction | Pumps | 96.95 | 0
CZ04 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXGF | New Construction | Humidification | 0 | 0
CZ04 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXGF | New Construction | Water Systems | 0 | 414713.48
CZ04 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ04 | cDXGF | New Construction | Generators | 0 | 0
CZ04 | cDXGF | New Construction | Total End Uses | 1888711.97 | 726924.38
CZ05 | cDXGF | New Construction | Heating | 0 | 126947.43
CZ05 | cDXGF | New Construction | Cooling | 162112.52 | 0
CZ05 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ05 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ05 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXGF | New Construction | Fans | 334908.14 | 0
CZ05 | cDXGF | New Construction | Pumps | 107.92 | 0
CZ05 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXGF | New Construction | Humidification | 0 | 0
CZ05 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXGF | New Construction | Water Systems | 0 | 429479.16
CZ05 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ05 | cDXGF | New Construction | Generators | 0 | 0
CZ05 | cDXGF | New Construction | Total End Uses | 1812832.37 | 781282.37
CZ06 | cDXGF | New Construction | Heating | 0 | 32566.54
CZ06 | cDXGF | New Construction | Cooling | 262048.55 | 0
CZ06 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ06 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ06 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXGF | New Construction | Fans | 353708.94 | 0
CZ06 | cDXGF | New Construction | Pumps | 130.93 | 0
CZ06 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXGF | New Construction | Humidification | 0 | 0
CZ06 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXGF | New Construction | Water Systems | 0 | 395628.2
CZ06 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ06 | cDXGF | New Construction | Generators | 0 | 0
CZ06 | cDXGF | New Construction | Total End Uses | 1931592.22 | 653050.53
CZ07 | cDXGF | New Construction | Heating | 0 | 28314.65
CZ07 | cDXGF | New Construction | Cooling | 272458.26 | 0
CZ07 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ07 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ07 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXGF | New Construction | Fans | 352418.78 | 0
CZ07 | cDXGF | New Construction | Pumps | 75.09 | 0
CZ07 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXGF | New Construction | Humidification | 0 | 0
CZ07 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXGF | New Construction | Water Systems | 0 | 390518.65
CZ07 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ07 | cDXGF | New Construction | Generators | 0 | 0
CZ07 | cDXGF | New Construction | Total End Uses | 1940655.92 | 643689.08
CZ08 | cDXGF | New Construction | Heating | 0 | 49401.35
CZ08 | cDXGF | New Construction | Cooling | 311824.2 | 0
CZ08 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ08 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ08 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXGF | New Construction | Fans | 370963.12 | 0
CZ08 | cDXGF | New Construction | Pumps | 104.8 | 0
CZ08 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXGF | New Construction | Humidification | 0 | 0
CZ08 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXGF | New Construction | Water Systems | 0 | 390005.49
CZ08 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ08 | cDXGF | New Construction | Generators | 0 | 0
CZ08 | cDXGF | New Construction | Total End Uses | 1998595.91 | 664262.62
CZ09 | cDXGF | New Construction | Heating | 0 | 37016.72
CZ09 | cDXGF | New Construction | Cooling | 334450.14 | 0
CZ09 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ09 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ09 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXGF | New Construction | Fans | 370365.41 | 0
CZ09 | cDXGF | New Construction | Pumps | 98.61 | 0
CZ09 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXGF | New Construction | Humidification | 0 | 0
CZ09 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXGF | New Construction | Water Systems | 0 | 384560.47
CZ09 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ09 | cDXGF | New Construction | Generators | 0 | 0
CZ09 | cDXGF | New Construction | Total End Uses | 2020617.96 | 646432.97
CZ10 | cDXGF | New Construction | Heating | 0 | 71210.44
CZ10 | cDXGF | New Construction | Cooling | 416221.67 | 0
CZ10 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ10 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ10 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXGF | New Construction | Fans | 399615.39 | 0
CZ10 | cDXGF | New Construction | Pumps | 104.38 | 0
CZ10 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXGF | New Construction | Humidification | 0 | 0
CZ10 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXGF | New Construction | Water Systems | 0 | 381519.95
CZ10 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ10 | cDXGF | New Construction | Generators | 0 | 0
CZ10 | cDXGF | New Construction | Total End Uses | 2131645.24 | 677586.17
CZ11 | cDXGF | New Construction | Heating | 0 | 194754.78
CZ11 | cDXGF | New Construction | Cooling | 426456.35 | 0
CZ11 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ11 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ11 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXGF | New Construction | Fans | 393822.77 | 0
CZ11 | cDXGF | New Construction | Pumps | 149.21 | 0
CZ11 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXGF | New Construction | Humidification | 0 | 0
CZ11 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXGF | New Construction | Water Systems | 0 | 389935.2
CZ11 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ11 | cDXGF | New Construction | Generators | 0 | 0
CZ11 | cDXGF | New Construction | Total End Uses | 2136132.13 | 809545.77
CZ12 | cDXGF | New Construction | Heating | 0 | 183132.44
CZ12 | cDXGF | New Construction | Cooling | 353354.07 | 0
CZ12 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ12 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ12 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXGF | New Construction | Fans | 373666.63 | 0
CZ12 | cDXGF | New Construction | Pumps | 123.63 | 0
CZ12 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXGF | New Construction | Humidification | 0 | 0
CZ12 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXGF | New Construction | Water Systems | 0 | 400979.06
CZ12 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ12 | cDXGF | New Construction | Generators | 0 | 0
CZ12 | cDXGF | New Construction | Total End Uses | 2042848.13 | 808967.28
CZ13 | cDXGF | New Construction | Heating | 0 | 154985.65
CZ13 | cDXGF | New Construction | Cooling | 474050.41 | 0
CZ13 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ13 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ13 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXGF | New Construction | Fans | 400943.75 | 0
CZ13 | cDXGF | New Construction | Pumps | 149.18 | 0
CZ13 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXGF | New Construction | Humidification | 0 | 0
CZ13 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXGF | New Construction | Water Systems | 0 | 378691.73
CZ13 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ13 | cDXGF | New Construction | Generators | 0 | 0
CZ13 | cDXGF | New Construction | Total End Uses | 2190847.13 | 758533.16
CZ14 | cDXGF | New Construction | Heating | 0 | 135682.43
CZ14 | cDXGF | New Construction | Cooling | 603029.65 | 0
CZ14 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ14 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ14 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXGF | New Construction | Fans | 437871.74 | 0
CZ14 | cDXGF | New Construction | Pumps | 178.53 | 0
CZ14 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXGF | New Construction | Humidification | 0 | 0
CZ14 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXGF | New Construction | Water Systems | 0 | 359344.14
CZ14 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ14 | cDXGF | New Construction | Generators | 0 | 0
CZ14 | cDXGF | New Construction | Total End Uses | 2356783.72 | 719882.35
CZ15 | cDXGF | New Construction | Heating | 0 | 89749.38
CZ15 | cDXGF | New Construction | Cooling | 837157.11 | 0
CZ15 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ15 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ15 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXGF | New Construction | Fans | 432259.1 | 0
CZ15 | cDXGF | New Construction | Pumps | 269.25 | 0
CZ15 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXGF | New Construction | Humidification | 0 | 0
CZ15 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXGF | New Construction | Water Systems | 0 | 319111.69
CZ15 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ15 | cDXGF | New Construction | Generators | 0 | 0
CZ15 | cDXGF | New Construction | Total End Uses | 2585389.25 | 633716.85
CZ16 | cDXGF | New Construction | Heating | 0 | 345013.92
CZ16 | cDXGF | New Construction | Cooling | 386665.65 | 0
CZ16 | cDXGF | New Construction | Interior Lighting | 352669.87 | 0
CZ16 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXGF | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ16 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXGF | New Construction | Fans | 446545.82 | 0
CZ16 | cDXGF | New Construction | Pumps | 147.63 | 0
CZ16 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXGF | New Construction | Humidification | 0 | 0
CZ16 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXGF | New Construction | Water Systems | 0 | 423978.93
CZ16 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ16 | cDXGF | New Construction | Generators | 0 | 0
CZ16 | cDXGF | New Construction | Total End Uses | 2149062.89 | 993848.63
CZ01 | cDXHP | Existing | Heating | 33124.14 | 243296.43
CZ01 | cDXHP | Existing | Cooling | 67482.22 | 0
CZ01 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ01 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ01 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXHP | Existing | Fans | 418647.07 | 0
CZ01 | cDXHP | Existing | Pumps | 93.47 | 0
CZ01 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ01 | cDXHP | Existing | Humidification | 0 | 0
CZ01 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ01 | cDXHP | Existing | Water Systems | 0 | 469374.71
CZ01 | cDXHP | Existing | Refrigeration | 0 | 0
CZ01 | cDXHP | Existing | Generators | 0 | 0
CZ01 | cDXHP | Existing | Total End Uses | 2169451.42 | 937526.92
CZ02 | cDXHP | Existing | Heating | 23483 | 171734.88
CZ02 | cDXHP | Existing | Cooling | 266289.83 | 0
CZ02 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ02 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ02 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXHP | Existing | Fans | 498811.72 | 0
CZ02 | cDXHP | Existing | Pumps | 78.9 | 0
CZ02 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ02 | cDXHP | Existing | Humidification | 0 | 0
CZ02 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ02 | cDXHP | Existing | Water Systems | 0 | 431325.1
CZ02 | cDXHP | Existing | Refrigeration | 0 | 0
CZ02 | cDXHP | Existing | Generators | 0 | 0
CZ02 | cDXHP | Existing | Total End Uses | 2438767.98 | 827915.76
CZ03 | cDXHP | Existing | Heating | 11699.28 | 94635.37
CZ03 | cDXHP | Existing | Cooling | 204047.48 | 0
CZ03 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ03 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ03 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXHP | Existing | Fans | 478779.55 | 0
CZ03 | cDXHP | Existing | Pumps | 79.4 | 0
CZ03 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ03 | cDXHP | Existing | Humidification | 0 | 0
CZ03 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ03 | cDXHP | Existing | Water Systems | 0 | 429641.82
CZ03 | cDXHP | Existing | Refrigeration | 0 | 0
CZ03 | cDXHP | Existing | Generators | 0 | 0
CZ03 | cDXHP | Existing | Total End Uses | 2344710.22 | 749132.97
CZ04 | cDXHP | Existing | Heating | 10252.83 | 74473.38
CZ04 | cDXHP | Existing | Cooling | 315827.82 | 0
CZ04 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ04 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ04 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXHP | Existing | Fans | 513126.99 | 0
CZ04 | cDXHP | Existing | Pumps | 48.9 | 0
CZ04 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ04 | cDXHP | Existing | Humidification | 0 | 0
CZ04 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ04 | cDXHP | Existing | Water Systems | 0 | 414901.04
CZ04 | cDXHP | Existing | Refrigeration | 0 | 0
CZ04 | cDXHP | Existing | Generators | 0 | 0
CZ04 | cDXHP | Existing | Total End Uses | 2489361.07 | 714230.2
CZ05 | cDXHP | Existing | Heating | 11948.25 | 85326.84
CZ05 | cDXHP | Existing | Cooling | 257149.07 | 0
CZ05 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ05 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ05 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXHP | Existing | Fans | 485668.03 | 0
CZ05 | cDXHP | Existing | Pumps | 117.82 | 0
CZ05 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ05 | cDXHP | Existing | Humidification | 0 | 0
CZ05 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ05 | cDXHP | Existing | Water Systems | 0 | 429676
CZ05 | cDXHP | Existing | Refrigeration | 0 | 0
CZ05 | cDXHP | Existing | Generators | 0 | 0
CZ05 | cDXHP | Existing | Total End Uses | 2404987.69 | 739858.63
CZ06 | cDXHP | Existing | Heating | 1485.56 | 39952.49
CZ06 | cDXHP | Existing | Cooling | 404821.76 | 0
CZ06 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ06 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ06 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXHP | Existing | Fans | 517746.01 | 0
CZ06 | cDXHP | Existing | Pumps | 133.83 | 0
CZ06 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ06 | cDXHP | Existing | Humidification | 0 | 0
CZ06 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ06 | cDXHP | Existing | Water Systems | 0 | 395842.91
CZ06 | cDXHP | Existing | Refrigeration | 0 | 0
CZ06 | cDXHP | Existing | Generators | 0 | 0
CZ06 | cDXHP | Existing | Total End Uses | 2574291.68 | 660651.18
CZ07 | cDXHP | Existing | Heating | 1262.8 | 22347.37
CZ07 | cDXHP | Existing | Cooling | 407626.86 | 0
CZ07 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ07 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ07 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXHP | Existing | Fans | 505686.05 | 0
CZ07 | cDXHP | Existing | Pumps | 75.76 | 0
CZ07 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ07 | cDXHP | Existing | Humidification | 0 | 0
CZ07 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ07 | cDXHP | Existing | Water Systems | 0 | 390807.03
CZ07 | cDXHP | Existing | Refrigeration | 0 | 0
CZ07 | cDXHP | Existing | Generators | 0 | 0
CZ07 | cDXHP | Existing | Total End Uses | 2564756 | 638010.18
CZ08 | cDXHP | Existing | Heating | 2690.69 | 41834.21
CZ08 | cDXHP | Existing | Cooling | 444117.71 | 0
CZ08 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ08 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ08 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXHP | Existing | Fans | 537504.08 | 0
CZ08 | cDXHP | Existing | Pumps | 61.18 | 0
CZ08 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ08 | cDXHP | Existing | Humidification | 0 | 0
CZ08 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ08 | cDXHP | Existing | Water Systems | 0 | 390234.52
CZ08 | cDXHP | Existing | Refrigeration | 0 | 0
CZ08 | cDXHP | Existing | Generators | 0 | 0
CZ08 | cDXHP | Existing | Total End Uses | 2634478.18 | 656924.51
CZ09 | cDXHP | Existing | Heating | 1899.99 | 44802.26
CZ09 | cDXHP | Existing | Cooling | 503461.16 | 0
CZ09 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ09 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ09 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXHP | Existing | Fans | 563478.74 | 0
CZ09 | cDXHP | Existing | Pumps | 66.72 | 0
CZ09 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ09 | cDXHP | Existing | Humidification | 0 | 0
CZ09 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ09 | cDXHP | Existing | Water Systems | 0 | 384843
CZ09 | cDXHP | Existing | Refrigeration | 0 | 0
CZ09 | cDXHP | Existing | Generators | 0 | 0
CZ09 | cDXHP | Existing | Total End Uses | 2719011.13 | 654501.03
CZ10 | cDXHP | Existing | Heating | 7810.88 | 54974.05
CZ10 | cDXHP | Existing | Cooling | 570637.46 | 0
CZ10 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ10 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ10 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXHP | Existing | Fans | 569851.9 | 0
CZ10 | cDXHP | Existing | Pumps | 69.93 | 0
CZ10 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ10 | cDXHP | Existing | Humidification | 0 | 0
CZ10 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ10 | cDXHP | Existing | Water Systems | 0 | 381729.95
CZ10 | cDXHP | Existing | Refrigeration | 0 | 0
CZ10 | cDXHP | Existing | Generators | 0 | 0
CZ10 | cDXHP | Existing | Total End Uses | 2798474.68 | 661559.78
CZ11 | cDXHP | Existing | Heating | 21230.24 | 217676.82
CZ11 | cDXHP | Existing | Cooling | 603930.99 | 0
CZ11 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ11 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ11 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXHP | Existing | Fans | 590666.2 | 0
CZ11 | cDXHP | Existing | Pumps | 100.59 | 0
CZ11 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ11 | cDXHP | Existing | Humidification | 0 | 0
CZ11 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ11 | cDXHP | Existing | Water Systems | 0 | 390230.49
CZ11 | cDXHP | Existing | Refrigeration | 0 | 0
CZ11 | cDXHP | Existing | Generators | 0 | 0
CZ11 | cDXHP | Existing | Total End Uses | 2866032.54 | 832763.09
CZ12 | cDXHP | Existing | Heating | 21419.03 | 172553.47
CZ12 | cDXHP | Existing | Cooling | 497875.05 | 0
CZ12 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ12 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ12 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXHP | Existing | Fans | 545209.12 | 0
CZ12 | cDXHP | Existing | Pumps | 87.58 | 0
CZ12 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ12 | cDXHP | Existing | Humidification | 0 | 0
CZ12 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ12 | cDXHP | Existing | Water Systems | 0 | 401209.75
CZ12 | cDXHP | Existing | Refrigeration | 0 | 0
CZ12 | cDXHP | Existing | Generators | 0 | 0
CZ12 | cDXHP | Existing | Total End Uses | 2714695.3 | 798619.01
CZ13 | cDXHP | Existing | Heating | 15942.57 | 144587.99
CZ13 | cDXHP | Existing | Cooling | 666548.75 | 0
CZ13 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ13 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ13 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXHP | Existing | Fans | 590698.13 | 0
CZ13 | cDXHP | Existing | Pumps | 84.43 | 0
CZ13 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ13 | cDXHP | Existing | Humidification | 0 | 0
CZ13 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ13 | cDXHP | Existing | Water Systems | 0 | 378882.8
CZ13 | cDXHP | Existing | Refrigeration | 0 | 0
CZ13 | cDXHP | Existing | Generators | 0 | 0
CZ13 | cDXHP | Existing | Total End Uses | 2923378.4 | 748326.56
CZ14 | cDXHP | Existing | Heating | 10190.93 | 108613.54
CZ14 | cDXHP | Existing | Cooling | 821057.83 | 0
CZ14 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ14 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ14 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXHP | Existing | Fans | 651493.74 | 0
CZ14 | cDXHP | Existing | Pumps | 78.31 | 0
CZ14 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ14 | cDXHP | Existing | Humidification | 0 | 0
CZ14 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ14 | cDXHP | Existing | Water Systems | 0 | 359695.18
CZ14 | cDXHP | Existing | Refrigeration | 0 | 0
CZ14 | cDXHP | Existing | Generators | 0 | 0
CZ14 | cDXHP | Existing | Total End Uses | 3132925.34 | 693164.5
CZ15 | cDXHP | Existing | Heating | 2840.39 | 65497.51
CZ15 | cDXHP | Existing | Cooling | 1128863.21 | 0
CZ15 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ15 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ15 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXHP | Existing | Fans | 659614.16 | 0
CZ15 | cDXHP | Existing | Pumps | 111.61 | 0
CZ15 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ15 | cDXHP | Existing | Humidification | 0 | 0
CZ15 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ15 | cDXHP | Existing | Water Systems | 0 | 319381.61
CZ15 | cDXHP | Existing | Refrigeration | 0 | 0
CZ15 | cDXHP | Existing | Generators | 0 | 0
CZ15 | cDXHP | Existing | Total End Uses | 3441533.89 | 609734.89
CZ16 | cDXHP | Existing | Heating | 46115 | 304324.55
CZ16 | cDXHP | Existing | Cooling | 530635.16 | 0
CZ16 | cDXHP | Existing | Interior Lighting | 687070.6 | 0
CZ16 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXHP | Existing | Interior Equipment | 963033.93 | 224855.78
CZ16 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXHP | Existing | Fans | 646033.38 | 0
CZ16 | cDXHP | Existing | Pumps | 113.33 | 0
CZ16 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ16 | cDXHP | Existing | Humidification | 0 | 0
CZ16 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ16 | cDXHP | Existing | Water Systems | 0 | 424217.9
CZ16 | cDXHP | Existing | Refrigeration | 0 | 0
CZ16 | cDXHP | Existing | Generators | 0 | 0
CZ16 | cDXHP | Existing | Total End Uses | 2873001.38 | 953398.23
CZ01 | cDXHP | New Construction | Heating | 42237.21 | 133145.33
CZ01 | cDXHP | New Construction | Cooling | 46331.34 | 0
CZ01 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ01 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ01 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXHP | New Construction | Fans | 309947.52 | 0
CZ01 | cDXHP | New Construction | Pumps | 71.05 | 0
CZ01 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXHP | New Construction | Humidification | 0 | 0
CZ01 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXHP | New Construction | Water Systems | 0 | 469136.72
CZ01 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ01 | cDXHP | New Construction | Generators | 0 | 0
CZ01 | cDXHP | New Construction | Total End Uses | 1714290.92 | 827137.82
CZ02 | cDXHP | New Construction | Heating | 27519.47 | 79471.6
CZ02 | cDXHP | New Construction | Cooling | 186086.41 | 0
CZ02 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ02 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ02 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXHP | New Construction | Fans | 344131.59 | 0
CZ02 | cDXHP | New Construction | Pumps | 110.57 | 0
CZ02 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXHP | New Construction | Humidification | 0 | 0
CZ02 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXHP | New Construction | Water Systems | 0 | 431091.78
CZ02 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ02 | cDXHP | New Construction | Generators | 0 | 0
CZ02 | cDXHP | New Construction | Total End Uses | 1873551.85 | 735419.16
CZ03 | cDXHP | New Construction | Heating | 17042.74 | 55808.7
CZ03 | cDXHP | New Construction | Cooling | 127915.03 | 0
CZ03 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ03 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ03 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXHP | New Construction | Fans | 331920.81 | 0
CZ03 | cDXHP | New Construction | Pumps | 76.78 | 0
CZ03 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXHP | New Construction | Humidification | 0 | 0
CZ03 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXHP | New Construction | Water Systems | 0 | 429405.49
CZ03 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ03 | cDXHP | New Construction | Generators | 0 | 0
CZ03 | cDXHP | New Construction | Total End Uses | 1792659.16 | 710069.98
CZ04 | cDXHP | New Construction | Heating | 13101.39 | 35073.26
CZ04 | cDXHP | New Construction | Cooling | 221794.08 | 0
CZ04 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ04 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ04 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXHP | New Construction | Fans | 351003.84 | 0
CZ04 | cDXHP | New Construction | Pumps | 97.64 | 0
CZ04 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXHP | New Construction | Humidification | 0 | 0
CZ04 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXHP | New Construction | Water Systems | 0 | 414707.07
CZ04 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ04 | cDXHP | New Construction | Generators | 0 | 0
CZ04 | cDXHP | New Construction | Total End Uses | 1901700.74 | 674636.11
CZ05 | cDXHP | New Construction | Heating | 18206.84 | 55995.13
CZ05 | cDXHP | New Construction | Cooling | 161698.21 | 0
CZ05 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ05 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ05 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXHP | New Construction | Fans | 334966.56 | 0
CZ05 | cDXHP | New Construction | Pumps | 108.51 | 0
CZ05 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXHP | New Construction | Humidification | 0 | 0
CZ05 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXHP | New Construction | Water Systems | 0 | 429482.17
CZ05 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ05 | cDXHP | New Construction | Generators | 0 | 0
CZ05 | cDXHP | New Construction | Total End Uses | 1830683.92 | 710333.07
CZ06 | cDXHP | New Construction | Heating | 3236.73 | 18870.99
CZ06 | cDXHP | New Construction | Cooling | 258954.37 | 0
CZ06 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ06 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ06 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXHP | New Construction | Fans | 353845.17 | 0
CZ06 | cDXHP | New Construction | Pumps | 131.44 | 0
CZ06 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXHP | New Construction | Humidification | 0 | 0
CZ06 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXHP | New Construction | Water Systems | 0 | 395629
CZ06 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ06 | cDXHP | New Construction | Generators | 0 | 0
CZ06 | cDXHP | New Construction | Total End Uses | 1931871.51 | 639355.78
CZ07 | cDXHP | New Construction | Heating | 2894.87 | 15817.68
CZ07 | cDXHP | New Construction | Cooling | 270465.95 | 0
CZ07 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ07 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ07 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXHP | New Construction | Fans | 352324.98 | 0
CZ07 | cDXHP | New Construction | Pumps | 74.47 | 0
CZ07 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXHP | New Construction | Humidification | 0 | 0
CZ07 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXHP | New Construction | Water Systems | 0 | 390526.89
CZ07 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ07 | cDXHP | New Construction | Generators | 0 | 0
CZ07 | cDXHP | New Construction | Total End Uses | 1941464.07 | 631200.34
CZ08 | cDXHP | New Construction | Heating | 4989.43 | 28560.86
CZ08 | cDXHP | New Construction | Cooling | 310821.66 | 0
CZ08 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ08 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ08 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXHP | New Construction | Fans | 371043.66 | 0
CZ08 | cDXHP | New Construction | Pumps | 104.02 | 0
CZ08 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXHP | New Construction | Humidification | 0 | 0
CZ08 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXHP | New Construction | Water Systems | 0 | 390031.99
CZ08 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ08 | cDXHP | New Construction | Generators | 0 | 0
CZ08 | cDXHP | New Construction | Total End Uses | 2002662.57 | 643448.63
CZ09 | cDXHP | New Construction | Heating | 3368.3 | 22855.96
CZ09 | cDXHP | New Construction | Cooling | 333389.76 | 0
CZ09 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ09 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ09 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXHP | New Construction | Fans | 370395.46 | 0
CZ09 | cDXHP | New Construction | Pumps | 97.08 | 0
CZ09 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXHP | New Construction | Humidification | 0 | 0
CZ09 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXHP | New Construction | Water Systems | 0 | 384581.12
CZ09 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ09 | cDXHP | New Construction | Generators | 0 | 0
CZ09 | cDXHP | New Construction | Total End Uses | 2022954.4 | 632292.86
CZ10 | cDXHP | New Construction | Heating | 10172.84 | 33838.06
CZ10 | cDXHP | New Construction | Cooling | 415951.06 | 0
CZ10 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ10 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ10 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXHP | New Construction | Fans | 399755.05 | 0
CZ10 | cDXHP | New Construction | Pumps | 104.03 | 0
CZ10 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXHP | New Construction | Humidification | 0 | 0
CZ10 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXHP | New Construction | Water Systems | 0 | 381514.6
CZ10 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ10 | cDXHP | New Construction | Generators | 0 | 0
CZ10 | cDXHP | New Construction | Total End Uses | 2141686.78 | 640208.43
CZ11 | cDXHP | New Construction | Heating | 24531.71 | 103891.32
CZ11 | cDXHP | New Construction | Cooling | 426086.59 | 0
CZ11 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ11 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ11 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXHP | New Construction | Fans | 393778.03 | 0
CZ11 | cDXHP | New Construction | Pumps | 148.88 | 0
CZ11 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXHP | New Construction | Humidification | 0 | 0
CZ11 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXHP | New Construction | Water Systems | 0 | 389974.19
CZ11 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ11 | cDXHP | New Construction | Generators | 0 | 0
CZ11 | cDXHP | New Construction | Total End Uses | 2160249 | 718721.28
CZ12 | cDXHP | New Construction | Heating | 25330.19 | 90604.24
CZ12 | cDXHP | New Construction | Cooling | 353281.3 | 0
CZ12 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ12 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ12 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXHP | New Construction | Fans | 373668.51 | 0
CZ12 | cDXHP | New Construction | Pumps | 126.34 | 0
CZ12 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXHP | New Construction | Humidification | 0 | 0
CZ12 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXHP | New Construction | Water Systems | 0 | 400951.53
CZ12 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ12 | cDXHP | New Construction | Generators | 0 | 0
CZ12 | cDXHP | New Construction | Total End Uses | 2068110.14 | 716411.55
CZ13 | cDXHP | New Construction | Heating | 19757.2 | 79531.09
CZ13 | cDXHP | New Construction | Cooling | 473605.8 | 0
CZ13 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ13 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ13 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXHP | New Construction | Fans | 400709.21 | 0
CZ13 | cDXHP | New Construction | Pumps | 147.96 | 0
CZ13 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXHP | New Construction | Humidification | 0 | 0
CZ13 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXHP | New Construction | Water Systems | 0 | 378730.43
CZ13 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ13 | cDXHP | New Construction | Generators | 0 | 0
CZ13 | cDXHP | New Construction | Total End Uses | 2209923.97 | 683117.3
CZ14 | cDXHP | New Construction | Heating | 13441.48 | 86325.41
CZ14 | cDXHP | New Construction | Cooling | 603366.98 | 0
CZ14 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ14 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ14 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXHP | New Construction | Fans | 437822.42 | 0
CZ14 | cDXHP | New Construction | Pumps | 179.04 | 0
CZ14 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXHP | New Construction | Humidification | 0 | 0
CZ14 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXHP | New Construction | Water Systems | 0 | 359403.05
CZ14 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ14 | cDXHP | New Construction | Generators | 0 | 0
CZ14 | cDXHP | New Construction | Total End Uses | 2370513.71 | 670584.24
CZ15 | cDXHP | New Construction | Heating | 4368.72 | 72547.3
CZ15 | cDXHP | New Construction | Cooling | 837064.24 | 0
CZ15 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ15 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ15 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXHP | New Construction | Fans | 432254.64 | 0
CZ15 | cDXHP | New Construction | Pumps | 267.76 | 0
CZ15 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXHP | New Construction | Humidification | 0 | 0
CZ15 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXHP | New Construction | Water Systems | 0 | 319087.29
CZ15 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ15 | cDXHP | New Construction | Generators | 0 | 0
CZ15 | cDXHP | New Construction | Total End Uses | 2589659.16 | 616490.37
CZ16 | cDXHP | New Construction | Heating | 52702.67 | 188762.55
CZ16 | cDXHP | New Construction | Cooling | 385955.26 | 0
CZ16 | cDXHP | New Construction | Interior Lighting | 352669.87 | 0
CZ16 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXHP | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ16 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXHP | New Construction | Fans | 446420.32 | 0
CZ16 | cDXHP | New Construction | Pumps | 147.33 | 0
CZ16 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXHP | New Construction | Humidification | 0 | 0
CZ16 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXHP | New Construction | Water Systems | 0 | 423991.21
CZ16 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ16 | cDXHP | New Construction | Generators | 0 | 0
CZ16 | cDXHP | New Construction | Total End Uses | 2200929.38 | 837609.54
CZ01 | cDXOH | Existing | Heating | 0 | 269182.92
CZ01 | cDXOH | Existing | Cooling | 67221.89 | 0
CZ01 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ01 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ01 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXOH | Existing | Fans | 418948.33 | 0
CZ01 | cDXOH | Existing | Pumps | 99.25 | 0
CZ01 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ01 | cDXOH | Existing | Humidification | 0 | 0
CZ01 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ01 | cDXOH | Existing | Water Systems | 0 | 469377.78
CZ01 | cDXOH | Existing | Refrigeration | 0 | 0
CZ01 | cDXOH | Existing | Generators | 0 | 0
CZ01 | cDXOH | Existing | Total End Uses | 2136373.99 | 963416.48
CZ02 | cDXOH | Existing | Heating | 0 | 187495.27
CZ02 | cDXOH | Existing | Cooling | 266245.33 | 0
CZ02 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ02 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ02 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXOH | Existing | Fans | 499016.24 | 0
CZ02 | cDXOH | Existing | Pumps | 81.85 | 0
CZ02 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ02 | cDXOH | Existing | Humidification | 0 | 0
CZ02 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ02 | cDXOH | Existing | Water Systems | 0 | 431329.66
CZ02 | cDXOH | Existing | Refrigeration | 0 | 0
CZ02 | cDXOH | Existing | Generators | 0 | 0
CZ02 | cDXOH | Existing | Total End Uses | 2415447.94 | 843680.7
CZ03 | cDXOH | Existing | Heating | 0 | 103648.23
CZ03 | cDXOH | Existing | Cooling | 204525.09 | 0
CZ03 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ03 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ03 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXOH | Existing | Fans | 478912.74 | 0
CZ03 | cDXOH | Existing | Pumps | 81.14 | 0
CZ03 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ03 | cDXOH | Existing | Humidification | 0 | 0
CZ03 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ03 | cDXOH | Existing | Water Systems | 0 | 429656.42
CZ03 | cDXOH | Existing | Refrigeration | 0 | 0
CZ03 | cDXOH | Existing | Generators | 0 | 0
CZ03 | cDXOH | Existing | Total End Uses | 2333623.49 | 758160.43
CZ04 | cDXOH | Existing | Heating | 0 | 81085.64
CZ04 | cDXOH | Existing | Cooling | 315588.78 | 0
CZ04 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ04 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ04 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXOH | Existing | Fans | 513130.05 | 0
CZ04 | cDXOH | Existing | Pumps | 49.75 | 0
CZ04 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ04 | cDXOH | Existing | Humidification | 0 | 0
CZ04 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ04 | cDXOH | Existing | Water Systems | 0 | 414905.14
CZ04 | cDXOH | Existing | Refrigeration | 0 | 0
CZ04 | cDXOH | Existing | Generators | 0 | 0
CZ04 | cDXOH | Existing | Total End Uses | 2478873.11 | 720846.56
CZ05 | cDXOH | Existing | Heating | 0 | 90654.41
CZ05 | cDXOH | Existing | Cooling | 257239.45 | 0
CZ05 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ05 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ05 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXOH | Existing | Fans | 485374.52 | 0
CZ05 | cDXOH | Existing | Pumps | 119.1 | 0
CZ05 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ05 | cDXOH | Existing | Humidification | 0 | 0
CZ05 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ05 | cDXOH | Existing | Water Systems | 0 | 429680.15
CZ05 | cDXOH | Existing | Refrigeration | 0 | 0
CZ05 | cDXOH | Existing | Generators | 0 | 0
CZ05 | cDXOH | Existing | Total End Uses | 2392837.59 | 745190.33
CZ06 | cDXOH | Existing | Heating | 0 | 40338.08
CZ06 | cDXOH | Existing | Cooling | 408234.26 | 0
CZ06 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ06 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ06 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXOH | Existing | Fans | 517747.7 | 0
CZ06 | cDXOH | Existing | Pumps | 134.6 | 0
CZ06 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ06 | cDXOH | Existing | Humidification | 0 | 0
CZ06 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ06 | cDXOH | Existing | Water Systems | 0 | 395856.7
CZ06 | cDXOH | Existing | Refrigeration | 0 | 0
CZ06 | cDXOH | Existing | Generators | 0 | 0
CZ06 | cDXOH | Existing | Total End Uses | 2576221.08 | 661050.56
CZ07 | cDXOH | Existing | Heating | 0 | 22453.45
CZ07 | cDXOH | Existing | Cooling | 409302.36 | 0
CZ07 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ07 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ07 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXOH | Existing | Fans | 505332.35 | 0
CZ07 | cDXOH | Existing | Pumps | 75.2 | 0
CZ07 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ07 | cDXOH | Existing | Humidification | 0 | 0
CZ07 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ07 | cDXOH | Existing | Water Systems | 0 | 390797.12
CZ07 | cDXOH | Existing | Refrigeration | 0 | 0
CZ07 | cDXOH | Existing | Generators | 0 | 0
CZ07 | cDXOH | Existing | Total End Uses | 2564814.43 | 638106.35
CZ08 | cDXOH | Existing | Heating | 0 | 42710.29
CZ08 | cDXOH | Existing | Cooling | 444896.7 | 0
CZ08 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ08 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ08 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXOH | Existing | Fans | 537404.17 | 0
CZ08 | cDXOH | Existing | Pumps | 61.75 | 0
CZ08 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ08 | cDXOH | Existing | Humidification | 0 | 0
CZ08 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ08 | cDXOH | Existing | Water Systems | 0 | 390221.74
CZ08 | cDXOH | Existing | Refrigeration | 0 | 0
CZ08 | cDXOH | Existing | Generators | 0 | 0
CZ08 | cDXOH | Existing | Total End Uses | 2632467.14 | 657787.8
CZ09 | cDXOH | Existing | Heating | 0 | 45063.27
CZ09 | cDXOH | Existing | Cooling | 504206.79 | 0
CZ09 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ09 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ09 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXOH | Existing | Fans | 563467.51 | 0
CZ09 | cDXOH | Existing | Pumps | 66.68 | 0
CZ09 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ09 | cDXOH | Existing | Humidification | 0 | 0
CZ09 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ09 | cDXOH | Existing | Water Systems | 0 | 384836.27
CZ09 | cDXOH | Existing | Refrigeration | 0 | 0
CZ09 | cDXOH | Existing | Generators | 0 | 0
CZ09 | cDXOH | Existing | Total End Uses | 2717845.5 | 654755.32
CZ10 | cDXOH | Existing | Heating | 0 | 58258.55
CZ10 | cDXOH | Existing | Cooling | 570460.99 | 0
CZ10 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ10 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ10 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXOH | Existing | Fans | 569690.76 | 0
CZ10 | cDXOH | Existing | Pumps | 70.78 | 0
CZ10 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ10 | cDXOH | Existing | Humidification | 0 | 0
CZ10 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ10 | cDXOH | Existing | Water Systems | 0 | 381742.21
CZ10 | cDXOH | Existing | Refrigeration | 0 | 0
CZ10 | cDXOH | Existing | Generators | 0 | 0
CZ10 | cDXOH | Existing | Total End Uses | 2790327.05 | 664856.54
CZ11 | cDXOH | Existing | Heating | 0 | 233054.39
CZ11 | cDXOH | Existing | Cooling | 603320.98 | 0
CZ11 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ11 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ11 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXOH | Existing | Fans | 590878.14 | 0
CZ11 | cDXOH | Existing | Pumps | 103.79 | 0
CZ11 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ11 | cDXOH | Existing | Humidification | 0 | 0
CZ11 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ11 | cDXOH | Existing | Water Systems | 0 | 390232.75
CZ11 | cDXOH | Existing | Refrigeration | 0 | 0
CZ11 | cDXOH | Existing | Generators | 0 | 0
CZ11 | cDXOH | Existing | Total End Uses | 2844407.44 | 848142.92
CZ12 | cDXOH | Existing | Heating | 0 | 188096.99
CZ12 | cDXOH | Existing | Cooling | 497405.27 | 0
CZ12 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ12 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ12 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXOH | Existing | Fans | 545385.2 | 0
CZ12 | cDXOH | Existing | Pumps | 91 | 0
CZ12 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ12 | cDXOH | Existing | Humidification | 0 | 0
CZ12 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ12 | cDXOH | Existing | Water Systems | 0 | 401213.42
CZ12 | cDXOH | Existing | Refrigeration | 0 | 0
CZ12 | cDXOH | Existing | Generators | 0 | 0
CZ12 | cDXOH | Existing | Total End Uses | 2692986 | 814166.19
CZ13 | cDXOH | Existing | Heating | 0 | 159312.28
CZ13 | cDXOH | Existing | Cooling | 666225.84 | 0
CZ13 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ13 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ13 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXOH | Existing | Fans | 591250.16 | 0
CZ13 | cDXOH | Existing | Pumps | 87.25 | 0
CZ13 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ13 | cDXOH | Existing | Humidification | 0 | 0
CZ13 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ13 | cDXOH | Existing | Water Systems | 0 | 378891.69
CZ13 | cDXOH | Existing | Refrigeration | 0 | 0
CZ13 | cDXOH | Existing | Generators | 0 | 0
CZ13 | cDXOH | Existing | Total End Uses | 2907667.78 | 763059.74
CZ14 | cDXOH | Existing | Heating | 0 | 113880.06
CZ14 | cDXOH | Existing | Cooling | 820510.87 | 0
CZ14 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ14 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ14 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXOH | Existing | Fans | 651315.79 | 0
CZ14 | cDXOH | Existing | Pumps | 79.92 | 0
CZ14 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ14 | cDXOH | Existing | Humidification | 0 | 0
CZ14 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ14 | cDXOH | Existing | Water Systems | 0 | 359701.01
CZ14 | cDXOH | Existing | Refrigeration | 0 | 0
CZ14 | cDXOH | Existing | Generators | 0 | 0
CZ14 | cDXOH | Existing | Total End Uses | 3122011.1 | 698436.85
CZ15 | cDXOH | Existing | Heating | 0 | 66578.85
CZ15 | cDXOH | Existing | Cooling | 1128885.28 | 0
CZ15 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ15 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ15 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXOH | Existing | Fans | 659333.98 | 0
CZ15 | cDXOH | Existing | Pumps | 112.14 | 0
CZ15 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ15 | cDXOH | Existing | Humidification | 0 | 0
CZ15 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ15 | cDXOH | Existing | Water Systems | 0 | 319324.28
CZ15 | cDXOH | Existing | Refrigeration | 0 | 0
CZ15 | cDXOH | Existing | Generators | 0 | 0
CZ15 | cDXOH | Existing | Total End Uses | 3438435.92 | 610758.91
CZ16 | cDXOH | Existing | Heating | 0 | 326887.38
CZ16 | cDXOH | Existing | Cooling | 529538.53 | 0
CZ16 | cDXOH | Existing | Interior Lighting | 687070.6 | 0
CZ16 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXOH | Existing | Interior Equipment | 963033.93 | 224855.78
CZ16 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXOH | Existing | Fans | 646493.65 | 0
CZ16 | cDXOH | Existing | Pumps | 120.03 | 0
CZ16 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ16 | cDXOH | Existing | Humidification | 0 | 0
CZ16 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ16 | cDXOH | Existing | Water Systems | 0 | 424215.76
CZ16 | cDXOH | Existing | Refrigeration | 0 | 0
CZ16 | cDXOH | Existing | Generators | 0 | 0
CZ16 | cDXOH | Existing | Total End Uses | 2826256.73 | 975958.93
CZ01 | cDXOH | New Construction | Heating | 0 | 169191.41
CZ01 | cDXOH | New Construction | Cooling | 45304.1 | 0
CZ01 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ01 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ01 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXOH | New Construction | Fans | 311162.5 | 0
CZ01 | cDXOH | New Construction | Pumps | 78.02 | 0
CZ01 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXOH | New Construction | Humidification | 0 | 0
CZ01 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXOH | New Construction | Water Systems | 0 | 469165.12
CZ01 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ01 | cDXOH | New Construction | Generators | 0 | 0
CZ01 | cDXOH | New Construction | Total End Uses | 1672248.41 | 863212.32
CZ02 | cDXOH | New Construction | Heating | 0 | 99209.28
CZ02 | cDXOH | New Construction | Cooling | 185053.85 | 0
CZ02 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ02 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ02 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXOH | New Construction | Fans | 344261.44 | 0
CZ02 | cDXOH | New Construction | Pumps | 118.25 | 0
CZ02 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXOH | New Construction | Humidification | 0 | 0
CZ02 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXOH | New Construction | Water Systems | 0 | 431048.37
CZ02 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ02 | cDXOH | New Construction | Generators | 0 | 0
CZ02 | cDXOH | New Construction | Total End Uses | 1845137.33 | 755113.43
CZ03 | cDXOH | New Construction | Heating | 0 | 68797.36
CZ03 | cDXOH | New Construction | Cooling | 127627.51 | 0
CZ03 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ03 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ03 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXOH | New Construction | Fans | 332190.76 | 0
CZ03 | cDXOH | New Construction | Pumps | 78.74 | 0
CZ03 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXOH | New Construction | Humidification | 0 | 0
CZ03 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXOH | New Construction | Water Systems | 0 | 429462.31
CZ03 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ03 | cDXOH | New Construction | Generators | 0 | 0
CZ03 | cDXOH | New Construction | Total End Uses | 1775600.81 | 723115.45
CZ04 | cDXOH | New Construction | Heating | 0 | 39096.85
CZ04 | cDXOH | New Construction | Cooling | 220824.58 | 0
CZ04 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ04 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ04 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXOH | New Construction | Fans | 350458.35 | 0
CZ04 | cDXOH | New Construction | Pumps | 98.03 | 0
CZ04 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXOH | New Construction | Humidification | 0 | 0
CZ04 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXOH | New Construction | Water Systems | 0 | 414703.25
CZ04 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ04 | cDXOH | New Construction | Generators | 0 | 0
CZ04 | cDXOH | New Construction | Total End Uses | 1887084.76 | 678655.88
CZ05 | cDXOH | New Construction | Heating | 0 | 63603.55
CZ05 | cDXOH | New Construction | Cooling | 160190.66 | 0
CZ05 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ05 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ05 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXOH | New Construction | Fans | 334515.85 | 0
CZ05 | cDXOH | New Construction | Pumps | 110.22 | 0
CZ05 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXOH | New Construction | Humidification | 0 | 0
CZ05 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXOH | New Construction | Water Systems | 0 | 429418.18
CZ05 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ05 | cDXOH | New Construction | Generators | 0 | 0
CZ05 | cDXOH | New Construction | Total End Uses | 1810520.53 | 717877.51
CZ06 | cDXOH | New Construction | Heating | 0 | 19683.59
CZ06 | cDXOH | New Construction | Cooling | 261837.26 | 0
CZ06 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ06 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ06 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXOH | New Construction | Fans | 353525.45 | 0
CZ06 | cDXOH | New Construction | Pumps | 130.88 | 0
CZ06 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXOH | New Construction | Humidification | 0 | 0
CZ06 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXOH | New Construction | Water Systems | 0 | 395573.68
CZ06 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ06 | cDXOH | New Construction | Generators | 0 | 0
CZ06 | cDXOH | New Construction | Total End Uses | 1931197.38 | 640113.05
CZ07 | cDXOH | New Construction | Heating | 0 | 16962.53
CZ07 | cDXOH | New Construction | Cooling | 272510.45 | 0
CZ07 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ07 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ07 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXOH | New Construction | Fans | 352460.54 | 0
CZ07 | cDXOH | New Construction | Pumps | 74.95 | 0
CZ07 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXOH | New Construction | Humidification | 0 | 0
CZ07 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXOH | New Construction | Water Systems | 0 | 390532.69
CZ07 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ07 | cDXOH | New Construction | Generators | 0 | 0
CZ07 | cDXOH | New Construction | Total End Uses | 1940749.74 | 632351
CZ08 | cDXOH | New Construction | Heating | 0 | 30367.39
CZ08 | cDXOH | New Construction | Cooling | 311360.43 | 0
CZ08 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ08 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ08 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXOH | New Construction | Fans | 370847.35 | 0
CZ08 | cDXOH | New Construction | Pumps | 106.14 | 0
CZ08 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXOH | New Construction | Humidification | 0 | 0
CZ08 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXOH | New Construction | Water Systems | 0 | 390033.24
CZ08 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ08 | cDXOH | New Construction | Generators | 0 | 0
CZ08 | cDXOH | New Construction | Total End Uses | 1998017.71 | 645256.4
CZ09 | cDXOH | New Construction | Heating | 0 | 23687.93
CZ09 | cDXOH | New Construction | Cooling | 333941.13 | 0
CZ09 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ09 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ09 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXOH | New Construction | Fans | 370048.53 | 0
CZ09 | cDXOH | New Construction | Pumps | 98.74 | 0
CZ09 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXOH | New Construction | Humidification | 0 | 0
CZ09 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXOH | New Construction | Water Systems | 0 | 384566.08
CZ09 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ09 | cDXOH | New Construction | Generators | 0 | 0
CZ09 | cDXOH | New Construction | Total End Uses | 2019792.21 | 633109.79
CZ10 | cDXOH | New Construction | Heating | 0 | 38128.57
CZ10 | cDXOH | New Construction | Cooling | 415563.25 | 0
CZ10 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ10 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ10 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXOH | New Construction | Fans | 399336.64 | 0
CZ10 | cDXOH | New Construction | Pumps | 105.79 | 0
CZ10 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXOH | New Construction | Humidification | 0 | 0
CZ10 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXOH | New Construction | Water Systems | 0 | 381508.75
CZ10 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ10 | cDXOH | New Construction | Generators | 0 | 0
CZ10 | cDXOH | New Construction | Total End Uses | 2130709.47 | 644493.1
CZ11 | cDXOH | New Construction | Heating | 0 | 125530.71
CZ11 | cDXOH | New Construction | Cooling | 425211.17 | 0
CZ11 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ11 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ11 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXOH | New Construction | Fans | 394563.79 | 0
CZ11 | cDXOH | New Construction | Pumps | 152.46 | 0
CZ11 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXOH | New Construction | Humidification | 0 | 0
CZ11 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXOH | New Construction | Water Systems | 0 | 389951.48
CZ11 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ11 | cDXOH | New Construction | Generators | 0 | 0
CZ11 | cDXOH | New Construction | Total End Uses | 2135631.21 | 740337.97
CZ12 | cDXOH | New Construction | Heating | 0 | 112327.72
CZ12 | cDXOH | New Construction | Cooling | 352445.51 | 0
CZ12 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ12 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ12 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXOH | New Construction | Fans | 374398.39 | 0
CZ12 | cDXOH | New Construction | Pumps | 130.24 | 0
CZ12 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXOH | New Construction | Humidification | 0 | 0
CZ12 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXOH | New Construction | Water Systems | 0 | 400954.17
CZ12 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ12 | cDXOH | New Construction | Generators | 0 | 0
CZ12 | cDXOH | New Construction | Total End Uses | 2042677.95 | 738137.66
CZ13 | cDXOH | New Construction | Heating | 0 | 97540.3
CZ13 | cDXOH | New Construction | Cooling | 472892.06 | 0
CZ13 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ13 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ13 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXOH | New Construction | Fans | 401403.15 | 0
CZ13 | cDXOH | New Construction | Pumps | 151.77 | 0
CZ13 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXOH | New Construction | Humidification | 0 | 0
CZ13 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXOH | New Construction | Water Systems | 0 | 378712.7
CZ13 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ13 | cDXOH | New Construction | Generators | 0 | 0
CZ13 | cDXOH | New Construction | Total End Uses | 2190150.77 | 701108.78
CZ14 | cDXOH | New Construction | Heating | 0 | 93259.17
CZ14 | cDXOH | New Construction | Cooling | 601859.14 | 0
CZ14 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ14 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ14 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXOH | New Construction | Fans | 437661.37 | 0
CZ14 | cDXOH | New Construction | Pumps | 178.46 | 0
CZ14 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXOH | New Construction | Humidification | 0 | 0
CZ14 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXOH | New Construction | Water Systems | 0 | 359401.06
CZ14 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ14 | cDXOH | New Construction | Generators | 0 | 0
CZ14 | cDXOH | New Construction | Total End Uses | 2355402.77 | 677516.01
CZ15 | cDXOH | New Construction | Heating | 0 | 72693.47
CZ15 | cDXOH | New Construction | Cooling | 836066.18 | 0
CZ15 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ15 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ15 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXOH | New Construction | Fans | 431843.55 | 0
CZ15 | cDXOH | New Construction | Pumps | 269.25 | 0
CZ15 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXOH | New Construction | Humidification | 0 | 0
CZ15 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXOH | New Construction | Water Systems | 0 | 319089.54
CZ15 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ15 | cDXOH | New Construction | Generators | 0 | 0
CZ15 | cDXOH | New Construction | Total End Uses | 2583882.78 | 616638.79
CZ16 | cDXOH | New Construction | Heating | 0 | 221608.94
CZ16 | cDXOH | New Construction | Cooling | 384268.55 | 0
CZ16 | cDXOH | New Construction | Interior Lighting | 352669.87 | 0
CZ16 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXOH | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ16 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXOH | New Construction | Fans | 447536.86 | 0
CZ16 | cDXOH | New Construction | Pumps | 150.16 | 0
CZ16 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXOH | New Construction | Humidification | 0 | 0
CZ16 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXOH | New Construction | Water Systems | 0 | 424062.78
CZ16 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ16 | cDXOH | New Construction | Generators | 0 | 0
CZ16 | cDXOH | New Construction | Total End Uses | 2147659.38 | 870527.51
CZ01 | cPVVG | Existing | Heating | 0 | 449209.09
CZ01 | cPVVG | Existing | Cooling | 69703.82 | 0
CZ01 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ01 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ01 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ01 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ01 | cPVVG | Existing | Fans | 228922.38 | 0
CZ01 | cPVVG | Existing | Pumps | 95.15 | 0
CZ01 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ01 | cPVVG | Existing | Humidification | 0 | 0
CZ01 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ01 | cPVVG | Existing | Water Systems | 0 | 469372.93
CZ01 | cPVVG | Existing | Refrigeration | 0 | 0
CZ01 | cPVVG | Existing | Generators | 0 | 0
CZ01 | cPVVG | Existing | Total End Uses | 1948825.87 | 1143437.8
CZ02 | cPVVG | Existing | Heating | 0 | 301168
CZ02 | cPVVG | Existing | Cooling | 264742.13 | 0
CZ02 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ02 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ02 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ02 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ02 | cPVVG | Existing | Fans | 299145.74 | 0
CZ02 | cPVVG | Existing | Pumps | 79.83 | 0
CZ02 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ02 | cPVVG | Existing | Humidification | 0 | 0
CZ02 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ02 | cPVVG | Existing | Water Systems | 0 | 431330.06
CZ02 | cPVVG | Existing | Refrigeration | 0 | 0
CZ02 | cPVVG | Existing | Generators | 0 | 0
CZ02 | cPVVG | Existing | Total End Uses | 2214072.23 | 957353.83
CZ03 | cPVVG | Existing | Heating | 0 | 173367.7
CZ03 | cPVVG | Existing | Cooling | 208970 | 0
CZ03 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ03 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ03 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ03 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ03 | cPVVG | Existing | Fans | 281081.53 | 0
CZ03 | cPVVG | Existing | Pumps | 80.48 | 0
CZ03 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ03 | cPVVG | Existing | Humidification | 0 | 0
CZ03 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ03 | cPVVG | Existing | Water Systems | 0 | 429645.67
CZ03 | cPVVG | Existing | Refrigeration | 0 | 0
CZ03 | cPVVG | Existing | Generators | 0 | 0
CZ03 | cPVVG | Existing | Total End Uses | 2140236.54 | 827869.15
CZ04 | cPVVG | Existing | Heating | 0 | 143924.87
CZ04 | cPVVG | Existing | Cooling | 314362.52 | 0
CZ04 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ04 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ04 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ04 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ04 | cPVVG | Existing | Fans | 315637.09 | 0
CZ04 | cPVVG | Existing | Pumps | 49.34 | 0
CZ04 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ04 | cPVVG | Existing | Humidification | 0 | 0
CZ04 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ04 | cPVVG | Existing | Water Systems | 0 | 414894.18
CZ04 | cPVVG | Existing | Refrigeration | 0 | 0
CZ04 | cPVVG | Existing | Generators | 0 | 0
CZ04 | cPVVG | Existing | Total End Uses | 2280153.47 | 783674.83
CZ05 | cPVVG | Existing | Heating | 0 | 159438.53
CZ05 | cPVVG | Existing | Cooling | 260422.69 | 0
CZ05 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ05 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ05 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ05 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ05 | cPVVG | Existing | Fans | 296486.59 | 0
CZ05 | cPVVG | Existing | Pumps | 119.19 | 0
CZ05 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ05 | cPVVG | Existing | Humidification | 0 | 0
CZ05 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ05 | cPVVG | Existing | Water Systems | 0 | 429663.64
CZ05 | cPVVG | Existing | Refrigeration | 0 | 0
CZ05 | cPVVG | Existing | Generators | 0 | 0
CZ05 | cPVVG | Existing | Total End Uses | 2207133 | 813957.95
CZ06 | cPVVG | Existing | Heating | 0 | 55027.19
CZ06 | cPVVG | Existing | Cooling | 412865.19 | 0
CZ06 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ06 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ06 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ06 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ06 | cPVVG | Existing | Fans | 338655.74 | 0
CZ06 | cPVVG | Existing | Pumps | 135.06 | 0
CZ06 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ06 | cPVVG | Existing | Humidification | 0 | 0
CZ06 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ06 | cPVVG | Existing | Water Systems | 0 | 395862.52
CZ06 | cPVVG | Existing | Refrigeration | 0 | 0
CZ06 | cPVVG | Existing | Generators | 0 | 0
CZ06 | cPVVG | Existing | Total End Uses | 2401760.52 | 675745.49
CZ07 | cPVVG | Existing | Heating | 0 | 33876.18
CZ07 | cPVVG | Existing | Cooling | 408875.48 | 0
CZ07 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ07 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ07 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ07 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ07 | cPVVG | Existing | Fans | 331820.82 | 0
CZ07 | cPVVG | Existing | Pumps | 75.73 | 0
CZ07 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ07 | cPVVG | Existing | Humidification | 0 | 0
CZ07 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ07 | cPVVG | Existing | Water Systems | 0 | 390807.62
CZ07 | cPVVG | Existing | Refrigeration | 0 | 0
CZ07 | cPVVG | Existing | Generators | 0 | 0
CZ07 | cPVVG | Existing | Total End Uses | 2390876.56 | 649539.58
CZ08 | cPVVG | Existing | Heating | 0 | 64103.17
CZ08 | cPVVG | Existing | Cooling | 443346.51 | 0
CZ08 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ08 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ08 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ08 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ08 | cPVVG | Existing | Fans | 352589.22 | 0
CZ08 | cPVVG | Existing | Pumps | 62.05 | 0
CZ08 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ08 | cPVVG | Existing | Humidification | 0 | 0
CZ08 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ08 | cPVVG | Existing | Water Systems | 0 | 390240.27
CZ08 | cPVVG | Existing | Refrigeration | 0 | 0
CZ08 | cPVVG | Existing | Generators | 0 | 0
CZ08 | cPVVG | Existing | Total End Uses | 2446102.29 | 679199.22
CZ09 | cPVVG | Existing | Heating | 0 | 61380.24
CZ09 | cPVVG | Existing | Cooling | 499705.78 | 0
CZ09 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ09 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ09 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ09 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ09 | cPVVG | Existing | Fans | 377509.9 | 0
CZ09 | cPVVG | Existing | Pumps | 67.02 | 0
CZ09 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ09 | cPVVG | Existing | Humidification | 0 | 0
CZ09 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ09 | cPVVG | Existing | Water Systems | 0 | 384822.06
CZ09 | cPVVG | Existing | Refrigeration | 0 | 0
CZ09 | cPVVG | Existing | Generators | 0 | 0
CZ09 | cPVVG | Existing | Total End Uses | 2527387.22 | 671058.08
CZ10 | cPVVG | Existing | Heating | 0 | 101498.24
CZ10 | cPVVG | Existing | Cooling | 560690.69 | 0
CZ10 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ10 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ10 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ10 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ10 | cPVVG | Existing | Fans | 382640.81 | 0
CZ10 | cPVVG | Existing | Pumps | 70.55 | 0
CZ10 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ10 | cPVVG | Existing | Humidification | 0 | 0
CZ10 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ10 | cPVVG | Existing | Water Systems | 0 | 381716.88
CZ10 | cPVVG | Existing | Refrigeration | 0 | 0
CZ10 | cPVVG | Existing | Generators | 0 | 0
CZ10 | cPVVG | Existing | Total End Uses | 2593506.57 | 708070.9
CZ11 | cPVVG | Existing | Heating | 0 | 345366.42
CZ11 | cPVVG | Existing | Cooling | 592936.8 | 0
CZ11 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ11 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ11 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ11 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ11 | cPVVG | Existing | Fans | 394778.18 | 0
CZ11 | cPVVG | Existing | Pumps | 101.74 | 0
CZ11 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ11 | cPVVG | Existing | Humidification | 0 | 0
CZ11 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ11 | cPVVG | Existing | Water Systems | 0 | 390216.56
CZ11 | cPVVG | Existing | Refrigeration | 0 | 0
CZ11 | cPVVG | Existing | Generators | 0 | 0
CZ11 | cPVVG | Existing | Total End Uses | 2637921.24 | 960438.76
CZ12 | cPVVG | Existing | Heating | 0 | 293024.51
CZ12 | cPVVG | Existing | Cooling | 490332.6 | 0
CZ12 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ12 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ12 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ12 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ12 | cPVVG | Existing | Fans | 358314.25 | 0
CZ12 | cPVVG | Existing | Pumps | 89.14 | 0
CZ12 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ12 | cPVVG | Existing | Humidification | 0 | 0
CZ12 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ12 | cPVVG | Existing | Water Systems | 0 | 401215.38
CZ12 | cPVVG | Existing | Refrigeration | 0 | 0
CZ12 | cPVVG | Existing | Generators | 0 | 0
CZ12 | cPVVG | Existing | Total End Uses | 2498840.51 | 919095.67
CZ13 | cPVVG | Existing | Heating | 0 | 242931.49
CZ13 | cPVVG | Existing | Cooling | 655251.37 | 0
CZ13 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ13 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ13 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ13 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ13 | cPVVG | Existing | Fans | 405232.99 | 0
CZ13 | cPVVG | Existing | Pumps | 84.92 | 0
CZ13 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ13 | cPVVG | Existing | Humidification | 0 | 0
CZ13 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ13 | cPVVG | Existing | Water Systems | 0 | 378873.18
CZ13 | cPVVG | Existing | Refrigeration | 0 | 0
CZ13 | cPVVG | Existing | Generators | 0 | 0
CZ13 | cPVVG | Existing | Total End Uses | 2710673.8 | 846660.45
CZ14 | cPVVG | Existing | Heating | 0 | 171697.51
CZ14 | cPVVG | Existing | Cooling | 804993.81 | 0
CZ14 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ14 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ14 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ14 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ14 | cPVVG | Existing | Fans | 458941.75 | 0
CZ14 | cPVVG | Existing | Pumps | 79.5 | 0
CZ14 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ14 | cPVVG | Existing | Humidification | 0 | 0
CZ14 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ14 | cPVVG | Existing | Water Systems | 0 | 359702.55
CZ14 | cPVVG | Existing | Refrigeration | 0 | 0
CZ14 | cPVVG | Existing | Generators | 0 | 0
CZ14 | cPVVG | Existing | Total End Uses | 2914119.58 | 756255.84
CZ15 | cPVVG | Existing | Heating | 0 | 85184.49
CZ15 | cPVVG | Existing | Cooling | 1109377.01 | 0
CZ15 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ15 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ15 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ15 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ15 | cPVVG | Existing | Fans | 496180.55 | 0
CZ15 | cPVVG | Existing | Pumps | 112.15 | 0
CZ15 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ15 | cPVVG | Existing | Humidification | 0 | 0
CZ15 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ15 | cPVVG | Existing | Water Systems | 0 | 319386.66
CZ15 | cPVVG | Existing | Refrigeration | 0 | 0
CZ15 | cPVVG | Existing | Generators | 0 | 0
CZ15 | cPVVG | Existing | Total End Uses | 3255774.23 | 629426.93
CZ16 | cPVVG | Existing | Heating | 0 | 496058.36
CZ16 | cPVVG | Existing | Cooling | 519272.07 | 0
CZ16 | cPVVG | Existing | Interior Lighting | 687070.6 | 0
CZ16 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ16 | cPVVG | Existing | Interior Equipment | 963033.93 | 224855.78
CZ16 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ16 | cPVVG | Existing | Fans | 436513.5 | 0
CZ16 | cPVVG | Existing | Pumps | 115.28 | 0
CZ16 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ16 | cPVVG | Existing | Humidification | 0 | 0
CZ16 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ16 | cPVVG | Existing | Water Systems | 0 | 424227.9
CZ16 | cPVVG | Existing | Refrigeration | 0 | 0
CZ16 | cPVVG | Existing | Generators | 0 | 0
CZ16 | cPVVG | Existing | Total End Uses | 2606005.37 | 1145142.04
CZ01 | cPVVG | New Construction | Heating | 0 | 367594.81
CZ01 | cPVVG | New Construction | Cooling | 47316.98 | 0
CZ01 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ01 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ01 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ01 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ01 | cPVVG | New Construction | Fans | 184682.76 | 0
CZ01 | cPVVG | New Construction | Pumps | 72.82 | 0
CZ01 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ01 | cPVVG | New Construction | Humidification | 0 | 0
CZ01 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ01 | cPVVG | New Construction | Water Systems | 0 | 469172.87
CZ01 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ01 | cPVVG | New Construction | Generators | 0 | 0
CZ01 | cPVVG | New Construction | Total End Uses | 1547776.35 | 1061623.47
CZ02 | cPVVG | New Construction | Heating | 0 | 219881.08
CZ02 | cPVVG | New Construction | Cooling | 183879.86 | 0
CZ02 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ02 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ02 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ02 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ02 | cPVVG | New Construction | Fans | 208689.54 | 0
CZ02 | cPVVG | New Construction | Pumps | 110.46 | 0
CZ02 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ02 | cPVVG | New Construction | Humidification | 0 | 0
CZ02 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ02 | cPVVG | New Construction | Water Systems | 0 | 431109.19
CZ02 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ02 | cPVVG | New Construction | Generators | 0 | 0
CZ02 | cPVVG | New Construction | Total End Uses | 1708383.66 | 875846.05
CZ03 | cPVVG | New Construction | Heating | 0 | 157336.8
CZ03 | cPVVG | New Construction | Cooling | 129713.15 | 0
CZ03 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ03 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ03 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ03 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ03 | cPVVG | New Construction | Fans | 193469.65 | 0
CZ03 | cPVVG | New Construction | Pumps | 76.99 | 0
CZ03 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ03 | cPVVG | New Construction | Humidification | 0 | 0
CZ03 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ03 | cPVVG | New Construction | Water Systems | 0 | 429441.54
CZ03 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ03 | cPVVG | New Construction | Generators | 0 | 0
CZ03 | cPVVG | New Construction | Total End Uses | 1638963.59 | 811634.12
CZ04 | cPVVG | New Construction | Heating | 0 | 112454.05
CZ04 | cPVVG | New Construction | Cooling | 219173.19 | 0
CZ04 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ04 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ04 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ04 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ04 | cPVVG | New Construction | Fans | 215674.74 | 0
CZ04 | cPVVG | New Construction | Pumps | 98.09 | 0
CZ04 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ04 | cPVVG | New Construction | Humidification | 0 | 0
CZ04 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ04 | cPVVG | New Construction | Water Systems | 0 | 414688.98
CZ04 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ04 | cPVVG | New Construction | Generators | 0 | 0
CZ04 | cPVVG | New Construction | Total End Uses | 1750649.82 | 751998.81
CZ05 | cPVVG | New Construction | Heating | 0 | 155926.64
CZ05 | cPVVG | New Construction | Cooling | 161395.31 | 0
CZ05 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ05 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ05 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ05 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ05 | cPVVG | New Construction | Fans | 201590.57 | 0
CZ05 | cPVVG | New Construction | Pumps | 106.93 | 0
CZ05 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ05 | cPVVG | New Construction | Humidification | 0 | 0
CZ05 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ05 | cPVVG | New Construction | Water Systems | 0 | 429448.54
CZ05 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ05 | cPVVG | New Construction | Generators | 0 | 0
CZ05 | cPVVG | New Construction | Total End Uses | 1678796.61 | 810230.97
CZ06 | cPVVG | New Construction | Heating | 0 | 41743.79
CZ06 | cPVVG | New Construction | Cooling | 262400.87 | 0
CZ06 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ06 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ06 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ06 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ06 | cPVVG | New Construction | Fans | 223217.8 | 0
CZ06 | cPVVG | New Construction | Pumps | 131.2 | 0
CZ06 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ06 | cPVVG | New Construction | Humidification | 0 | 0
CZ06 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ06 | cPVVG | New Construction | Water Systems | 0 | 395612.24
CZ06 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ06 | cPVVG | New Construction | Generators | 0 | 0
CZ06 | cPVVG | New Construction | Total End Uses | 1801453.67 | 662211.81
CZ07 | cPVVG | New Construction | Heating | 0 | 36722.34
CZ07 | cPVVG | New Construction | Cooling | 269868.72 | 0
CZ07 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ07 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ07 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ07 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ07 | cPVVG | New Construction | Fans | 225596.46 | 0
CZ07 | cPVVG | New Construction | Pumps | 76.02 | 0
CZ07 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ07 | cPVVG | New Construction | Humidification | 0 | 0
CZ07 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ07 | cPVVG | New Construction | Water Systems | 0 | 390520.99
CZ07 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ07 | cPVVG | New Construction | Generators | 0 | 0
CZ07 | cPVVG | New Construction | Total End Uses | 1811245 | 652099.11
CZ08 | cPVVG | New Construction | Heating | 0 | 61507.68
CZ08 | cPVVG | New Construction | Cooling | 308261.07 | 0
CZ08 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ08 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ08 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ08 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ08 | cPVVG | New Construction | Fans | 237644.12 | 0
CZ08 | cPVVG | New Construction | Pumps | 104.73 | 0
CZ08 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ08 | cPVVG | New Construction | Humidification | 0 | 0
CZ08 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ08 | cPVVG | New Construction | Water Systems | 0 | 390041.3
CZ08 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ08 | cPVVG | New Construction | Generators | 0 | 0
CZ08 | cPVVG | New Construction | Total End Uses | 1861713.71 | 676404.76
CZ09 | cPVVG | New Construction | Heating | 0 | 46204.71
CZ09 | cPVVG | New Construction | Cooling | 329193.4 | 0
CZ09 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ09 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ09 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ09 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ09 | cPVVG | New Construction | Fans | 243352.55 | 0
CZ09 | cPVVG | New Construction | Pumps | 98.82 | 0
CZ09 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ09 | cPVVG | New Construction | Humidification | 0 | 0
CZ09 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ09 | cPVVG | New Construction | Water Systems | 0 | 384613.3
CZ09 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ09 | cPVVG | New Construction | Generators | 0 | 0
CZ09 | cPVVG | New Construction | Total End Uses | 1888348.56 | 655673.79
CZ10 | cPVVG | New Construction | Heating | 0 | 89763.49
CZ10 | cPVVG | New Construction | Cooling | 407309.58 | 0
CZ10 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ10 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ10 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ10 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ10 | cPVVG | New Construction | Fans | 265692.41 | 0
CZ10 | cPVVG | New Construction | Pumps | 103.97 | 0
CZ10 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ10 | cPVVG | New Construction | Humidification | 0 | 0
CZ10 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ10 | cPVVG | New Construction | Water Systems | 0 | 381455.97
CZ10 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ10 | cPVVG | New Construction | Generators | 0 | 0
CZ10 | cPVVG | New Construction | Total End Uses | 1988809.75 | 696075.24
CZ11 | cPVVG | New Construction | Heating | 0 | 236793.03
CZ11 | cPVVG | New Construction | Cooling | 418201.5 | 0
CZ11 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ11 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ11 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ11 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ11 | cPVVG | New Construction | Fans | 261294.04 | 0
CZ11 | cPVVG | New Construction | Pumps | 150.13 | 0
CZ11 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ11 | cPVVG | New Construction | Humidification | 0 | 0
CZ11 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ11 | cPVVG | New Construction | Water Systems | 0 | 389955.37
CZ11 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ11 | cPVVG | New Construction | Generators | 0 | 0
CZ11 | cPVVG | New Construction | Total End Uses | 1995349.46 | 851604.18
CZ12 | cPVVG | New Construction | Heating | 0 | 219576.96
CZ12 | cPVVG | New Construction | Cooling | 346414.93 | 0
CZ12 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ12 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ12 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ12 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ12 | cPVVG | New Construction | Fans | 243184 | 0
CZ12 | cPVVG | New Construction | Pumps | 123 | 0
CZ12 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ12 | cPVVG | New Construction | Humidification | 0 | 0
CZ12 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ12 | cPVVG | New Construction | Water Systems | 0 | 400988.74
CZ12 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ12 | cPVVG | New Construction | Generators | 0 | 0
CZ12 | cPVVG | New Construction | Total End Uses | 1905425.73 | 845421.47
CZ13 | cPVVG | New Construction | Heating | 0 | 189365.45
CZ13 | cPVVG | New Construction | Cooling | 465027.5 | 0
CZ13 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ13 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ13 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ13 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ13 | cPVVG | New Construction | Fans | 271522.82 | 0
CZ13 | cPVVG | New Construction | Pumps | 148.19 | 0
CZ13 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ13 | cPVVG | New Construction | Humidification | 0 | 0
CZ13 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ13 | cPVVG | New Construction | Water Systems | 0 | 378701.54
CZ13 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ13 | cPVVG | New Construction | Generators | 0 | 0
CZ13 | cPVVG | New Construction | Total End Uses | 2052402.3 | 792922.76
CZ14 | cPVVG | New Construction | Heating | 0 | 161279.22
CZ14 | cPVVG | New Construction | Cooling | 591426.98 | 0
CZ14 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ14 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ14 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ14 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ14 | cPVVG | New Construction | Fans | 305226.83 | 0
CZ14 | cPVVG | New Construction | Pumps | 179.13 | 0
CZ14 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ14 | cPVVG | New Construction | Humidification | 0 | 0
CZ14 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ14 | cPVVG | New Construction | Water Systems | 0 | 359443.54
CZ14 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ14 | cPVVG | New Construction | Generators | 0 | 0
CZ14 | cPVVG | New Construction | Total End Uses | 2212536.74 | 745578.54
CZ15 | cPVVG | New Construction | Heating | 0 | 98382.35
CZ15 | cPVVG | New Construction | Cooling | 823719.58 | 0
CZ15 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ15 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ15 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ15 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ15 | cPVVG | New Construction | Fans | 322662.26 | 0
CZ15 | cPVVG | New Construction | Pumps | 268.95 | 0
CZ15 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ15 | cPVVG | New Construction | Humidification | 0 | 0
CZ15 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ15 | cPVVG | New Construction | Water Systems | 0 | 319094.31
CZ15 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ15 | cPVVG | New Construction | Generators | 0 | 0
CZ15 | cPVVG | New Construction | Total End Uses | 2462354.59 | 642332.44
CZ16 | cPVVG | New Construction | Heating | 0 | 401682.37
CZ16 | cPVVG | New Construction | Cooling | 377372.88 | 0
CZ16 | cPVVG | New Construction | Interior Lighting | 352669.87 | 0
CZ16 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ16 | cPVVG | New Construction | Interior Equipment | 963033.93 | 224855.78
CZ16 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ16 | cPVVG | New Construction | Fans | 297029.26 | 0
CZ16 | cPVVG | New Construction | Pumps | 147.74 | 0
CZ16 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ16 | cPVVG | New Construction | Humidification | 0 | 0
CZ16 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ16 | cPVVG | New Construction | Water Systems | 0 | 423982.96
CZ16 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ16 | cPVVG | New Construction | Generators | 0 | 0
CZ16 | cPVVG | New Construction | Total End Uses | 1990253.68 | 1050521.11

## Raw_endusebreakdownannual (hidden)
Vintage | Climate Zone | HVAC System | End Use | Electricity [kBtu] | Natural Gas [kBtu]
Existing | CZ01 | cAVVG | Heating | 0 | 514010.34
Existing | CZ01 | cAVVG | Cooling | 71008.63 | 0
Existing | CZ01 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ01 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ01 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ01 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ01 | cAVVG | Fans | 216053.37 | 0
Existing | CZ01 | cAVVG | Pumps | 806.93 | 0
Existing | CZ01 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ01 | cAVVG | Humidification | 0 | 0
Existing | CZ01 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ01 | cAVVG | Water Systems | 0 | 469376.41
Existing | CZ01 | cAVVG | Refrigeration | 0 | 0
Existing | CZ01 | cAVVG | Generators | 0 | 0
Existing | CZ01 | cAVVG | Total End Uses | 1937973.45 | 1208242.52
Existing | CZ02 | cAVVG | Heating | 0 | 345324.29
Existing | CZ02 | cAVVG | Cooling | 292904.16 | 0
Existing | CZ02 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ02 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ02 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ02 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ02 | cAVVG | Fans | 269720.73 | 0
Existing | CZ02 | cAVVG | Pumps | 5311.08 | 0
Existing | CZ02 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ02 | cAVVG | Humidification | 0 | 0
Existing | CZ02 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ02 | cAVVG | Water Systems | 0 | 431341.4
Existing | CZ02 | cAVVG | Refrigeration | 0 | 0
Existing | CZ02 | cAVVG | Generators | 0 | 0
Existing | CZ02 | cAVVG | Total End Uses | 2218040.49 | 1001521.47
Existing | CZ03 | cAVVG | Heating | 0 | 198227.66
Existing | CZ03 | cAVVG | Cooling | 225235.41 | 0
Existing | CZ03 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ03 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ03 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ03 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ03 | cAVVG | Fans | 252643.51 | 0
Existing | CZ03 | cAVVG | Pumps | 4454.73 | 0
Existing | CZ03 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ03 | cAVVG | Humidification | 0 | 0
Existing | CZ03 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ03 | cAVVG | Water Systems | 0 | 429646.85
Existing | CZ03 | cAVVG | Refrigeration | 0 | 0
Existing | CZ03 | cAVVG | Generators | 0 | 0
Existing | CZ03 | cAVVG | Total End Uses | 2132438.18 | 852730.29
Existing | CZ04 | cAVVG | Heating | 0 | 167479.39
Existing | CZ04 | cAVVG | Cooling | 346023.64 | 0
Existing | CZ04 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ04 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ04 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ04 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ04 | cAVVG | Fans | 289646.1 | 0
Existing | CZ04 | cAVVG | Pumps | 6336.91 | 0
Existing | CZ04 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ04 | cAVVG | Humidification | 0 | 0
Existing | CZ04 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ04 | cAVVG | Water Systems | 0 | 414905.65
Existing | CZ04 | cAVVG | Refrigeration | 0 | 0
Existing | CZ04 | cAVVG | Generators | 0 | 0
Existing | CZ04 | cAVVG | Total End Uses | 2292111.17 | 807240.82
Existing | CZ05 | cAVVG | Heating | 0 | 184878.26
Existing | CZ05 | cAVVG | Cooling | 273255.83 | 0
Existing | CZ05 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ05 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ05 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ05 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ05 | cAVVG | Fans | 269550.36 | 0
Existing | CZ05 | cAVVG | Pumps | 4330.73 | 0
Existing | CZ05 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ05 | cAVVG | Humidification | 0 | 0
Existing | CZ05 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ05 | cAVVG | Water Systems | 0 | 429679.76
Existing | CZ05 | cAVVG | Refrigeration | 0 | 0
Existing | CZ05 | cAVVG | Generators | 0 | 0
Existing | CZ05 | cAVVG | Total End Uses | 2197241.44 | 839413.8
Existing | CZ06 | cAVVG | Heating | 0 | 62553.66
Existing | CZ06 | cAVVG | Cooling | 448347.44 | 0
Existing | CZ06 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ06 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ06 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ06 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ06 | cAVVG | Fans | 329965.71 | 0
Existing | CZ06 | cAVVG | Pumps | 8277.03 | 0
Existing | CZ06 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ06 | cAVVG | Humidification | 0 | 0
Existing | CZ06 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ06 | cAVVG | Water Systems | 0 | 395831.07
Existing | CZ06 | cAVVG | Refrigeration | 0 | 0
Existing | CZ06 | cAVVG | Generators | 0 | 0
Existing | CZ06 | cAVVG | Total End Uses | 2436694.71 | 683240.51
Existing | CZ07 | cAVVG | Heating | 0 | 43953.85
Existing | CZ07 | cAVVG | Cooling | 453101.86 | 0
Existing | CZ07 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ07 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ07 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ07 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ07 | cAVVG | Fans | 327308.74 | 0
Existing | CZ07 | cAVVG | Pumps | 9154.93 | 0
Existing | CZ07 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ07 | cAVVG | Humidification | 0 | 0
Existing | CZ07 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ07 | cAVVG | Water Systems | 0 | 390819.63
Existing | CZ07 | cAVVG | Refrigeration | 0 | 0
Existing | CZ07 | cAVVG | Generators | 0 | 0
Existing | CZ07 | cAVVG | Total End Uses | 2439670.05 | 659629.25
Existing | CZ08 | cAVVG | Heating | 0 | 93877.24
Existing | CZ08 | cAVVG | Cooling | 483036.57 | 0
Existing | CZ08 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ08 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ08 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ08 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ08 | cAVVG | Fans | 326055.89 | 0
Existing | CZ08 | cAVVG | Pumps | 7038.09 | 0
Existing | CZ08 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ08 | cAVVG | Humidification | 0 | 0
Existing | CZ08 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ08 | cAVVG | Water Systems | 0 | 390248.14
Existing | CZ08 | cAVVG | Refrigeration | 0 | 0
Existing | CZ08 | cAVVG | Generators | 0 | 0
Existing | CZ08 | cAVVG | Total End Uses | 2466235.07 | 708981.16
Existing | CZ09 | cAVVG | Heating | 0 | 73602.98
Existing | CZ09 | cAVVG | Cooling | 555684.84 | 0
Existing | CZ09 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ09 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ09 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ09 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ09 | cAVVG | Fans | 367630.75 | 0
Existing | CZ09 | cAVVG | Pumps | 9863.18 | 0
Existing | CZ09 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ09 | cAVVG | Humidification | 0 | 0
Existing | CZ09 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ09 | cAVVG | Water Systems | 0 | 384836.09
Existing | CZ09 | cAVVG | Refrigeration | 0 | 0
Existing | CZ09 | cAVVG | Generators | 0 | 0
Existing | CZ09 | cAVVG | Total End Uses | 2583283.29 | 683294.85
Existing | CZ10 | cAVVG | Heating | 0 | 149781.39
Existing | CZ10 | cAVVG | Cooling | 605504.8 | 0
Existing | CZ10 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ10 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ10 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ10 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ10 | cAVVG | Fans | 357228.71 | 0
Existing | CZ10 | cAVVG | Pumps | 6951.57 | 0
Existing | CZ10 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ10 | cAVVG | Humidification | 0 | 0
Existing | CZ10 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ10 | cAVVG | Water Systems | 0 | 381748.89
Existing | CZ10 | cAVVG | Refrigeration | 0 | 0
Existing | CZ10 | cAVVG | Generators | 0 | 0
Existing | CZ10 | cAVVG | Total End Uses | 2619789.6 | 756386.05
Existing | CZ11 | cAVVG | Heating | 0 | 413763.4
Existing | CZ11 | cAVVG | Cooling | 638140.11 | 0
Existing | CZ11 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ11 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ11 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ11 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ11 | cAVVG | Fans | 364973.29 | 0
Existing | CZ11 | cAVVG | Pumps | 6331.11 | 0
Existing | CZ11 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ11 | cAVVG | Humidification | 0 | 0
Existing | CZ11 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ11 | cAVVG | Water Systems | 0 | 390241.83
Existing | CZ11 | cAVVG | Refrigeration | 0 | 0
Existing | CZ11 | cAVVG | Generators | 0 | 0
Existing | CZ11 | cAVVG | Total End Uses | 2659549.03 | 1028861.01
Existing | CZ12 | cAVVG | Heating | 0 | 354163.22
Existing | CZ12 | cAVVG | Cooling | 527187.85 | 0
Existing | CZ12 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ12 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ12 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ12 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ12 | cAVVG | Fans | 332990.67 | 0
Existing | CZ12 | cAVVG | Pumps | 5996.85 | 0
Existing | CZ12 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ12 | cAVVG | Humidification | 0 | 0
Existing | CZ12 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ12 | cAVVG | Water Systems | 0 | 401232.94
Existing | CZ12 | cAVVG | Refrigeration | 0 | 0
Existing | CZ12 | cAVVG | Generators | 0 | 0
Existing | CZ12 | cAVVG | Total End Uses | 2516279.9 | 980251.94
Existing | CZ13 | cAVVG | Heating | 0 | 299332.92
Existing | CZ13 | cAVVG | Cooling | 704741.31 | 0
Existing | CZ13 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ13 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ13 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ13 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ13 | cAVVG | Fans | 383537.81 | 0
Existing | CZ13 | cAVVG | Pumps | 7103.18 | 0
Existing | CZ13 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ13 | cAVVG | Humidification | 0 | 0
Existing | CZ13 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ13 | cAVVG | Water Systems | 0 | 378918.69
Existing | CZ13 | cAVVG | Refrigeration | 0 | 0
Existing | CZ13 | cAVVG | Generators | 0 | 0
Existing | CZ13 | cAVVG | Total End Uses | 2745486.83 | 903107.39
Existing | CZ14 | cAVVG | Heating | 0 | 199606.42
Existing | CZ14 | cAVVG | Cooling | 869420.88 | 0
Existing | CZ14 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ14 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ14 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ14 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ14 | cAVVG | Fans | 453839.61 | 0
Existing | CZ14 | cAVVG | Pumps | 10586.36 | 0
Existing | CZ14 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ14 | cAVVG | Humidification | 0 | 0
Existing | CZ14 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ14 | cAVVG | Water Systems | 0 | 359701.9
Existing | CZ14 | cAVVG | Refrigeration | 0 | 0
Existing | CZ14 | cAVVG | Generators | 0 | 0
Existing | CZ14 | cAVVG | Total End Uses | 2983951.37 | 784164.1
Existing | CZ15 | cAVVG | Heating | 0 | 126013.2
Existing | CZ15 | cAVVG | Cooling | 1214832.82 | 0
Existing | CZ15 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ15 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ15 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ15 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ15 | cAVVG | Fans | 474396.02 | 0
Existing | CZ15 | cAVVG | Pumps | 10068.99 | 0
Existing | CZ15 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ15 | cAVVG | Humidification | 0 | 0
Existing | CZ15 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ15 | cAVVG | Water Systems | 0 | 319393.16
Existing | CZ15 | cAVVG | Refrigeration | 0 | 0
Existing | CZ15 | cAVVG | Generators | 0 | 0
Existing | CZ15 | cAVVG | Total End Uses | 3349402.35 | 670262.14
Existing | CZ16 | cAVVG | Heating | 0 | 557960.29
Existing | CZ16 | cAVVG | Cooling | 547952.92 | 0
Existing | CZ16 | cAVVG | Interior Lighting | 687070.6 | 0
Existing | CZ16 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ16 | cAVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ16 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ16 | cAVVG | Fans | 415594.07 | 0
Existing | CZ16 | cAVVG | Pumps | 6280 | 0
Existing | CZ16 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ16 | cAVVG | Humidification | 0 | 0
Existing | CZ16 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ16 | cAVVG | Water Systems | 0 | 424237.74
Existing | CZ16 | cAVVG | Refrigeration | 0 | 0
Existing | CZ16 | cAVVG | Generators | 0 | 0
Existing | CZ16 | cAVVG | Total End Uses | 2619931.51 | 1207053.82
New Construction | CZ01 | cAVVG | Heating | 0 | 481355.79
New Construction | CZ01 | cAVVG | Cooling | 49179.03 | 0
New Construction | CZ01 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ01 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ01 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ01 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ01 | cAVVG | Fans | 181192.96 | 0
New Construction | CZ01 | cAVVG | Pumps | 619.92 | 0
New Construction | CZ01 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ01 | cAVVG | Humidification | 0 | 0
New Construction | CZ01 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ01 | cAVVG | Water Systems | 0 | 469147.19
New Construction | CZ01 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ01 | cAVVG | Generators | 0 | 0
New Construction | CZ01 | cAVVG | Total End Uses | 1546695.71 | 1175358.76
New Construction | CZ02 | cAVVG | Heating | 0 | 289043.58
New Construction | CZ02 | cAVVG | Cooling | 199915.31 | 0
New Construction | CZ02 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ02 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ02 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ02 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ02 | cAVVG | Fans | 195162.19 | 0
New Construction | CZ02 | cAVVG | Pumps | 2993.14 | 0
New Construction | CZ02 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ02 | cAVVG | Humidification | 0 | 0
New Construction | CZ02 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ02 | cAVVG | Water Systems | 0 | 431054.23
New Construction | CZ02 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ02 | cAVVG | Generators | 0 | 0
New Construction | CZ02 | cAVVG | Total End Uses | 1713774.44 | 944953.58
New Construction | CZ03 | cAVVG | Heating | 0 | 197660.19
New Construction | CZ03 | cAVVG | Cooling | 144394.39 | 0
New Construction | CZ03 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ03 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ03 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ03 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ03 | cAVVG | Fans | 180732.48 | 0
New Construction | CZ03 | cAVVG | Pumps | 3164.49 | 0
New Construction | CZ03 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ03 | cAVVG | Humidification | 0 | 0
New Construction | CZ03 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ03 | cAVVG | Water Systems | 0 | 429442.24
New Construction | CZ03 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ03 | cAVVG | Generators | 0 | 0
New Construction | CZ03 | cAVVG | Total End Uses | 1643995.15 | 851958.21
New Construction | CZ04 | cAVVG | Heating | 0 | 160657.83
New Construction | CZ04 | cAVVG | Cooling | 235873.63 | 0
New Construction | CZ04 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ04 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ04 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ04 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ04 | cAVVG | Fans | 201001.52 | 0
New Construction | CZ04 | cAVVG | Pumps | 3390.34 | 0
New Construction | CZ04 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ04 | cAVVG | Humidification | 0 | 0
New Construction | CZ04 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ04 | cAVVG | Water Systems | 0 | 414599.25
New Construction | CZ04 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ04 | cAVVG | Generators | 0 | 0
New Construction | CZ04 | cAVVG | Total End Uses | 1755969.29 | 800112.86
New Construction | CZ05 | cAVVG | Heating | 0 | 202273.26
New Construction | CZ05 | cAVVG | Cooling | 173312.44 | 0
New Construction | CZ05 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ05 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ05 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ05 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ05 | cAVVG | Fans | 188861.75 | 0
New Construction | CZ05 | cAVVG | Pumps | 3006.96 | 0
New Construction | CZ05 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ05 | cAVVG | Humidification | 0 | 0
New Construction | CZ05 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ05 | cAVVG | Water Systems | 0 | 429472.45
New Construction | CZ05 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ05 | cAVVG | Generators | 0 | 0
New Construction | CZ05 | cAVVG | Total End Uses | 1680884.94 | 856601.49
New Construction | CZ06 | cAVVG | Heating | 0 | 55295.47
New Construction | CZ06 | cAVVG | Cooling | 294839.46 | 0
New Construction | CZ06 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ06 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ06 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ06 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ06 | cAVVG | Fans | 216629.65 | 0
New Construction | CZ06 | cAVVG | Pumps | 5830.04 | 0
New Construction | CZ06 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ06 | cAVVG | Humidification | 0 | 0
New Construction | CZ06 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ06 | cAVVG | Water Systems | 0 | 395630.62
New Construction | CZ06 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ06 | cAVVG | Generators | 0 | 0
New Construction | CZ06 | cAVVG | Total End Uses | 1833002.95 | 675781.87
New Construction | CZ07 | cAVVG | Heating | 0 | 64160.71
New Construction | CZ07 | cAVVG | Cooling | 298920.87 | 0
New Construction | CZ07 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ07 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ07 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ07 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ07 | cAVVG | Fans | 210568.1 | 0
New Construction | CZ07 | cAVVG | Pumps | 4951.83 | 0
New Construction | CZ07 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ07 | cAVVG | Humidification | 0 | 0
New Construction | CZ07 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ07 | cAVVG | Water Systems | 0 | 390526.63
New Construction | CZ07 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ07 | cAVVG | Generators | 0 | 0
New Construction | CZ07 | cAVVG | Total End Uses | 1830144.6 | 679543.13
New Construction | CZ08 | cAVVG | Heating | 0 | 100312.34
New Construction | CZ08 | cAVVG | Cooling | 338115.76 | 0
New Construction | CZ08 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ08 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ08 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ08 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ08 | cAVVG | Fans | 222328.1 | 0
New Construction | CZ08 | cAVVG | Pumps | 4988.58 | 0
New Construction | CZ08 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ08 | cAVVG | Humidification | 0 | 0
New Construction | CZ08 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ08 | cAVVG | Water Systems | 0 | 390033.95
New Construction | CZ08 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ08 | cAVVG | Generators | 0 | 0
New Construction | CZ08 | cAVVG | Total End Uses | 1881136.23 | 715202.07
New Construction | CZ09 | cAVVG | Heating | 0 | 79506.14
New Construction | CZ09 | cAVVG | Cooling | 358445.68 | 0
New Construction | CZ09 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ09 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ09 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ09 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ09 | cAVVG | Fans | 227454.41 | 0
New Construction | CZ09 | cAVVG | Pumps | 4959.04 | 0
New Construction | CZ09 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ09 | cAVVG | Humidification | 0 | 0
New Construction | CZ09 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ09 | cAVVG | Water Systems | 0 | 384549.01
New Construction | CZ09 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ09 | cAVVG | Generators | 0 | 0
New Construction | CZ09 | cAVVG | Total End Uses | 1906562.93 | 688910.93
New Construction | CZ10 | cAVVG | Heating | 0 | 140667.3
New Construction | CZ10 | cAVVG | Cooling | 439352.91 | 0
New Construction | CZ10 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ10 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ10 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ10 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ10 | cAVVG | Fans | 250434.92 | 0
New Construction | CZ10 | cAVVG | Pumps | 5149.75 | 0
New Construction | CZ10 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ10 | cAVVG | Humidification | 0 | 0
New Construction | CZ10 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ10 | cAVVG | Water Systems | 0 | 381479.5
New Construction | CZ10 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ10 | cAVVG | Generators | 0 | 0
New Construction | CZ10 | cAVVG | Total End Uses | 2010641.37 | 747002.58
New Construction | CZ11 | cAVVG | Heating | 0 | 305432.34
New Construction | CZ11 | cAVVG | Cooling | 452129.02 | 0
New Construction | CZ11 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ11 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ11 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ11 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ11 | cAVVG | Fans | 246688.49 | 0
New Construction | CZ11 | cAVVG | Pumps | 4471.23 | 0
New Construction | CZ11 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ11 | cAVVG | Humidification | 0 | 0
New Construction | CZ11 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ11 | cAVVG | Water Systems | 0 | 389911.09
New Construction | CZ11 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ11 | cAVVG | Generators | 0 | 0
New Construction | CZ11 | cAVVG | Total End Uses | 2018992.54 | 920199.21
New Construction | CZ12 | cAVVG | Heating | 0 | 287394.5
New Construction | CZ12 | cAVVG | Cooling | 374576.91 | 0
New Construction | CZ12 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ12 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ12 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ12 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ12 | cAVVG | Fans | 230101.59 | 0
New Construction | CZ12 | cAVVG | Pumps | 4405.35 | 0
New Construction | CZ12 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ12 | cAVVG | Humidification | 0 | 0
New Construction | CZ12 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ12 | cAVVG | Water Systems | 0 | 400999.58
New Construction | CZ12 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ12 | cAVVG | Generators | 0 | 0
New Construction | CZ12 | cAVVG | Total End Uses | 1924787.64 | 913249.85
New Construction | CZ13 | cAVVG | Heating | 0 | 253291.96
New Construction | CZ13 | cAVVG | Cooling | 501835.58 | 0
New Construction | CZ13 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ13 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ13 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ13 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ13 | cAVVG | Fans | 259379.6 | 0
New Construction | CZ13 | cAVVG | Pumps | 5155.29 | 0
New Construction | CZ13 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ13 | cAVVG | Humidification | 0 | 0
New Construction | CZ13 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ13 | cAVVG | Water Systems | 0 | 378730.98
New Construction | CZ13 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ13 | cAVVG | Generators | 0 | 0
New Construction | CZ13 | cAVVG | Total End Uses | 2082074.27 | 856878.72
New Construction | CZ14 | cAVVG | Heating | 0 | 212393.73
New Construction | CZ14 | cAVVG | Cooling | 634579.55 | 0
New Construction | CZ14 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ14 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ14 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ14 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ14 | cAVVG | Fans | 286847.91 | 0
New Construction | CZ14 | cAVVG | Pumps | 4951.57 | 0
New Construction | CZ14 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ14 | cAVVG | Humidification | 0 | 0
New Construction | CZ14 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ14 | cAVVG | Water Systems | 0 | 359515.9
New Construction | CZ14 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ14 | cAVVG | Generators | 0 | 0
New Construction | CZ14 | cAVVG | Total End Uses | 2242082.84 | 796765.41
New Construction | CZ15 | cAVVG | Heating | 0 | 136880.19
New Construction | CZ15 | cAVVG | Cooling | 912344.05 | 0
New Construction | CZ15 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ15 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ15 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ15 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ15 | cAVVG | Fans | 303747.45 | 0
New Construction | CZ15 | cAVVG | Pumps | 7285.88 | 0
New Construction | CZ15 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ15 | cAVVG | Humidification | 0 | 0
New Construction | CZ15 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ15 | cAVVG | Water Systems | 0 | 319092.13
New Construction | CZ15 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ15 | cAVVG | Generators | 0 | 0
New Construction | CZ15 | cAVVG | Total End Uses | 2539081.18 | 680828.1
New Construction | CZ16 | cAVVG | Heating | 0 | 473821.89
New Construction | CZ16 | cAVVG | Cooling | 398255.34 | 0
New Construction | CZ16 | cAVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ16 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ16 | cAVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ16 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ16 | cAVVG | Fans | 282937.86 | 0
New Construction | CZ16 | cAVVG | Pumps | 4611.67 | 0
New Construction | CZ16 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ16 | cAVVG | Humidification | 0 | 0
New Construction | CZ16 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ16 | cAVVG | Water Systems | 0 | 424061.69
New Construction | CZ16 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ16 | cAVVG | Generators | 0 | 0
New Construction | CZ16 | cAVVG | Total End Uses | 2001508.68 | 1122739.36
Existing | CZ01 | cDXGF | Heating | 0 | 375841.32
Existing | CZ01 | cDXGF | Cooling | 67852.82 | 0
Existing | CZ01 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ01 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ01 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXGF | Fans | 418595.52 | 0
Existing | CZ01 | cDXGF | Pumps | 93.44 | 0
Existing | CZ01 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ01 | cDXGF | Humidification | 0 | 0
Existing | CZ01 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ01 | cDXGF | Water Systems | 0 | 469375.61
Existing | CZ01 | cDXGF | Refrigeration | 0 | 0
Existing | CZ01 | cDXGF | Generators | 0 | 0
Existing | CZ01 | cDXGF | Total End Uses | 2136646.3 | 1070072.71
Existing | CZ02 | cDXGF | Heating | 0 | 253027.43
Existing | CZ02 | cDXGF | Cooling | 266941.89 | 0
Existing | CZ02 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ02 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ02 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXGF | Fans | 498802.14 | 0
Existing | CZ02 | cDXGF | Pumps | 78.49 | 0
Existing | CZ02 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ02 | cDXGF | Humidification | 0 | 0
Existing | CZ02 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ02 | cDXGF | Water Systems | 0 | 431332.86
Existing | CZ02 | cDXGF | Refrigeration | 0 | 0
Existing | CZ02 | cDXGF | Generators | 0 | 0
Existing | CZ02 | cDXGF | Total End Uses | 2415927.04 | 909216.07
Existing | CZ03 | cDXGF | Heating | 0 | 140076.03
Existing | CZ03 | cDXGF | Cooling | 204982.04 | 0
Existing | CZ03 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ03 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ03 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXGF | Fans | 478855.83 | 0
Existing | CZ03 | cDXGF | Pumps | 79.44 | 0
Existing | CZ03 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ03 | cDXGF | Humidification | 0 | 0
Existing | CZ03 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ03 | cDXGF | Water Systems | 0 | 429645.79
Existing | CZ03 | cDXGF | Refrigeration | 0 | 0
Existing | CZ03 | cDXGF | Generators | 0 | 0
Existing | CZ03 | cDXGF | Total End Uses | 2334021.84 | 794577.6
Existing | CZ04 | cDXGF | Heating | 0 | 113655.82
Existing | CZ04 | cDXGF | Cooling | 316061.82 | 0
Existing | CZ04 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ04 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ04 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXGF | Fans | 513139.47 | 0
Existing | CZ04 | cDXGF | Pumps | 48.66 | 0
Existing | CZ04 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ04 | cDXGF | Humidification | 0 | 0
Existing | CZ04 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ04 | cDXGF | Water Systems | 0 | 414900.14
Existing | CZ04 | cDXGF | Refrigeration | 0 | 0
Existing | CZ04 | cDXGF | Generators | 0 | 0
Existing | CZ04 | cDXGF | Total End Uses | 2479354.48 | 753411.74
Existing | CZ05 | cDXGF | Heating | 0 | 129962.27
Existing | CZ05 | cDXGF | Cooling | 257990.06 | 0
Existing | CZ05 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ05 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ05 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXGF | Fans | 485634.33 | 0
Existing | CZ05 | cDXGF | Pumps | 118.18 | 0
Existing | CZ05 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ05 | cDXGF | Humidification | 0 | 0
Existing | CZ05 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ05 | cDXGF | Water Systems | 0 | 429659.13
Existing | CZ05 | cDXGF | Refrigeration | 0 | 0
Existing | CZ05 | cDXGF | Generators | 0 | 0
Existing | CZ05 | cDXGF | Total End Uses | 2393847.1 | 784477.17
Existing | CZ06 | cDXGF | Heating | 0 | 46252.54
Existing | CZ06 | cDXGF | Cooling | 408162.53 | 0
Existing | CZ06 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ06 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ06 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXGF | Fans | 517823.01 | 0
Existing | CZ06 | cDXGF | Pumps | 134.32 | 0
Existing | CZ06 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ06 | cDXGF | Humidification | 0 | 0
Existing | CZ06 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ06 | cDXGF | Water Systems | 0 | 395858.3
Existing | CZ06 | cDXGF | Refrigeration | 0 | 0
Existing | CZ06 | cDXGF | Generators | 0 | 0
Existing | CZ06 | cDXGF | Total End Uses | 2576224.39 | 666966.62
Existing | CZ07 | cDXGF | Heating | 0 | 27758.66
Existing | CZ07 | cDXGF | Cooling | 409565.7 | 0
Existing | CZ07 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ07 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ07 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXGF | Fans | 505508.63 | 0
Existing | CZ07 | cDXGF | Pumps | 75.85 | 0
Existing | CZ07 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ07 | cDXGF | Humidification | 0 | 0
Existing | CZ07 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ07 | cDXGF | Water Systems | 0 | 390807.67
Existing | CZ07 | cDXGF | Refrigeration | 0 | 0
Existing | CZ07 | cDXGF | Generators | 0 | 0
Existing | CZ07 | cDXGF | Total End Uses | 2565254.7 | 643422.11
Existing | CZ08 | cDXGF | Heating | 0 | 53363.87
Existing | CZ08 | cDXGF | Cooling | 445251.33 | 0
Existing | CZ08 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ08 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ08 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXGF | Fans | 537557.1 | 0
Existing | CZ08 | cDXGF | Pumps | 61.34 | 0
Existing | CZ08 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ08 | cDXGF | Humidification | 0 | 0
Existing | CZ08 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ08 | cDXGF | Water Systems | 0 | 390220.56
Existing | CZ08 | cDXGF | Refrigeration | 0 | 0
Existing | CZ08 | cDXGF | Generators | 0 | 0
Existing | CZ08 | cDXGF | Total End Uses | 2632974.29 | 668440.2
Existing | CZ09 | cDXGF | Heating | 0 | 52844.06
Existing | CZ09 | cDXGF | Cooling | 504532.75 | 0
Existing | CZ09 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ09 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ09 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXGF | Fans | 563565.5 | 0
Existing | CZ09 | cDXGF | Pumps | 66.46 | 0
Existing | CZ09 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ09 | cDXGF | Humidification | 0 | 0
Existing | CZ09 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ09 | cDXGF | Water Systems | 0 | 384835.05
Existing | CZ09 | cDXGF | Refrigeration | 0 | 0
Existing | CZ09 | cDXGF | Generators | 0 | 0
Existing | CZ09 | cDXGF | Total End Uses | 2718269.23 | 662534.89
Existing | CZ10 | cDXGF | Heating | 0 | 81904.47
Existing | CZ10 | cDXGF | Cooling | 570808.11 | 0
Existing | CZ10 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ10 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ10 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXGF | Fans | 569848.6 | 0
Existing | CZ10 | cDXGF | Pumps | 69.67 | 0
Existing | CZ10 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ10 | cDXGF | Humidification | 0 | 0
Existing | CZ10 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ10 | cDXGF | Water Systems | 0 | 381731.4
Existing | CZ10 | cDXGF | Refrigeration | 0 | 0
Existing | CZ10 | cDXGF | Generators | 0 | 0
Existing | CZ10 | cDXGF | Total End Uses | 2790830.9 | 688491.65
Existing | CZ11 | cDXGF | Heating | 0 | 294345.33
Existing | CZ11 | cDXGF | Cooling | 603818.82 | 0
Existing | CZ11 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ11 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ11 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXGF | Fans | 590699.1 | 0
Existing | CZ11 | cDXGF | Pumps | 100.81 | 0
Existing | CZ11 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ11 | cDXGF | Humidification | 0 | 0
Existing | CZ11 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ11 | cDXGF | Water Systems | 0 | 390240.29
Existing | CZ11 | cDXGF | Refrigeration | 0 | 0
Existing | CZ11 | cDXGF | Generators | 0 | 0
Existing | CZ11 | cDXGF | Total End Uses | 2844723.25 | 909441.4
Existing | CZ12 | cDXGF | Heating | 0 | 247857.58
Existing | CZ12 | cDXGF | Cooling | 498009.12 | 0
Existing | CZ12 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ12 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ12 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXGF | Fans | 545144.07 | 0
Existing | CZ12 | cDXGF | Pumps | 87.67 | 0
Existing | CZ12 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ12 | cDXGF | Humidification | 0 | 0
Existing | CZ12 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ12 | cDXGF | Water Systems | 0 | 401211.49
Existing | CZ12 | cDXGF | Refrigeration | 0 | 0
Existing | CZ12 | cDXGF | Generators | 0 | 0
Existing | CZ12 | cDXGF | Total End Uses | 2693345.38 | 873924.85
Existing | CZ13 | cDXGF | Heating | 0 | 202485.8
Existing | CZ13 | cDXGF | Cooling | 666381.8 | 0
Existing | CZ13 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ13 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ13 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXGF | Fans | 590828.05 | 0
Existing | CZ13 | cDXGF | Pumps | 84.19 | 0
Existing | CZ13 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ13 | cDXGF | Humidification | 0 | 0
Existing | CZ13 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ13 | cDXGF | Water Systems | 0 | 378887.03
Existing | CZ13 | cDXGF | Refrigeration | 0 | 0
Existing | CZ13 | cDXGF | Generators | 0 | 0
Existing | CZ13 | cDXGF | Total End Uses | 2907398.57 | 806228.6
Existing | CZ14 | cDXGF | Heating | 0 | 144312.25
Existing | CZ14 | cDXGF | Cooling | 821102.62 | 0
Existing | CZ14 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ14 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ14 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXGF | Fans | 651420.05 | 0
Existing | CZ14 | cDXGF | Pumps | 78.71 | 0
Existing | CZ14 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ14 | cDXGF | Humidification | 0 | 0
Existing | CZ14 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ14 | cDXGF | Water Systems | 0 | 359698.2
Existing | CZ14 | cDXGF | Refrigeration | 0 | 0
Existing | CZ14 | cDXGF | Generators | 0 | 0
Existing | CZ14 | cDXGF | Total End Uses | 3122705.9 | 728866.22
Existing | CZ15 | cDXGF | Heating | 0 | 77762.02
Existing | CZ15 | cDXGF | Cooling | 1129579.74 | 0
Existing | CZ15 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ15 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ15 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXGF | Fans | 659583.45 | 0
Existing | CZ15 | cDXGF | Pumps | 113.28 | 0
Existing | CZ15 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ15 | cDXGF | Humidification | 0 | 0
Existing | CZ15 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ15 | cDXGF | Water Systems | 0 | 319363.55
Existing | CZ15 | cDXGF | Refrigeration | 0 | 0
Existing | CZ15 | cDXGF | Generators | 0 | 0
Existing | CZ15 | cDXGF | Total End Uses | 3439380.99 | 621981.35
Existing | CZ16 | cDXGF | Heating | 0 | 433232.15
Existing | CZ16 | cDXGF | Cooling | 530549.15 | 0
Existing | CZ16 | cDXGF | Interior Lighting | 687070.6 | 0
Existing | CZ16 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXGF | Interior Equipment | 963033.93 | 224855.78
Existing | CZ16 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXGF | Fans | 646057.52 | 0
Existing | CZ16 | cDXGF | Pumps | 113.02 | 0
Existing | CZ16 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ16 | cDXGF | Humidification | 0 | 0
Existing | CZ16 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ16 | cDXGF | Water Systems | 0 | 424216.48
Existing | CZ16 | cDXGF | Refrigeration | 0 | 0
Existing | CZ16 | cDXGF | Generators | 0 | 0
Existing | CZ16 | cDXGF | Total End Uses | 2826824.21 | 1082304.41
New Construction | CZ01 | cDXGF | Heating | 0 | 305586.73
New Construction | CZ01 | cDXGF | Cooling | 46679.82 | 0
New Construction | CZ01 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ01 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ01 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXGF | Fans | 309913.98 | 0
New Construction | CZ01 | cDXGF | Pumps | 70.84 | 0
New Construction | CZ01 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXGF | Humidification | 0 | 0
New Construction | CZ01 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXGF | Water Systems | 0 | 469147.89
New Construction | CZ01 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ01 | cDXGF | Generators | 0 | 0
New Construction | CZ01 | cDXGF | Total End Uses | 1672368.44 | 999590.4
New Construction | CZ02 | cDXGF | Heating | 0 | 179680.67
New Construction | CZ02 | cDXGF | Cooling | 186599.57 | 0
New Construction | CZ02 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ02 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ02 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXGF | Fans | 344074.28 | 0
New Construction | CZ02 | cDXGF | Pumps | 110.47 | 0
New Construction | CZ02 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXGF | Humidification | 0 | 0
New Construction | CZ02 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXGF | Water Systems | 0 | 431130.67
New Construction | CZ02 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ02 | cDXGF | Generators | 0 | 0
New Construction | CZ02 | cDXGF | Total End Uses | 1846488.12 | 835667.12
New Construction | CZ03 | cDXGF | Heating | 0 | 124463.85
New Construction | CZ03 | cDXGF | Cooling | 128497.27 | 0
New Construction | CZ03 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ03 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ03 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXGF | Fans | 331924.32 | 0
New Construction | CZ03 | cDXGF | Pumps | 77.02 | 0
New Construction | CZ03 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXGF | Humidification | 0 | 0
New Construction | CZ03 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXGF | Water Systems | 0 | 429429.5
New Construction | CZ03 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ03 | cDXGF | Generators | 0 | 0
New Construction | CZ03 | cDXGF | Total End Uses | 1776202.4 | 778749.13
New Construction | CZ04 | cDXGF | Heating | 0 | 87355.12
New Construction | CZ04 | cDXGF | Cooling | 222038.45 | 0
New Construction | CZ04 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ04 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ04 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXGF | Fans | 350872.78 | 0
New Construction | CZ04 | cDXGF | Pumps | 96.95 | 0
New Construction | CZ04 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXGF | Humidification | 0 | 0
New Construction | CZ04 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXGF | Water Systems | 0 | 414713.48
New Construction | CZ04 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ04 | cDXGF | Generators | 0 | 0
New Construction | CZ04 | cDXGF | Total End Uses | 1888711.97 | 726924.38
New Construction | CZ05 | cDXGF | Heating | 0 | 126947.43
New Construction | CZ05 | cDXGF | Cooling | 162112.52 | 0
New Construction | CZ05 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ05 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ05 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXGF | Fans | 334908.14 | 0
New Construction | CZ05 | cDXGF | Pumps | 107.92 | 0
New Construction | CZ05 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXGF | Humidification | 0 | 0
New Construction | CZ05 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXGF | Water Systems | 0 | 429479.16
New Construction | CZ05 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ05 | cDXGF | Generators | 0 | 0
New Construction | CZ05 | cDXGF | Total End Uses | 1812832.37 | 781282.37
New Construction | CZ06 | cDXGF | Heating | 0 | 32566.54
New Construction | CZ06 | cDXGF | Cooling | 262048.55 | 0
New Construction | CZ06 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ06 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ06 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXGF | Fans | 353708.94 | 0
New Construction | CZ06 | cDXGF | Pumps | 130.93 | 0
New Construction | CZ06 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXGF | Humidification | 0 | 0
New Construction | CZ06 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXGF | Water Systems | 0 | 395628.2
New Construction | CZ06 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ06 | cDXGF | Generators | 0 | 0
New Construction | CZ06 | cDXGF | Total End Uses | 1931592.22 | 653050.53
New Construction | CZ07 | cDXGF | Heating | 0 | 28314.65
New Construction | CZ07 | cDXGF | Cooling | 272458.26 | 0
New Construction | CZ07 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ07 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ07 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXGF | Fans | 352418.78 | 0
New Construction | CZ07 | cDXGF | Pumps | 75.09 | 0
New Construction | CZ07 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXGF | Humidification | 0 | 0
New Construction | CZ07 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXGF | Water Systems | 0 | 390518.65
New Construction | CZ07 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ07 | cDXGF | Generators | 0 | 0
New Construction | CZ07 | cDXGF | Total End Uses | 1940655.92 | 643689.08
New Construction | CZ08 | cDXGF | Heating | 0 | 49401.35
New Construction | CZ08 | cDXGF | Cooling | 311824.2 | 0
New Construction | CZ08 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ08 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ08 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXGF | Fans | 370963.12 | 0
New Construction | CZ08 | cDXGF | Pumps | 104.8 | 0
New Construction | CZ08 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXGF | Humidification | 0 | 0
New Construction | CZ08 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXGF | Water Systems | 0 | 390005.49
New Construction | CZ08 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ08 | cDXGF | Generators | 0 | 0
New Construction | CZ08 | cDXGF | Total End Uses | 1998595.91 | 664262.62
New Construction | CZ09 | cDXGF | Heating | 0 | 37016.72
New Construction | CZ09 | cDXGF | Cooling | 334450.14 | 0
New Construction | CZ09 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ09 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ09 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXGF | Fans | 370365.41 | 0
New Construction | CZ09 | cDXGF | Pumps | 98.61 | 0
New Construction | CZ09 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXGF | Humidification | 0 | 0
New Construction | CZ09 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXGF | Water Systems | 0 | 384560.47
New Construction | CZ09 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ09 | cDXGF | Generators | 0 | 0
New Construction | CZ09 | cDXGF | Total End Uses | 2020617.96 | 646432.97
New Construction | CZ10 | cDXGF | Heating | 0 | 71210.44
New Construction | CZ10 | cDXGF | Cooling | 416221.67 | 0
New Construction | CZ10 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ10 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ10 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXGF | Fans | 399615.39 | 0
New Construction | CZ10 | cDXGF | Pumps | 104.38 | 0
New Construction | CZ10 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXGF | Humidification | 0 | 0
New Construction | CZ10 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXGF | Water Systems | 0 | 381519.95
New Construction | CZ10 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ10 | cDXGF | Generators | 0 | 0
New Construction | CZ10 | cDXGF | Total End Uses | 2131645.24 | 677586.17
New Construction | CZ11 | cDXGF | Heating | 0 | 194754.78
New Construction | CZ11 | cDXGF | Cooling | 426456.35 | 0
New Construction | CZ11 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ11 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ11 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXGF | Fans | 393822.77 | 0
New Construction | CZ11 | cDXGF | Pumps | 149.21 | 0
New Construction | CZ11 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXGF | Humidification | 0 | 0
New Construction | CZ11 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXGF | Water Systems | 0 | 389935.2
New Construction | CZ11 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ11 | cDXGF | Generators | 0 | 0
New Construction | CZ11 | cDXGF | Total End Uses | 2136132.13 | 809545.77
New Construction | CZ12 | cDXGF | Heating | 0 | 183132.44
New Construction | CZ12 | cDXGF | Cooling | 353354.07 | 0
New Construction | CZ12 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ12 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ12 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXGF | Fans | 373666.63 | 0
New Construction | CZ12 | cDXGF | Pumps | 123.63 | 0
New Construction | CZ12 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXGF | Humidification | 0 | 0
New Construction | CZ12 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXGF | Water Systems | 0 | 400979.06
New Construction | CZ12 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ12 | cDXGF | Generators | 0 | 0
New Construction | CZ12 | cDXGF | Total End Uses | 2042848.13 | 808967.28
New Construction | CZ13 | cDXGF | Heating | 0 | 154985.65
New Construction | CZ13 | cDXGF | Cooling | 474050.41 | 0
New Construction | CZ13 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ13 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ13 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXGF | Fans | 400943.75 | 0
New Construction | CZ13 | cDXGF | Pumps | 149.18 | 0
New Construction | CZ13 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXGF | Humidification | 0 | 0
New Construction | CZ13 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXGF | Water Systems | 0 | 378691.73
New Construction | CZ13 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ13 | cDXGF | Generators | 0 | 0
New Construction | CZ13 | cDXGF | Total End Uses | 2190847.13 | 758533.16
New Construction | CZ14 | cDXGF | Heating | 0 | 135682.43
New Construction | CZ14 | cDXGF | Cooling | 603029.65 | 0
New Construction | CZ14 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ14 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ14 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXGF | Fans | 437871.74 | 0
New Construction | CZ14 | cDXGF | Pumps | 178.53 | 0
New Construction | CZ14 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXGF | Humidification | 0 | 0
New Construction | CZ14 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXGF | Water Systems | 0 | 359344.14
New Construction | CZ14 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ14 | cDXGF | Generators | 0 | 0
New Construction | CZ14 | cDXGF | Total End Uses | 2356783.72 | 719882.35
New Construction | CZ15 | cDXGF | Heating | 0 | 89749.38
New Construction | CZ15 | cDXGF | Cooling | 837157.11 | 0
New Construction | CZ15 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ15 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ15 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXGF | Fans | 432259.1 | 0
New Construction | CZ15 | cDXGF | Pumps | 269.25 | 0
New Construction | CZ15 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXGF | Humidification | 0 | 0
New Construction | CZ15 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXGF | Water Systems | 0 | 319111.69
New Construction | CZ15 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ15 | cDXGF | Generators | 0 | 0
New Construction | CZ15 | cDXGF | Total End Uses | 2585389.25 | 633716.85
New Construction | CZ16 | cDXGF | Heating | 0 | 345013.92
New Construction | CZ16 | cDXGF | Cooling | 386665.65 | 0
New Construction | CZ16 | cDXGF | Interior Lighting | 352669.87 | 0
New Construction | CZ16 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXGF | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ16 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXGF | Fans | 446545.82 | 0
New Construction | CZ16 | cDXGF | Pumps | 147.63 | 0
New Construction | CZ16 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXGF | Humidification | 0 | 0
New Construction | CZ16 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXGF | Water Systems | 0 | 423978.93
New Construction | CZ16 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ16 | cDXGF | Generators | 0 | 0
New Construction | CZ16 | cDXGF | Total End Uses | 2149062.89 | 993848.63
Existing | CZ01 | cDXHP | Heating | 33124.14 | 243296.43
Existing | CZ01 | cDXHP | Cooling | 67482.22 | 0
Existing | CZ01 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ01 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ01 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXHP | Fans | 418647.07 | 0
Existing | CZ01 | cDXHP | Pumps | 93.47 | 0
Existing | CZ01 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ01 | cDXHP | Humidification | 0 | 0
Existing | CZ01 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ01 | cDXHP | Water Systems | 0 | 469374.71
Existing | CZ01 | cDXHP | Refrigeration | 0 | 0
Existing | CZ01 | cDXHP | Generators | 0 | 0
Existing | CZ01 | cDXHP | Total End Uses | 2169451.42 | 937526.92
Existing | CZ02 | cDXHP | Heating | 23483 | 171734.88
Existing | CZ02 | cDXHP | Cooling | 266289.83 | 0
Existing | CZ02 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ02 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ02 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXHP | Fans | 498811.72 | 0
Existing | CZ02 | cDXHP | Pumps | 78.9 | 0
Existing | CZ02 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ02 | cDXHP | Humidification | 0 | 0
Existing | CZ02 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ02 | cDXHP | Water Systems | 0 | 431325.1
Existing | CZ02 | cDXHP | Refrigeration | 0 | 0
Existing | CZ02 | cDXHP | Generators | 0 | 0
Existing | CZ02 | cDXHP | Total End Uses | 2438767.98 | 827915.76
Existing | CZ03 | cDXHP | Heating | 11699.28 | 94635.37
Existing | CZ03 | cDXHP | Cooling | 204047.48 | 0
Existing | CZ03 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ03 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ03 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXHP | Fans | 478779.55 | 0
Existing | CZ03 | cDXHP | Pumps | 79.4 | 0
Existing | CZ03 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ03 | cDXHP | Humidification | 0 | 0
Existing | CZ03 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ03 | cDXHP | Water Systems | 0 | 429641.82
Existing | CZ03 | cDXHP | Refrigeration | 0 | 0
Existing | CZ03 | cDXHP | Generators | 0 | 0
Existing | CZ03 | cDXHP | Total End Uses | 2344710.22 | 749132.97
Existing | CZ04 | cDXHP | Heating | 10252.83 | 74473.38
Existing | CZ04 | cDXHP | Cooling | 315827.82 | 0
Existing | CZ04 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ04 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ04 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXHP | Fans | 513126.99 | 0
Existing | CZ04 | cDXHP | Pumps | 48.9 | 0
Existing | CZ04 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ04 | cDXHP | Humidification | 0 | 0
Existing | CZ04 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ04 | cDXHP | Water Systems | 0 | 414901.04
Existing | CZ04 | cDXHP | Refrigeration | 0 | 0
Existing | CZ04 | cDXHP | Generators | 0 | 0
Existing | CZ04 | cDXHP | Total End Uses | 2489361.07 | 714230.2
Existing | CZ05 | cDXHP | Heating | 11948.25 | 85326.84
Existing | CZ05 | cDXHP | Cooling | 257149.07 | 0
Existing | CZ05 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ05 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ05 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXHP | Fans | 485668.03 | 0
Existing | CZ05 | cDXHP | Pumps | 117.82 | 0
Existing | CZ05 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ05 | cDXHP | Humidification | 0 | 0
Existing | CZ05 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ05 | cDXHP | Water Systems | 0 | 429676
Existing | CZ05 | cDXHP | Refrigeration | 0 | 0
Existing | CZ05 | cDXHP | Generators | 0 | 0
Existing | CZ05 | cDXHP | Total End Uses | 2404987.69 | 739858.63
Existing | CZ06 | cDXHP | Heating | 1485.56 | 39952.49
Existing | CZ06 | cDXHP | Cooling | 404821.76 | 0
Existing | CZ06 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ06 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ06 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXHP | Fans | 517746.01 | 0
Existing | CZ06 | cDXHP | Pumps | 133.83 | 0
Existing | CZ06 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ06 | cDXHP | Humidification | 0 | 0
Existing | CZ06 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ06 | cDXHP | Water Systems | 0 | 395842.91
Existing | CZ06 | cDXHP | Refrigeration | 0 | 0
Existing | CZ06 | cDXHP | Generators | 0 | 0
Existing | CZ06 | cDXHP | Total End Uses | 2574291.68 | 660651.18
Existing | CZ07 | cDXHP | Heating | 1262.8 | 22347.37
Existing | CZ07 | cDXHP | Cooling | 407626.86 | 0
Existing | CZ07 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ07 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ07 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXHP | Fans | 505686.05 | 0
Existing | CZ07 | cDXHP | Pumps | 75.76 | 0
Existing | CZ07 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ07 | cDXHP | Humidification | 0 | 0
Existing | CZ07 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ07 | cDXHP | Water Systems | 0 | 390807.03
Existing | CZ07 | cDXHP | Refrigeration | 0 | 0
Existing | CZ07 | cDXHP | Generators | 0 | 0
Existing | CZ07 | cDXHP | Total End Uses | 2564756 | 638010.18
Existing | CZ08 | cDXHP | Heating | 2690.69 | 41834.21
Existing | CZ08 | cDXHP | Cooling | 444117.71 | 0
Existing | CZ08 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ08 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ08 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXHP | Fans | 537504.08 | 0
Existing | CZ08 | cDXHP | Pumps | 61.18 | 0
Existing | CZ08 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ08 | cDXHP | Humidification | 0 | 0
Existing | CZ08 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ08 | cDXHP | Water Systems | 0 | 390234.52
Existing | CZ08 | cDXHP | Refrigeration | 0 | 0
Existing | CZ08 | cDXHP | Generators | 0 | 0
Existing | CZ08 | cDXHP | Total End Uses | 2634478.18 | 656924.51
Existing | CZ09 | cDXHP | Heating | 1899.99 | 44802.26
Existing | CZ09 | cDXHP | Cooling | 503461.16 | 0
Existing | CZ09 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ09 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ09 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXHP | Fans | 563478.74 | 0
Existing | CZ09 | cDXHP | Pumps | 66.72 | 0
Existing | CZ09 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ09 | cDXHP | Humidification | 0 | 0
Existing | CZ09 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ09 | cDXHP | Water Systems | 0 | 384843
Existing | CZ09 | cDXHP | Refrigeration | 0 | 0
Existing | CZ09 | cDXHP | Generators | 0 | 0
Existing | CZ09 | cDXHP | Total End Uses | 2719011.13 | 654501.03
Existing | CZ10 | cDXHP | Heating | 7810.88 | 54974.05
Existing | CZ10 | cDXHP | Cooling | 570637.46 | 0
Existing | CZ10 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ10 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ10 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXHP | Fans | 569851.9 | 0
Existing | CZ10 | cDXHP | Pumps | 69.93 | 0
Existing | CZ10 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ10 | cDXHP | Humidification | 0 | 0
Existing | CZ10 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ10 | cDXHP | Water Systems | 0 | 381729.95
Existing | CZ10 | cDXHP | Refrigeration | 0 | 0
Existing | CZ10 | cDXHP | Generators | 0 | 0
Existing | CZ10 | cDXHP | Total End Uses | 2798474.68 | 661559.78
Existing | CZ11 | cDXHP | Heating | 21230.24 | 217676.82
Existing | CZ11 | cDXHP | Cooling | 603930.99 | 0
Existing | CZ11 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ11 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ11 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXHP | Fans | 590666.2 | 0
Existing | CZ11 | cDXHP | Pumps | 100.59 | 0
Existing | CZ11 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ11 | cDXHP | Humidification | 0 | 0
Existing | CZ11 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ11 | cDXHP | Water Systems | 0 | 390230.49
Existing | CZ11 | cDXHP | Refrigeration | 0 | 0
Existing | CZ11 | cDXHP | Generators | 0 | 0
Existing | CZ11 | cDXHP | Total End Uses | 2866032.54 | 832763.09
Existing | CZ12 | cDXHP | Heating | 21419.03 | 172553.47
Existing | CZ12 | cDXHP | Cooling | 497875.05 | 0
Existing | CZ12 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ12 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ12 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXHP | Fans | 545209.12 | 0
Existing | CZ12 | cDXHP | Pumps | 87.58 | 0
Existing | CZ12 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ12 | cDXHP | Humidification | 0 | 0
Existing | CZ12 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ12 | cDXHP | Water Systems | 0 | 401209.75
Existing | CZ12 | cDXHP | Refrigeration | 0 | 0
Existing | CZ12 | cDXHP | Generators | 0 | 0
Existing | CZ12 | cDXHP | Total End Uses | 2714695.3 | 798619.01
Existing | CZ13 | cDXHP | Heating | 15942.57 | 144587.99
Existing | CZ13 | cDXHP | Cooling | 666548.75 | 0
Existing | CZ13 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ13 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ13 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXHP | Fans | 590698.13 | 0
Existing | CZ13 | cDXHP | Pumps | 84.43 | 0
Existing | CZ13 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ13 | cDXHP | Humidification | 0 | 0
Existing | CZ13 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ13 | cDXHP | Water Systems | 0 | 378882.8
Existing | CZ13 | cDXHP | Refrigeration | 0 | 0
Existing | CZ13 | cDXHP | Generators | 0 | 0
Existing | CZ13 | cDXHP | Total End Uses | 2923378.4 | 748326.56
Existing | CZ14 | cDXHP | Heating | 10190.93 | 108613.54
Existing | CZ14 | cDXHP | Cooling | 821057.83 | 0
Existing | CZ14 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ14 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ14 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXHP | Fans | 651493.74 | 0
Existing | CZ14 | cDXHP | Pumps | 78.31 | 0
Existing | CZ14 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ14 | cDXHP | Humidification | 0 | 0
Existing | CZ14 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ14 | cDXHP | Water Systems | 0 | 359695.18
Existing | CZ14 | cDXHP | Refrigeration | 0 | 0
Existing | CZ14 | cDXHP | Generators | 0 | 0
Existing | CZ14 | cDXHP | Total End Uses | 3132925.34 | 693164.5
Existing | CZ15 | cDXHP | Heating | 2840.39 | 65497.51
Existing | CZ15 | cDXHP | Cooling | 1128863.21 | 0
Existing | CZ15 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ15 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ15 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXHP | Fans | 659614.16 | 0
Existing | CZ15 | cDXHP | Pumps | 111.61 | 0
Existing | CZ15 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ15 | cDXHP | Humidification | 0 | 0
Existing | CZ15 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ15 | cDXHP | Water Systems | 0 | 319381.61
Existing | CZ15 | cDXHP | Refrigeration | 0 | 0
Existing | CZ15 | cDXHP | Generators | 0 | 0
Existing | CZ15 | cDXHP | Total End Uses | 3441533.89 | 609734.89
Existing | CZ16 | cDXHP | Heating | 46115 | 304324.55
Existing | CZ16 | cDXHP | Cooling | 530635.16 | 0
Existing | CZ16 | cDXHP | Interior Lighting | 687070.6 | 0
Existing | CZ16 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXHP | Interior Equipment | 963033.93 | 224855.78
Existing | CZ16 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXHP | Fans | 646033.38 | 0
Existing | CZ16 | cDXHP | Pumps | 113.33 | 0
Existing | CZ16 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ16 | cDXHP | Humidification | 0 | 0
Existing | CZ16 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ16 | cDXHP | Water Systems | 0 | 424217.9
Existing | CZ16 | cDXHP | Refrigeration | 0 | 0
Existing | CZ16 | cDXHP | Generators | 0 | 0
Existing | CZ16 | cDXHP | Total End Uses | 2873001.38 | 953398.23
New Construction | CZ01 | cDXHP | Heating | 42237.21 | 133145.33
New Construction | CZ01 | cDXHP | Cooling | 46331.34 | 0
New Construction | CZ01 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ01 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ01 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXHP | Fans | 309947.52 | 0
New Construction | CZ01 | cDXHP | Pumps | 71.05 | 0
New Construction | CZ01 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXHP | Humidification | 0 | 0
New Construction | CZ01 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXHP | Water Systems | 0 | 469136.72
New Construction | CZ01 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ01 | cDXHP | Generators | 0 | 0
New Construction | CZ01 | cDXHP | Total End Uses | 1714290.92 | 827137.82
New Construction | CZ02 | cDXHP | Heating | 27519.47 | 79471.6
New Construction | CZ02 | cDXHP | Cooling | 186086.41 | 0
New Construction | CZ02 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ02 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ02 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXHP | Fans | 344131.59 | 0
New Construction | CZ02 | cDXHP | Pumps | 110.57 | 0
New Construction | CZ02 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXHP | Humidification | 0 | 0
New Construction | CZ02 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXHP | Water Systems | 0 | 431091.78
New Construction | CZ02 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ02 | cDXHP | Generators | 0 | 0
New Construction | CZ02 | cDXHP | Total End Uses | 1873551.85 | 735419.16
New Construction | CZ03 | cDXHP | Heating | 17042.74 | 55808.7
New Construction | CZ03 | cDXHP | Cooling | 127915.03 | 0
New Construction | CZ03 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ03 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ03 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXHP | Fans | 331920.81 | 0
New Construction | CZ03 | cDXHP | Pumps | 76.78 | 0
New Construction | CZ03 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXHP | Humidification | 0 | 0
New Construction | CZ03 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXHP | Water Systems | 0 | 429405.49
New Construction | CZ03 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ03 | cDXHP | Generators | 0 | 0
New Construction | CZ03 | cDXHP | Total End Uses | 1792659.16 | 710069.98
New Construction | CZ04 | cDXHP | Heating | 13101.39 | 35073.26
New Construction | CZ04 | cDXHP | Cooling | 221794.08 | 0
New Construction | CZ04 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ04 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ04 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXHP | Fans | 351003.84 | 0
New Construction | CZ04 | cDXHP | Pumps | 97.64 | 0
New Construction | CZ04 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXHP | Humidification | 0 | 0
New Construction | CZ04 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXHP | Water Systems | 0 | 414707.07
New Construction | CZ04 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ04 | cDXHP | Generators | 0 | 0
New Construction | CZ04 | cDXHP | Total End Uses | 1901700.74 | 674636.11
New Construction | CZ05 | cDXHP | Heating | 18206.84 | 55995.13
New Construction | CZ05 | cDXHP | Cooling | 161698.21 | 0
New Construction | CZ05 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ05 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ05 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXHP | Fans | 334966.56 | 0
New Construction | CZ05 | cDXHP | Pumps | 108.51 | 0
New Construction | CZ05 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXHP | Humidification | 0 | 0
New Construction | CZ05 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXHP | Water Systems | 0 | 429482.17
New Construction | CZ05 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ05 | cDXHP | Generators | 0 | 0
New Construction | CZ05 | cDXHP | Total End Uses | 1830683.92 | 710333.07
New Construction | CZ06 | cDXHP | Heating | 3236.73 | 18870.99
New Construction | CZ06 | cDXHP | Cooling | 258954.37 | 0
New Construction | CZ06 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ06 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ06 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXHP | Fans | 353845.17 | 0
New Construction | CZ06 | cDXHP | Pumps | 131.44 | 0
New Construction | CZ06 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXHP | Humidification | 0 | 0
New Construction | CZ06 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXHP | Water Systems | 0 | 395629
New Construction | CZ06 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ06 | cDXHP | Generators | 0 | 0
New Construction | CZ06 | cDXHP | Total End Uses | 1931871.51 | 639355.78
New Construction | CZ07 | cDXHP | Heating | 2894.87 | 15817.68
New Construction | CZ07 | cDXHP | Cooling | 270465.95 | 0
New Construction | CZ07 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ07 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ07 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXHP | Fans | 352324.98 | 0
New Construction | CZ07 | cDXHP | Pumps | 74.47 | 0
New Construction | CZ07 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXHP | Humidification | 0 | 0
New Construction | CZ07 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXHP | Water Systems | 0 | 390526.89
New Construction | CZ07 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ07 | cDXHP | Generators | 0 | 0
New Construction | CZ07 | cDXHP | Total End Uses | 1941464.07 | 631200.34
New Construction | CZ08 | cDXHP | Heating | 4989.43 | 28560.86
New Construction | CZ08 | cDXHP | Cooling | 310821.66 | 0
New Construction | CZ08 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ08 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ08 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXHP | Fans | 371043.66 | 0
New Construction | CZ08 | cDXHP | Pumps | 104.02 | 0
New Construction | CZ08 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXHP | Humidification | 0 | 0
New Construction | CZ08 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXHP | Water Systems | 0 | 390031.99
New Construction | CZ08 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ08 | cDXHP | Generators | 0 | 0
New Construction | CZ08 | cDXHP | Total End Uses | 2002662.57 | 643448.63
New Construction | CZ09 | cDXHP | Heating | 3368.3 | 22855.96
New Construction | CZ09 | cDXHP | Cooling | 333389.76 | 0
New Construction | CZ09 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ09 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ09 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXHP | Fans | 370395.46 | 0
New Construction | CZ09 | cDXHP | Pumps | 97.08 | 0
New Construction | CZ09 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXHP | Humidification | 0 | 0
New Construction | CZ09 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXHP | Water Systems | 0 | 384581.12
New Construction | CZ09 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ09 | cDXHP | Generators | 0 | 0
New Construction | CZ09 | cDXHP | Total End Uses | 2022954.4 | 632292.86
New Construction | CZ10 | cDXHP | Heating | 10172.84 | 33838.06
New Construction | CZ10 | cDXHP | Cooling | 415951.06 | 0
New Construction | CZ10 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ10 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ10 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXHP | Fans | 399755.05 | 0
New Construction | CZ10 | cDXHP | Pumps | 104.03 | 0
New Construction | CZ10 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXHP | Humidification | 0 | 0
New Construction | CZ10 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXHP | Water Systems | 0 | 381514.6
New Construction | CZ10 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ10 | cDXHP | Generators | 0 | 0
New Construction | CZ10 | cDXHP | Total End Uses | 2141686.78 | 640208.43
New Construction | CZ11 | cDXHP | Heating | 24531.71 | 103891.32
New Construction | CZ11 | cDXHP | Cooling | 426086.59 | 0
New Construction | CZ11 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ11 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ11 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXHP | Fans | 393778.03 | 0
New Construction | CZ11 | cDXHP | Pumps | 148.88 | 0
New Construction | CZ11 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXHP | Humidification | 0 | 0
New Construction | CZ11 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXHP | Water Systems | 0 | 389974.19
New Construction | CZ11 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ11 | cDXHP | Generators | 0 | 0
New Construction | CZ11 | cDXHP | Total End Uses | 2160249 | 718721.28
New Construction | CZ12 | cDXHP | Heating | 25330.19 | 90604.24
New Construction | CZ12 | cDXHP | Cooling | 353281.3 | 0
New Construction | CZ12 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ12 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ12 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXHP | Fans | 373668.51 | 0
New Construction | CZ12 | cDXHP | Pumps | 126.34 | 0
New Construction | CZ12 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXHP | Humidification | 0 | 0
New Construction | CZ12 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXHP | Water Systems | 0 | 400951.53
New Construction | CZ12 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ12 | cDXHP | Generators | 0 | 0
New Construction | CZ12 | cDXHP | Total End Uses | 2068110.14 | 716411.55
New Construction | CZ13 | cDXHP | Heating | 19757.2 | 79531.09
New Construction | CZ13 | cDXHP | Cooling | 473605.8 | 0
New Construction | CZ13 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ13 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ13 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXHP | Fans | 400709.21 | 0
New Construction | CZ13 | cDXHP | Pumps | 147.96 | 0
New Construction | CZ13 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXHP | Humidification | 0 | 0
New Construction | CZ13 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXHP | Water Systems | 0 | 378730.43
New Construction | CZ13 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ13 | cDXHP | Generators | 0 | 0
New Construction | CZ13 | cDXHP | Total End Uses | 2209923.97 | 683117.3
New Construction | CZ14 | cDXHP | Heating | 13441.48 | 86325.41
New Construction | CZ14 | cDXHP | Cooling | 603366.98 | 0
New Construction | CZ14 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ14 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ14 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXHP | Fans | 437822.42 | 0
New Construction | CZ14 | cDXHP | Pumps | 179.04 | 0
New Construction | CZ14 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXHP | Humidification | 0 | 0
New Construction | CZ14 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXHP | Water Systems | 0 | 359403.05
New Construction | CZ14 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ14 | cDXHP | Generators | 0 | 0
New Construction | CZ14 | cDXHP | Total End Uses | 2370513.71 | 670584.24
New Construction | CZ15 | cDXHP | Heating | 4368.72 | 72547.3
New Construction | CZ15 | cDXHP | Cooling | 837064.24 | 0
New Construction | CZ15 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ15 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ15 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXHP | Fans | 432254.64 | 0
New Construction | CZ15 | cDXHP | Pumps | 267.76 | 0
New Construction | CZ15 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXHP | Humidification | 0 | 0
New Construction | CZ15 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXHP | Water Systems | 0 | 319087.29
New Construction | CZ15 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ15 | cDXHP | Generators | 0 | 0
New Construction | CZ15 | cDXHP | Total End Uses | 2589659.16 | 616490.37
New Construction | CZ16 | cDXHP | Heating | 52702.67 | 188762.55
New Construction | CZ16 | cDXHP | Cooling | 385955.26 | 0
New Construction | CZ16 | cDXHP | Interior Lighting | 352669.87 | 0
New Construction | CZ16 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXHP | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ16 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXHP | Fans | 446420.32 | 0
New Construction | CZ16 | cDXHP | Pumps | 147.33 | 0
New Construction | CZ16 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXHP | Humidification | 0 | 0
New Construction | CZ16 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXHP | Water Systems | 0 | 423991.21
New Construction | CZ16 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ16 | cDXHP | Generators | 0 | 0
New Construction | CZ16 | cDXHP | Total End Uses | 2200929.38 | 837609.54
Existing | CZ01 | cDXOH | Heating | 0 | 269182.92
Existing | CZ01 | cDXOH | Cooling | 67221.89 | 0
Existing | CZ01 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ01 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ01 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXOH | Fans | 418948.33 | 0
Existing | CZ01 | cDXOH | Pumps | 99.25 | 0
Existing | CZ01 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ01 | cDXOH | Humidification | 0 | 0
Existing | CZ01 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ01 | cDXOH | Water Systems | 0 | 469377.78
Existing | CZ01 | cDXOH | Refrigeration | 0 | 0
Existing | CZ01 | cDXOH | Generators | 0 | 0
Existing | CZ01 | cDXOH | Total End Uses | 2136373.99 | 963416.48
Existing | CZ02 | cDXOH | Heating | 0 | 187495.27
Existing | CZ02 | cDXOH | Cooling | 266245.33 | 0
Existing | CZ02 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ02 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ02 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXOH | Fans | 499016.24 | 0
Existing | CZ02 | cDXOH | Pumps | 81.85 | 0
Existing | CZ02 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ02 | cDXOH | Humidification | 0 | 0
Existing | CZ02 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ02 | cDXOH | Water Systems | 0 | 431329.66
Existing | CZ02 | cDXOH | Refrigeration | 0 | 0
Existing | CZ02 | cDXOH | Generators | 0 | 0
Existing | CZ02 | cDXOH | Total End Uses | 2415447.94 | 843680.7
Existing | CZ03 | cDXOH | Heating | 0 | 103648.23
Existing | CZ03 | cDXOH | Cooling | 204525.09 | 0
Existing | CZ03 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ03 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ03 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXOH | Fans | 478912.74 | 0
Existing | CZ03 | cDXOH | Pumps | 81.14 | 0
Existing | CZ03 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ03 | cDXOH | Humidification | 0 | 0
Existing | CZ03 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ03 | cDXOH | Water Systems | 0 | 429656.42
Existing | CZ03 | cDXOH | Refrigeration | 0 | 0
Existing | CZ03 | cDXOH | Generators | 0 | 0
Existing | CZ03 | cDXOH | Total End Uses | 2333623.49 | 758160.43
Existing | CZ04 | cDXOH | Heating | 0 | 81085.64
Existing | CZ04 | cDXOH | Cooling | 315588.78 | 0
Existing | CZ04 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ04 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ04 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXOH | Fans | 513130.05 | 0
Existing | CZ04 | cDXOH | Pumps | 49.75 | 0
Existing | CZ04 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ04 | cDXOH | Humidification | 0 | 0
Existing | CZ04 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ04 | cDXOH | Water Systems | 0 | 414905.14
Existing | CZ04 | cDXOH | Refrigeration | 0 | 0
Existing | CZ04 | cDXOH | Generators | 0 | 0
Existing | CZ04 | cDXOH | Total End Uses | 2478873.11 | 720846.56
Existing | CZ05 | cDXOH | Heating | 0 | 90654.41
Existing | CZ05 | cDXOH | Cooling | 257239.45 | 0
Existing | CZ05 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ05 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ05 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXOH | Fans | 485374.52 | 0
Existing | CZ05 | cDXOH | Pumps | 119.1 | 0
Existing | CZ05 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ05 | cDXOH | Humidification | 0 | 0
Existing | CZ05 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ05 | cDXOH | Water Systems | 0 | 429680.15
Existing | CZ05 | cDXOH | Refrigeration | 0 | 0
Existing | CZ05 | cDXOH | Generators | 0 | 0
Existing | CZ05 | cDXOH | Total End Uses | 2392837.59 | 745190.33
Existing | CZ06 | cDXOH | Heating | 0 | 40338.08
Existing | CZ06 | cDXOH | Cooling | 408234.26 | 0
Existing | CZ06 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ06 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ06 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXOH | Fans | 517747.7 | 0
Existing | CZ06 | cDXOH | Pumps | 134.6 | 0
Existing | CZ06 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ06 | cDXOH | Humidification | 0 | 0
Existing | CZ06 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ06 | cDXOH | Water Systems | 0 | 395856.7
Existing | CZ06 | cDXOH | Refrigeration | 0 | 0
Existing | CZ06 | cDXOH | Generators | 0 | 0
Existing | CZ06 | cDXOH | Total End Uses | 2576221.08 | 661050.56
Existing | CZ07 | cDXOH | Heating | 0 | 22453.45
Existing | CZ07 | cDXOH | Cooling | 409302.36 | 0
Existing | CZ07 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ07 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ07 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXOH | Fans | 505332.35 | 0
Existing | CZ07 | cDXOH | Pumps | 75.2 | 0
Existing | CZ07 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ07 | cDXOH | Humidification | 0 | 0
Existing | CZ07 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ07 | cDXOH | Water Systems | 0 | 390797.12
Existing | CZ07 | cDXOH | Refrigeration | 0 | 0
Existing | CZ07 | cDXOH | Generators | 0 | 0
Existing | CZ07 | cDXOH | Total End Uses | 2564814.43 | 638106.35
Existing | CZ08 | cDXOH | Heating | 0 | 42710.29
Existing | CZ08 | cDXOH | Cooling | 444896.7 | 0
Existing | CZ08 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ08 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ08 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXOH | Fans | 537404.17 | 0
Existing | CZ08 | cDXOH | Pumps | 61.75 | 0
Existing | CZ08 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ08 | cDXOH | Humidification | 0 | 0
Existing | CZ08 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ08 | cDXOH | Water Systems | 0 | 390221.74
Existing | CZ08 | cDXOH | Refrigeration | 0 | 0
Existing | CZ08 | cDXOH | Generators | 0 | 0
Existing | CZ08 | cDXOH | Total End Uses | 2632467.14 | 657787.8
Existing | CZ09 | cDXOH | Heating | 0 | 45063.27
Existing | CZ09 | cDXOH | Cooling | 504206.79 | 0
Existing | CZ09 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ09 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ09 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXOH | Fans | 563467.51 | 0
Existing | CZ09 | cDXOH | Pumps | 66.68 | 0
Existing | CZ09 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ09 | cDXOH | Humidification | 0 | 0
Existing | CZ09 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ09 | cDXOH | Water Systems | 0 | 384836.27
Existing | CZ09 | cDXOH | Refrigeration | 0 | 0
Existing | CZ09 | cDXOH | Generators | 0 | 0
Existing | CZ09 | cDXOH | Total End Uses | 2717845.5 | 654755.32
Existing | CZ10 | cDXOH | Heating | 0 | 58258.55
Existing | CZ10 | cDXOH | Cooling | 570460.99 | 0
Existing | CZ10 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ10 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ10 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXOH | Fans | 569690.76 | 0
Existing | CZ10 | cDXOH | Pumps | 70.78 | 0
Existing | CZ10 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ10 | cDXOH | Humidification | 0 | 0
Existing | CZ10 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ10 | cDXOH | Water Systems | 0 | 381742.21
Existing | CZ10 | cDXOH | Refrigeration | 0 | 0
Existing | CZ10 | cDXOH | Generators | 0 | 0
Existing | CZ10 | cDXOH | Total End Uses | 2790327.05 | 664856.54
Existing | CZ11 | cDXOH | Heating | 0 | 233054.39
Existing | CZ11 | cDXOH | Cooling | 603320.98 | 0
Existing | CZ11 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ11 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ11 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXOH | Fans | 590878.14 | 0
Existing | CZ11 | cDXOH | Pumps | 103.79 | 0
Existing | CZ11 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ11 | cDXOH | Humidification | 0 | 0
Existing | CZ11 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ11 | cDXOH | Water Systems | 0 | 390232.75
Existing | CZ11 | cDXOH | Refrigeration | 0 | 0
Existing | CZ11 | cDXOH | Generators | 0 | 0
Existing | CZ11 | cDXOH | Total End Uses | 2844407.44 | 848142.92
Existing | CZ12 | cDXOH | Heating | 0 | 188096.99
Existing | CZ12 | cDXOH | Cooling | 497405.27 | 0
Existing | CZ12 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ12 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ12 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXOH | Fans | 545385.2 | 0
Existing | CZ12 | cDXOH | Pumps | 91 | 0
Existing | CZ12 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ12 | cDXOH | Humidification | 0 | 0
Existing | CZ12 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ12 | cDXOH | Water Systems | 0 | 401213.42
Existing | CZ12 | cDXOH | Refrigeration | 0 | 0
Existing | CZ12 | cDXOH | Generators | 0 | 0
Existing | CZ12 | cDXOH | Total End Uses | 2692986 | 814166.19
Existing | CZ13 | cDXOH | Heating | 0 | 159312.28
Existing | CZ13 | cDXOH | Cooling | 666225.84 | 0
Existing | CZ13 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ13 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ13 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXOH | Fans | 591250.16 | 0
Existing | CZ13 | cDXOH | Pumps | 87.25 | 0
Existing | CZ13 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ13 | cDXOH | Humidification | 0 | 0
Existing | CZ13 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ13 | cDXOH | Water Systems | 0 | 378891.69
Existing | CZ13 | cDXOH | Refrigeration | 0 | 0
Existing | CZ13 | cDXOH | Generators | 0 | 0
Existing | CZ13 | cDXOH | Total End Uses | 2907667.78 | 763059.74
Existing | CZ14 | cDXOH | Heating | 0 | 113880.06
Existing | CZ14 | cDXOH | Cooling | 820510.87 | 0
Existing | CZ14 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ14 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ14 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXOH | Fans | 651315.79 | 0
Existing | CZ14 | cDXOH | Pumps | 79.92 | 0
Existing | CZ14 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ14 | cDXOH | Humidification | 0 | 0
Existing | CZ14 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ14 | cDXOH | Water Systems | 0 | 359701.01
Existing | CZ14 | cDXOH | Refrigeration | 0 | 0
Existing | CZ14 | cDXOH | Generators | 0 | 0
Existing | CZ14 | cDXOH | Total End Uses | 3122011.1 | 698436.85
Existing | CZ15 | cDXOH | Heating | 0 | 66578.85
Existing | CZ15 | cDXOH | Cooling | 1128885.28 | 0
Existing | CZ15 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ15 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ15 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXOH | Fans | 659333.98 | 0
Existing | CZ15 | cDXOH | Pumps | 112.14 | 0
Existing | CZ15 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ15 | cDXOH | Humidification | 0 | 0
Existing | CZ15 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ15 | cDXOH | Water Systems | 0 | 319324.28
Existing | CZ15 | cDXOH | Refrigeration | 0 | 0
Existing | CZ15 | cDXOH | Generators | 0 | 0
Existing | CZ15 | cDXOH | Total End Uses | 3438435.92 | 610758.91
Existing | CZ16 | cDXOH | Heating | 0 | 326887.38
Existing | CZ16 | cDXOH | Cooling | 529538.53 | 0
Existing | CZ16 | cDXOH | Interior Lighting | 687070.6 | 0
Existing | CZ16 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXOH | Interior Equipment | 963033.93 | 224855.78
Existing | CZ16 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXOH | Fans | 646493.65 | 0
Existing | CZ16 | cDXOH | Pumps | 120.03 | 0
Existing | CZ16 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ16 | cDXOH | Humidification | 0 | 0
Existing | CZ16 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ16 | cDXOH | Water Systems | 0 | 424215.76
Existing | CZ16 | cDXOH | Refrigeration | 0 | 0
Existing | CZ16 | cDXOH | Generators | 0 | 0
Existing | CZ16 | cDXOH | Total End Uses | 2826256.73 | 975958.93
New Construction | CZ01 | cDXOH | Heating | 0 | 169191.41
New Construction | CZ01 | cDXOH | Cooling | 45304.1 | 0
New Construction | CZ01 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ01 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ01 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXOH | Fans | 311162.5 | 0
New Construction | CZ01 | cDXOH | Pumps | 78.02 | 0
New Construction | CZ01 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXOH | Humidification | 0 | 0
New Construction | CZ01 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXOH | Water Systems | 0 | 469165.12
New Construction | CZ01 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ01 | cDXOH | Generators | 0 | 0
New Construction | CZ01 | cDXOH | Total End Uses | 1672248.41 | 863212.32
New Construction | CZ02 | cDXOH | Heating | 0 | 99209.28
New Construction | CZ02 | cDXOH | Cooling | 185053.85 | 0
New Construction | CZ02 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ02 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ02 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXOH | Fans | 344261.44 | 0
New Construction | CZ02 | cDXOH | Pumps | 118.25 | 0
New Construction | CZ02 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXOH | Humidification | 0 | 0
New Construction | CZ02 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXOH | Water Systems | 0 | 431048.37
New Construction | CZ02 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ02 | cDXOH | Generators | 0 | 0
New Construction | CZ02 | cDXOH | Total End Uses | 1845137.33 | 755113.43
New Construction | CZ03 | cDXOH | Heating | 0 | 68797.36
New Construction | CZ03 | cDXOH | Cooling | 127627.51 | 0
New Construction | CZ03 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ03 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ03 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXOH | Fans | 332190.76 | 0
New Construction | CZ03 | cDXOH | Pumps | 78.74 | 0
New Construction | CZ03 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXOH | Humidification | 0 | 0
New Construction | CZ03 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXOH | Water Systems | 0 | 429462.31
New Construction | CZ03 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ03 | cDXOH | Generators | 0 | 0
New Construction | CZ03 | cDXOH | Total End Uses | 1775600.81 | 723115.45
New Construction | CZ04 | cDXOH | Heating | 0 | 39096.85
New Construction | CZ04 | cDXOH | Cooling | 220824.58 | 0
New Construction | CZ04 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ04 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ04 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXOH | Fans | 350458.35 | 0
New Construction | CZ04 | cDXOH | Pumps | 98.03 | 0
New Construction | CZ04 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXOH | Humidification | 0 | 0
New Construction | CZ04 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXOH | Water Systems | 0 | 414703.25
New Construction | CZ04 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ04 | cDXOH | Generators | 0 | 0
New Construction | CZ04 | cDXOH | Total End Uses | 1887084.76 | 678655.88
New Construction | CZ05 | cDXOH | Heating | 0 | 63603.55
New Construction | CZ05 | cDXOH | Cooling | 160190.66 | 0
New Construction | CZ05 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ05 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ05 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXOH | Fans | 334515.85 | 0
New Construction | CZ05 | cDXOH | Pumps | 110.22 | 0
New Construction | CZ05 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXOH | Humidification | 0 | 0
New Construction | CZ05 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXOH | Water Systems | 0 | 429418.18
New Construction | CZ05 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ05 | cDXOH | Generators | 0 | 0
New Construction | CZ05 | cDXOH | Total End Uses | 1810520.53 | 717877.51
New Construction | CZ06 | cDXOH | Heating | 0 | 19683.59
New Construction | CZ06 | cDXOH | Cooling | 261837.26 | 0
New Construction | CZ06 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ06 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ06 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXOH | Fans | 353525.45 | 0
New Construction | CZ06 | cDXOH | Pumps | 130.88 | 0
New Construction | CZ06 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXOH | Humidification | 0 | 0
New Construction | CZ06 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXOH | Water Systems | 0 | 395573.68
New Construction | CZ06 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ06 | cDXOH | Generators | 0 | 0
New Construction | CZ06 | cDXOH | Total End Uses | 1931197.38 | 640113.05
New Construction | CZ07 | cDXOH | Heating | 0 | 16962.53
New Construction | CZ07 | cDXOH | Cooling | 272510.45 | 0
New Construction | CZ07 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ07 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ07 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXOH | Fans | 352460.54 | 0
New Construction | CZ07 | cDXOH | Pumps | 74.95 | 0
New Construction | CZ07 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXOH | Humidification | 0 | 0
New Construction | CZ07 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXOH | Water Systems | 0 | 390532.69
New Construction | CZ07 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ07 | cDXOH | Generators | 0 | 0
New Construction | CZ07 | cDXOH | Total End Uses | 1940749.74 | 632351
New Construction | CZ08 | cDXOH | Heating | 0 | 30367.39
New Construction | CZ08 | cDXOH | Cooling | 311360.43 | 0
New Construction | CZ08 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ08 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ08 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXOH | Fans | 370847.35 | 0
New Construction | CZ08 | cDXOH | Pumps | 106.14 | 0
New Construction | CZ08 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXOH | Humidification | 0 | 0
New Construction | CZ08 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXOH | Water Systems | 0 | 390033.24
New Construction | CZ08 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ08 | cDXOH | Generators | 0 | 0
New Construction | CZ08 | cDXOH | Total End Uses | 1998017.71 | 645256.4
New Construction | CZ09 | cDXOH | Heating | 0 | 23687.93
New Construction | CZ09 | cDXOH | Cooling | 333941.13 | 0
New Construction | CZ09 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ09 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ09 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXOH | Fans | 370048.53 | 0
New Construction | CZ09 | cDXOH | Pumps | 98.74 | 0
New Construction | CZ09 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXOH | Humidification | 0 | 0
New Construction | CZ09 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXOH | Water Systems | 0 | 384566.08
New Construction | CZ09 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ09 | cDXOH | Generators | 0 | 0
New Construction | CZ09 | cDXOH | Total End Uses | 2019792.21 | 633109.79
New Construction | CZ10 | cDXOH | Heating | 0 | 38128.57
New Construction | CZ10 | cDXOH | Cooling | 415563.25 | 0
New Construction | CZ10 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ10 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ10 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXOH | Fans | 399336.64 | 0
New Construction | CZ10 | cDXOH | Pumps | 105.79 | 0
New Construction | CZ10 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXOH | Humidification | 0 | 0
New Construction | CZ10 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXOH | Water Systems | 0 | 381508.75
New Construction | CZ10 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ10 | cDXOH | Generators | 0 | 0
New Construction | CZ10 | cDXOH | Total End Uses | 2130709.47 | 644493.1
New Construction | CZ11 | cDXOH | Heating | 0 | 125530.71
New Construction | CZ11 | cDXOH | Cooling | 425211.17 | 0
New Construction | CZ11 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ11 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ11 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXOH | Fans | 394563.79 | 0
New Construction | CZ11 | cDXOH | Pumps | 152.46 | 0
New Construction | CZ11 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXOH | Humidification | 0 | 0
New Construction | CZ11 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXOH | Water Systems | 0 | 389951.48
New Construction | CZ11 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ11 | cDXOH | Generators | 0 | 0
New Construction | CZ11 | cDXOH | Total End Uses | 2135631.21 | 740337.97
New Construction | CZ12 | cDXOH | Heating | 0 | 112327.72
New Construction | CZ12 | cDXOH | Cooling | 352445.51 | 0
New Construction | CZ12 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ12 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ12 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXOH | Fans | 374398.39 | 0
New Construction | CZ12 | cDXOH | Pumps | 130.24 | 0
New Construction | CZ12 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXOH | Humidification | 0 | 0
New Construction | CZ12 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXOH | Water Systems | 0 | 400954.17
New Construction | CZ12 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ12 | cDXOH | Generators | 0 | 0
New Construction | CZ12 | cDXOH | Total End Uses | 2042677.95 | 738137.66
New Construction | CZ13 | cDXOH | Heating | 0 | 97540.3
New Construction | CZ13 | cDXOH | Cooling | 472892.06 | 0
New Construction | CZ13 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ13 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ13 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXOH | Fans | 401403.15 | 0
New Construction | CZ13 | cDXOH | Pumps | 151.77 | 0
New Construction | CZ13 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXOH | Humidification | 0 | 0
New Construction | CZ13 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXOH | Water Systems | 0 | 378712.7
New Construction | CZ13 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ13 | cDXOH | Generators | 0 | 0
New Construction | CZ13 | cDXOH | Total End Uses | 2190150.77 | 701108.78
New Construction | CZ14 | cDXOH | Heating | 0 | 93259.17
New Construction | CZ14 | cDXOH | Cooling | 601859.14 | 0
New Construction | CZ14 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ14 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ14 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXOH | Fans | 437661.37 | 0
New Construction | CZ14 | cDXOH | Pumps | 178.46 | 0
New Construction | CZ14 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXOH | Humidification | 0 | 0
New Construction | CZ14 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXOH | Water Systems | 0 | 359401.06
New Construction | CZ14 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ14 | cDXOH | Generators | 0 | 0
New Construction | CZ14 | cDXOH | Total End Uses | 2355402.77 | 677516.01
New Construction | CZ15 | cDXOH | Heating | 0 | 72693.47
New Construction | CZ15 | cDXOH | Cooling | 836066.18 | 0
New Construction | CZ15 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ15 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ15 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXOH | Fans | 431843.55 | 0
New Construction | CZ15 | cDXOH | Pumps | 269.25 | 0
New Construction | CZ15 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXOH | Humidification | 0 | 0
New Construction | CZ15 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXOH | Water Systems | 0 | 319089.54
New Construction | CZ15 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ15 | cDXOH | Generators | 0 | 0
New Construction | CZ15 | cDXOH | Total End Uses | 2583882.78 | 616638.79
New Construction | CZ16 | cDXOH | Heating | 0 | 221608.94
New Construction | CZ16 | cDXOH | Cooling | 384268.55 | 0
New Construction | CZ16 | cDXOH | Interior Lighting | 352669.87 | 0
New Construction | CZ16 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXOH | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ16 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXOH | Fans | 447536.86 | 0
New Construction | CZ16 | cDXOH | Pumps | 150.16 | 0
New Construction | CZ16 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXOH | Humidification | 0 | 0
New Construction | CZ16 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXOH | Water Systems | 0 | 424062.78
New Construction | CZ16 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ16 | cDXOH | Generators | 0 | 0
New Construction | CZ16 | cDXOH | Total End Uses | 2147659.38 | 870527.51
Existing | CZ01 | cPVVG | Heating | 0 | 449209.09
Existing | CZ01 | cPVVG | Cooling | 69703.82 | 0
Existing | CZ01 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ01 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ01 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ01 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ01 | cPVVG | Fans | 228922.38 | 0
Existing | CZ01 | cPVVG | Pumps | 95.15 | 0
Existing | CZ01 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ01 | cPVVG | Humidification | 0 | 0
Existing | CZ01 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ01 | cPVVG | Water Systems | 0 | 469372.93
Existing | CZ01 | cPVVG | Refrigeration | 0 | 0
Existing | CZ01 | cPVVG | Generators | 0 | 0
Existing | CZ01 | cPVVG | Total End Uses | 1948825.87 | 1143437.8
Existing | CZ02 | cPVVG | Heating | 0 | 301168
Existing | CZ02 | cPVVG | Cooling | 264742.13 | 0
Existing | CZ02 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ02 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ02 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ02 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ02 | cPVVG | Fans | 299145.74 | 0
Existing | CZ02 | cPVVG | Pumps | 79.83 | 0
Existing | CZ02 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ02 | cPVVG | Humidification | 0 | 0
Existing | CZ02 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ02 | cPVVG | Water Systems | 0 | 431330.06
Existing | CZ02 | cPVVG | Refrigeration | 0 | 0
Existing | CZ02 | cPVVG | Generators | 0 | 0
Existing | CZ02 | cPVVG | Total End Uses | 2214072.23 | 957353.83
Existing | CZ03 | cPVVG | Heating | 0 | 173367.7
Existing | CZ03 | cPVVG | Cooling | 208970 | 0
Existing | CZ03 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ03 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ03 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ03 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ03 | cPVVG | Fans | 281081.53 | 0
Existing | CZ03 | cPVVG | Pumps | 80.48 | 0
Existing | CZ03 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ03 | cPVVG | Humidification | 0 | 0
Existing | CZ03 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ03 | cPVVG | Water Systems | 0 | 429645.67
Existing | CZ03 | cPVVG | Refrigeration | 0 | 0
Existing | CZ03 | cPVVG | Generators | 0 | 0
Existing | CZ03 | cPVVG | Total End Uses | 2140236.54 | 827869.15
Existing | CZ04 | cPVVG | Heating | 0 | 143924.87
Existing | CZ04 | cPVVG | Cooling | 314362.52 | 0
Existing | CZ04 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ04 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ04 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ04 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ04 | cPVVG | Fans | 315637.09 | 0
Existing | CZ04 | cPVVG | Pumps | 49.34 | 0
Existing | CZ04 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ04 | cPVVG | Humidification | 0 | 0
Existing | CZ04 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ04 | cPVVG | Water Systems | 0 | 414894.18
Existing | CZ04 | cPVVG | Refrigeration | 0 | 0
Existing | CZ04 | cPVVG | Generators | 0 | 0
Existing | CZ04 | cPVVG | Total End Uses | 2280153.47 | 783674.83
Existing | CZ05 | cPVVG | Heating | 0 | 159438.53
Existing | CZ05 | cPVVG | Cooling | 260422.69 | 0
Existing | CZ05 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ05 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ05 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ05 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ05 | cPVVG | Fans | 296486.59 | 0
Existing | CZ05 | cPVVG | Pumps | 119.19 | 0
Existing | CZ05 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ05 | cPVVG | Humidification | 0 | 0
Existing | CZ05 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ05 | cPVVG | Water Systems | 0 | 429663.64
Existing | CZ05 | cPVVG | Refrigeration | 0 | 0
Existing | CZ05 | cPVVG | Generators | 0 | 0
Existing | CZ05 | cPVVG | Total End Uses | 2207133 | 813957.95
Existing | CZ06 | cPVVG | Heating | 0 | 55027.19
Existing | CZ06 | cPVVG | Cooling | 412865.19 | 0
Existing | CZ06 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ06 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ06 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ06 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ06 | cPVVG | Fans | 338655.74 | 0
Existing | CZ06 | cPVVG | Pumps | 135.06 | 0
Existing | CZ06 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ06 | cPVVG | Humidification | 0 | 0
Existing | CZ06 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ06 | cPVVG | Water Systems | 0 | 395862.52
Existing | CZ06 | cPVVG | Refrigeration | 0 | 0
Existing | CZ06 | cPVVG | Generators | 0 | 0
Existing | CZ06 | cPVVG | Total End Uses | 2401760.52 | 675745.49
Existing | CZ07 | cPVVG | Heating | 0 | 33876.18
Existing | CZ07 | cPVVG | Cooling | 408875.48 | 0
Existing | CZ07 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ07 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ07 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ07 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ07 | cPVVG | Fans | 331820.82 | 0
Existing | CZ07 | cPVVG | Pumps | 75.73 | 0
Existing | CZ07 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ07 | cPVVG | Humidification | 0 | 0
Existing | CZ07 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ07 | cPVVG | Water Systems | 0 | 390807.62
Existing | CZ07 | cPVVG | Refrigeration | 0 | 0
Existing | CZ07 | cPVVG | Generators | 0 | 0
Existing | CZ07 | cPVVG | Total End Uses | 2390876.56 | 649539.58
Existing | CZ08 | cPVVG | Heating | 0 | 64103.17
Existing | CZ08 | cPVVG | Cooling | 443346.51 | 0
Existing | CZ08 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ08 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ08 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ08 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ08 | cPVVG | Fans | 352589.22 | 0
Existing | CZ08 | cPVVG | Pumps | 62.05 | 0
Existing | CZ08 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ08 | cPVVG | Humidification | 0 | 0
Existing | CZ08 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ08 | cPVVG | Water Systems | 0 | 390240.27
Existing | CZ08 | cPVVG | Refrigeration | 0 | 0
Existing | CZ08 | cPVVG | Generators | 0 | 0
Existing | CZ08 | cPVVG | Total End Uses | 2446102.29 | 679199.22
Existing | CZ09 | cPVVG | Heating | 0 | 61380.24
Existing | CZ09 | cPVVG | Cooling | 499705.78 | 0
Existing | CZ09 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ09 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ09 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ09 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ09 | cPVVG | Fans | 377509.9 | 0
Existing | CZ09 | cPVVG | Pumps | 67.02 | 0
Existing | CZ09 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ09 | cPVVG | Humidification | 0 | 0
Existing | CZ09 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ09 | cPVVG | Water Systems | 0 | 384822.06
Existing | CZ09 | cPVVG | Refrigeration | 0 | 0
Existing | CZ09 | cPVVG | Generators | 0 | 0
Existing | CZ09 | cPVVG | Total End Uses | 2527387.22 | 671058.08
Existing | CZ10 | cPVVG | Heating | 0 | 101498.24
Existing | CZ10 | cPVVG | Cooling | 560690.69 | 0
Existing | CZ10 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ10 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ10 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ10 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ10 | cPVVG | Fans | 382640.81 | 0
Existing | CZ10 | cPVVG | Pumps | 70.55 | 0
Existing | CZ10 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ10 | cPVVG | Humidification | 0 | 0
Existing | CZ10 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ10 | cPVVG | Water Systems | 0 | 381716.88
Existing | CZ10 | cPVVG | Refrigeration | 0 | 0
Existing | CZ10 | cPVVG | Generators | 0 | 0
Existing | CZ10 | cPVVG | Total End Uses | 2593506.57 | 708070.9
Existing | CZ11 | cPVVG | Heating | 0 | 345366.42
Existing | CZ11 | cPVVG | Cooling | 592936.8 | 0
Existing | CZ11 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ11 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ11 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ11 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ11 | cPVVG | Fans | 394778.18 | 0
Existing | CZ11 | cPVVG | Pumps | 101.74 | 0
Existing | CZ11 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ11 | cPVVG | Humidification | 0 | 0
Existing | CZ11 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ11 | cPVVG | Water Systems | 0 | 390216.56
Existing | CZ11 | cPVVG | Refrigeration | 0 | 0
Existing | CZ11 | cPVVG | Generators | 0 | 0
Existing | CZ11 | cPVVG | Total End Uses | 2637921.24 | 960438.76
Existing | CZ12 | cPVVG | Heating | 0 | 293024.51
Existing | CZ12 | cPVVG | Cooling | 490332.6 | 0
Existing | CZ12 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ12 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ12 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ12 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ12 | cPVVG | Fans | 358314.25 | 0
Existing | CZ12 | cPVVG | Pumps | 89.14 | 0
Existing | CZ12 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ12 | cPVVG | Humidification | 0 | 0
Existing | CZ12 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ12 | cPVVG | Water Systems | 0 | 401215.38
Existing | CZ12 | cPVVG | Refrigeration | 0 | 0
Existing | CZ12 | cPVVG | Generators | 0 | 0
Existing | CZ12 | cPVVG | Total End Uses | 2498840.51 | 919095.67
Existing | CZ13 | cPVVG | Heating | 0 | 242931.49
Existing | CZ13 | cPVVG | Cooling | 655251.37 | 0
Existing | CZ13 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ13 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ13 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ13 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ13 | cPVVG | Fans | 405232.99 | 0
Existing | CZ13 | cPVVG | Pumps | 84.92 | 0
Existing | CZ13 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ13 | cPVVG | Humidification | 0 | 0
Existing | CZ13 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ13 | cPVVG | Water Systems | 0 | 378873.18
Existing | CZ13 | cPVVG | Refrigeration | 0 | 0
Existing | CZ13 | cPVVG | Generators | 0 | 0
Existing | CZ13 | cPVVG | Total End Uses | 2710673.8 | 846660.45
Existing | CZ14 | cPVVG | Heating | 0 | 171697.51
Existing | CZ14 | cPVVG | Cooling | 804993.81 | 0
Existing | CZ14 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ14 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ14 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ14 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ14 | cPVVG | Fans | 458941.75 | 0
Existing | CZ14 | cPVVG | Pumps | 79.5 | 0
Existing | CZ14 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ14 | cPVVG | Humidification | 0 | 0
Existing | CZ14 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ14 | cPVVG | Water Systems | 0 | 359702.55
Existing | CZ14 | cPVVG | Refrigeration | 0 | 0
Existing | CZ14 | cPVVG | Generators | 0 | 0
Existing | CZ14 | cPVVG | Total End Uses | 2914119.58 | 756255.84
Existing | CZ15 | cPVVG | Heating | 0 | 85184.49
Existing | CZ15 | cPVVG | Cooling | 1109377.01 | 0
Existing | CZ15 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ15 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ15 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ15 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ15 | cPVVG | Fans | 496180.55 | 0
Existing | CZ15 | cPVVG | Pumps | 112.15 | 0
Existing | CZ15 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ15 | cPVVG | Humidification | 0 | 0
Existing | CZ15 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ15 | cPVVG | Water Systems | 0 | 319386.66
Existing | CZ15 | cPVVG | Refrigeration | 0 | 0
Existing | CZ15 | cPVVG | Generators | 0 | 0
Existing | CZ15 | cPVVG | Total End Uses | 3255774.23 | 629426.93
Existing | CZ16 | cPVVG | Heating | 0 | 496058.36
Existing | CZ16 | cPVVG | Cooling | 519272.07 | 0
Existing | CZ16 | cPVVG | Interior Lighting | 687070.6 | 0
Existing | CZ16 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ16 | cPVVG | Interior Equipment | 963033.93 | 224855.78
Existing | CZ16 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ16 | cPVVG | Fans | 436513.5 | 0
Existing | CZ16 | cPVVG | Pumps | 115.28 | 0
Existing | CZ16 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ16 | cPVVG | Humidification | 0 | 0
Existing | CZ16 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ16 | cPVVG | Water Systems | 0 | 424227.9
Existing | CZ16 | cPVVG | Refrigeration | 0 | 0
Existing | CZ16 | cPVVG | Generators | 0 | 0
Existing | CZ16 | cPVVG | Total End Uses | 2606005.37 | 1145142.04
New Construction | CZ01 | cPVVG | Heating | 0 | 367594.81
New Construction | CZ01 | cPVVG | Cooling | 47316.98 | 0
New Construction | CZ01 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ01 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ01 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ01 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ01 | cPVVG | Fans | 184682.76 | 0
New Construction | CZ01 | cPVVG | Pumps | 72.82 | 0
New Construction | CZ01 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ01 | cPVVG | Humidification | 0 | 0
New Construction | CZ01 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ01 | cPVVG | Water Systems | 0 | 469172.87
New Construction | CZ01 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ01 | cPVVG | Generators | 0 | 0
New Construction | CZ01 | cPVVG | Total End Uses | 1547776.35 | 1061623.47
New Construction | CZ02 | cPVVG | Heating | 0 | 219881.08
New Construction | CZ02 | cPVVG | Cooling | 183879.86 | 0
New Construction | CZ02 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ02 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ02 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ02 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ02 | cPVVG | Fans | 208689.54 | 0
New Construction | CZ02 | cPVVG | Pumps | 110.46 | 0
New Construction | CZ02 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ02 | cPVVG | Humidification | 0 | 0
New Construction | CZ02 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ02 | cPVVG | Water Systems | 0 | 431109.19
New Construction | CZ02 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ02 | cPVVG | Generators | 0 | 0
New Construction | CZ02 | cPVVG | Total End Uses | 1708383.66 | 875846.05
New Construction | CZ03 | cPVVG | Heating | 0 | 157336.8
New Construction | CZ03 | cPVVG | Cooling | 129713.15 | 0
New Construction | CZ03 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ03 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ03 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ03 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ03 | cPVVG | Fans | 193469.65 | 0
New Construction | CZ03 | cPVVG | Pumps | 76.99 | 0
New Construction | CZ03 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ03 | cPVVG | Humidification | 0 | 0
New Construction | CZ03 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ03 | cPVVG | Water Systems | 0 | 429441.54
New Construction | CZ03 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ03 | cPVVG | Generators | 0 | 0
New Construction | CZ03 | cPVVG | Total End Uses | 1638963.59 | 811634.12
New Construction | CZ04 | cPVVG | Heating | 0 | 112454.05
New Construction | CZ04 | cPVVG | Cooling | 219173.19 | 0
New Construction | CZ04 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ04 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ04 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ04 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ04 | cPVVG | Fans | 215674.74 | 0
New Construction | CZ04 | cPVVG | Pumps | 98.09 | 0
New Construction | CZ04 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ04 | cPVVG | Humidification | 0 | 0
New Construction | CZ04 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ04 | cPVVG | Water Systems | 0 | 414688.98
New Construction | CZ04 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ04 | cPVVG | Generators | 0 | 0
New Construction | CZ04 | cPVVG | Total End Uses | 1750649.82 | 751998.81
New Construction | CZ05 | cPVVG | Heating | 0 | 155926.64
New Construction | CZ05 | cPVVG | Cooling | 161395.31 | 0
New Construction | CZ05 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ05 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ05 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ05 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ05 | cPVVG | Fans | 201590.57 | 0
New Construction | CZ05 | cPVVG | Pumps | 106.93 | 0
New Construction | CZ05 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ05 | cPVVG | Humidification | 0 | 0
New Construction | CZ05 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ05 | cPVVG | Water Systems | 0 | 429448.54
New Construction | CZ05 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ05 | cPVVG | Generators | 0 | 0
New Construction | CZ05 | cPVVG | Total End Uses | 1678796.61 | 810230.97
New Construction | CZ06 | cPVVG | Heating | 0 | 41743.79
New Construction | CZ06 | cPVVG | Cooling | 262400.87 | 0
New Construction | CZ06 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ06 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ06 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ06 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ06 | cPVVG | Fans | 223217.8 | 0
New Construction | CZ06 | cPVVG | Pumps | 131.2 | 0
New Construction | CZ06 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ06 | cPVVG | Humidification | 0 | 0
New Construction | CZ06 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ06 | cPVVG | Water Systems | 0 | 395612.24
New Construction | CZ06 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ06 | cPVVG | Generators | 0 | 0
New Construction | CZ06 | cPVVG | Total End Uses | 1801453.67 | 662211.81
New Construction | CZ07 | cPVVG | Heating | 0 | 36722.34
New Construction | CZ07 | cPVVG | Cooling | 269868.72 | 0
New Construction | CZ07 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ07 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ07 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ07 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ07 | cPVVG | Fans | 225596.46 | 0
New Construction | CZ07 | cPVVG | Pumps | 76.02 | 0
New Construction | CZ07 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ07 | cPVVG | Humidification | 0 | 0
New Construction | CZ07 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ07 | cPVVG | Water Systems | 0 | 390520.99
New Construction | CZ07 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ07 | cPVVG | Generators | 0 | 0
New Construction | CZ07 | cPVVG | Total End Uses | 1811245 | 652099.11
New Construction | CZ08 | cPVVG | Heating | 0 | 61507.68
New Construction | CZ08 | cPVVG | Cooling | 308261.07 | 0
New Construction | CZ08 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ08 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ08 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ08 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ08 | cPVVG | Fans | 237644.12 | 0
New Construction | CZ08 | cPVVG | Pumps | 104.73 | 0
New Construction | CZ08 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ08 | cPVVG | Humidification | 0 | 0
New Construction | CZ08 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ08 | cPVVG | Water Systems | 0 | 390041.3
New Construction | CZ08 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ08 | cPVVG | Generators | 0 | 0
New Construction | CZ08 | cPVVG | Total End Uses | 1861713.71 | 676404.76
New Construction | CZ09 | cPVVG | Heating | 0 | 46204.71
New Construction | CZ09 | cPVVG | Cooling | 329193.4 | 0
New Construction | CZ09 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ09 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ09 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ09 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ09 | cPVVG | Fans | 243352.55 | 0
New Construction | CZ09 | cPVVG | Pumps | 98.82 | 0
New Construction | CZ09 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ09 | cPVVG | Humidification | 0 | 0
New Construction | CZ09 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ09 | cPVVG | Water Systems | 0 | 384613.3
New Construction | CZ09 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ09 | cPVVG | Generators | 0 | 0
New Construction | CZ09 | cPVVG | Total End Uses | 1888348.56 | 655673.79
New Construction | CZ10 | cPVVG | Heating | 0 | 89763.49
New Construction | CZ10 | cPVVG | Cooling | 407309.58 | 0
New Construction | CZ10 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ10 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ10 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ10 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ10 | cPVVG | Fans | 265692.41 | 0
New Construction | CZ10 | cPVVG | Pumps | 103.97 | 0
New Construction | CZ10 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ10 | cPVVG | Humidification | 0 | 0
New Construction | CZ10 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ10 | cPVVG | Water Systems | 0 | 381455.97
New Construction | CZ10 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ10 | cPVVG | Generators | 0 | 0
New Construction | CZ10 | cPVVG | Total End Uses | 1988809.75 | 696075.24
New Construction | CZ11 | cPVVG | Heating | 0 | 236793.03
New Construction | CZ11 | cPVVG | Cooling | 418201.5 | 0
New Construction | CZ11 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ11 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ11 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ11 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ11 | cPVVG | Fans | 261294.04 | 0
New Construction | CZ11 | cPVVG | Pumps | 150.13 | 0
New Construction | CZ11 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ11 | cPVVG | Humidification | 0 | 0
New Construction | CZ11 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ11 | cPVVG | Water Systems | 0 | 389955.37
New Construction | CZ11 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ11 | cPVVG | Generators | 0 | 0
New Construction | CZ11 | cPVVG | Total End Uses | 1995349.46 | 851604.18
New Construction | CZ12 | cPVVG | Heating | 0 | 219576.96
New Construction | CZ12 | cPVVG | Cooling | 346414.93 | 0
New Construction | CZ12 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ12 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ12 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ12 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ12 | cPVVG | Fans | 243184 | 0
New Construction | CZ12 | cPVVG | Pumps | 123 | 0
New Construction | CZ12 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ12 | cPVVG | Humidification | 0 | 0
New Construction | CZ12 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ12 | cPVVG | Water Systems | 0 | 400988.74
New Construction | CZ12 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ12 | cPVVG | Generators | 0 | 0
New Construction | CZ12 | cPVVG | Total End Uses | 1905425.73 | 845421.47
New Construction | CZ13 | cPVVG | Heating | 0 | 189365.45
New Construction | CZ13 | cPVVG | Cooling | 465027.5 | 0
New Construction | CZ13 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ13 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ13 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ13 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ13 | cPVVG | Fans | 271522.82 | 0
New Construction | CZ13 | cPVVG | Pumps | 148.19 | 0
New Construction | CZ13 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ13 | cPVVG | Humidification | 0 | 0
New Construction | CZ13 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ13 | cPVVG | Water Systems | 0 | 378701.54
New Construction | CZ13 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ13 | cPVVG | Generators | 0 | 0
New Construction | CZ13 | cPVVG | Total End Uses | 2052402.3 | 792922.76
New Construction | CZ14 | cPVVG | Heating | 0 | 161279.22
New Construction | CZ14 | cPVVG | Cooling | 591426.98 | 0
New Construction | CZ14 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ14 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ14 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ14 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ14 | cPVVG | Fans | 305226.83 | 0
New Construction | CZ14 | cPVVG | Pumps | 179.13 | 0
New Construction | CZ14 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ14 | cPVVG | Humidification | 0 | 0
New Construction | CZ14 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ14 | cPVVG | Water Systems | 0 | 359443.54
New Construction | CZ14 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ14 | cPVVG | Generators | 0 | 0
New Construction | CZ14 | cPVVG | Total End Uses | 2212536.74 | 745578.54
New Construction | CZ15 | cPVVG | Heating | 0 | 98382.35
New Construction | CZ15 | cPVVG | Cooling | 823719.58 | 0
New Construction | CZ15 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ15 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ15 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ15 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ15 | cPVVG | Fans | 322662.26 | 0
New Construction | CZ15 | cPVVG | Pumps | 268.95 | 0
New Construction | CZ15 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ15 | cPVVG | Humidification | 0 | 0
New Construction | CZ15 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ15 | cPVVG | Water Systems | 0 | 319094.31
New Construction | CZ15 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ15 | cPVVG | Generators | 0 | 0
New Construction | CZ15 | cPVVG | Total End Uses | 2462354.59 | 642332.44
New Construction | CZ16 | cPVVG | Heating | 0 | 401682.37
New Construction | CZ16 | cPVVG | Cooling | 377372.88 | 0
New Construction | CZ16 | cPVVG | Interior Lighting | 352669.87 | 0
New Construction | CZ16 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ16 | cPVVG | Interior Equipment | 963033.93 | 224855.78
New Construction | CZ16 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ16 | cPVVG | Fans | 297029.26 | 0
New Construction | CZ16 | cPVVG | Pumps | 147.74 | 0
New Construction | CZ16 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ16 | cPVVG | Humidification | 0 | 0
New Construction | CZ16 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ16 | cPVVG | Water Systems | 0 | 423982.96
New Construction | CZ16 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ16 | cPVVG | Generators | 0 | 0
New Construction | CZ16 | cPVVG | Total End Uses | 1990253.68 | 1050521.11

## PV
PV - Health/Medical - Nursing Home (NA)

## EV Charger
EV Charger - Health/Medical - Nursing Home (NA)

## Raw_building (hidden)
Building Type | Building Category | Roof Type | Window Wall Ratio (%)
Health/Medical - Nursing Home | Nonresidential | Flat Roof | 20

## Raw_windowdimensionsillheight (hidden)
Window Name | Width [ft] | Height [ft] | Sill Height [ft]
EL4 CORE SPC (G.C3) - WALL 090:A - SUB:A | 2.99 | 5.22 | 3
EL4 CORE SPC (G.C3) - WALL 270:A - SUB:A | 2.99 | 5.22 | 3
EL1 WEST PERIM SPC (G.W1) - WALL 000:A - SUB:A | 58.14 | 5.22 | 3
EL1 WEST PERIM SPC (G.W1) - WALL 180:A - SUB:A | 58.14 | 5.22 | 3
EL1 WEST PERIM SPC (G.W1) - WALL 270:A - SUB:A | 26.87 | 5.22 | 3
EL1 EAST PERIM SPC (G.E2) - WALL 0:A - SUB:A | 24.93 | 5.22 | 3
EL1 EAST PERIM SPC (G.E2) - WALL 180:A - SUB:A | 24.93 | 5.22 | 3
EL2 NORTH PERIM SPC (G.N3) - WALL 000:A - SUB:A | 138.29 | 5.22 | 3
EL2 SOUTH PERIM SPC (G.S2) - WALL 180:A - SUB:A | 138.29 | 5.22 | 3
EL3 NORTH PERIM SPC (G.N3) - WALL 000:A - SUB:A | 55.38 | 5.22 | 3
EL3 NORTH PERIM SPC (G.N3) - WALL 090:A - SUB:A | 9.94 | 5.22 | 3
EL3 SOUTH PERIM SPC (G.S2) - WALL 090:A - SUB:A | 9.94 | 5.22 | 3
EL3 SOUTH PERIM SPC (G.S2) - WALL 180:A - SUB:A | 55.38 | 5.22 | 3
EL3 WEST PERIM SPC (G.W1) - WALL 090:A - SUB:A | 6.99 | 5.22 | 3
EL4 NORTH PERIM SPC (G.N1) - WALL 000:A - SUB:A | 276.74 | 5.22 | 3
EL4 NORTH PERIM SPC (G.N1) - WALL 090:A - SUB:A | 11.98 | 5.22 | 3
EL4 NORTH PERIM SPC (G.N1) - WALL 270:A - SUB:A | 11.98 | 5.22 | 3
EL4 SOUTH PERIM SPC (G.S2) - WALL 090:A - SUB:A | 11.94 | 5.22 | 3
EL4 SOUTH PERIM SPC (G.S2) - WALL 180:A - SUB:A | 276.74 | 5.22 | 3
EL4 SOUTH PERIM SPC (G.S2) - WALL 270:A - SUB:A | 11.94 | 5.22 | 3

## Raw_shadinggeometry (hidden)
Shading Name | Width [ft] | Length [ft]
No Shading

## Raw_zonesummary (hidden)
Vintage | Space | Zone Name | Conditioned | Area (Excluding Plenums and CrawlSpace) (ft2) | Area (Including Plenums and CrawlSpace) (ft2) | Width (ft) | Length (ft) | Volume (ft3) | Multipliers | People (Persons/1000 ft2) | Lighting (Btu/h-ft2) | Plug Loads (Btu/h-ft2) | Outdoor Air Flow per Person (cfm/person) | Outdoor Air Flow per Zone Floor Area (cfm/ft2) | Zone Type | HVAC System Identifier | Schedule Identifier | Height (ft)
Existing | CORRIDOR EL4 CORE SPC (G.C3) | CORRIDOR EL4 CORE SPC (G.C3) | Yes | 3328.42 | 3328.42 | 555.61 | 6 | 29957.28 | 1 | 5 | 2.1238 | 0 | 0.0 | 0.15 | Corridor | Alternative | Health | 9.0005
Existing | DINING EL1 WEST PERIM SPC (G.W1) | DINING EL1 WEST PERIM SPC (G.W1) | Yes | 6303.51 | 6303.51 | 116.73 | 54 | 81936.69 | 1 | 33.33 | 4.1409 | 2.5588 | 0.0 | 0.5 | Dining_fast | Main | Office | 12.9986
Existing | EL2 CORE PLNM (G.4) | EL2 CORE PLNM (G.4) | No | 0 | 3893.77 | 277.66 | 14.04 | 15596.62 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0055
Existing | EL2 NORTH PLNM (G.4) | EL2 NORTH PLNM (G.4) | No | 0 | 5549.35 | 277.66 | 277.66 | 22198.24 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | EL2 SOUTH PLNM (G.4) | EL2 SOUTH PLNM (G.4) | No | 0 | 5549.38 | 277.66 | 19.98 | 22192.59 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.9991
Existing | EL3 NORTH PLNM (G.4) | EL3 NORTH PLNM (G.4) | No | 0 | 2222.49 | 111.19 | 111.19 | 8880.6 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.9958
Existing | EL3 SOUTH PLNM (G.4) | EL3 SOUTH PLNM (G.4) | No | 0 | 2222.55 | 111.19 | 19.98 | 8890.59 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | EL3 WEST PLNM (G.4) | EL3 WEST PLNM (G.4) | No | 0 | 1560.31 | 111.19 | 14.04 | 6251.26 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0064
Existing | EL4 CORE PLNM (G.4) | EL4 CORE PLNM (G.4) | No | 0 | 3328.42 | 555.61 | 6 | 13314.35 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | EL4 NORTH PLNM (G.4) | EL4 NORTH PLNM (G.4) | No | 0 | 13352.26 | 555.61 | 24.02 | 53411.42 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | EL4 SOUTH PLNM (G.4) | EL4 SOUTH PLNM (G.4) | No | 0 | 13324.59 | 555.61 | 23.98 | 53301.05 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | KITCHEN EL1 EAST PERIM SPC (G.E2) | KITCHEN EL1 EAST PERIM SPC (G.E2) | Yes | 2701.87 | 2701.87 | 50.03 | 54 | 35120.65 | 1 | 2.5 | 5.6273 | 26.4716 | 0.0 | 0.15 | Kitchen | Customized | Kitchen | 12.9986
Existing | OFFICE EL2 CORE SPC (G.C1) | OFFICE EL2 CORE SPC (G.C1) | Yes | 3895.75 | 3895.75 | 277.66 | 14.04 | 35057.54 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 8.9989
Existing | OFFICE EL2 NORTH PERIM SPC (G.N3) | OFFICE EL2 NORTH PERIM SPC (G.N3) | Yes | 5549.46 | 5549.46 | 277.66 | 19.98 | 49947.45 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
Existing | OFFICE EL2 SOUTH PERIM SPC (G.S2) | OFFICE EL2 SOUTH PERIM SPC (G.S2) | Yes | 5549.38 | 5549.38 | 277.66 | 19.98 | 49946.82 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
Existing | OFFICE EL3 NORTH PERIM SPC (G.N3) | OFFICE EL3 NORTH PERIM SPC (G.N3) | Yes | 2222.58 | 2222.58 | 111.19 | 19.98 | 20003.95 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0003
Existing | OFFICE EL3 SOUTH PERIM SPC (G.S2) | OFFICE EL3 SOUTH PERIM SPC (G.S2) | Yes | 2222.55 | 2222.55 | 111.19 | 19.98 | 20003.91 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
Existing | OFFICE EL3 WEST PERIM SPC (G.W1) | OFFICE EL3 WEST PERIM SPC (G.W1) | Yes | 1560.27 | 1560.27 | 111.19 | 14.04 | 14043.21 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0005
Existing | PATIENT EL4 NORTH PERIM SPC (G.N1) | PATIENT EL4 NORTH PERIM SPC (G.N1) | Yes | 13348.11 | 13348.11 | 555.61 | 24.02 | 120193.7 | 1 | 5 | 4.4427 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 9.0045
Existing | PATIENTROOM EL4 SOUTH PERIM SPC (G.S2) | PATIENTROOM EL4 SOUTH PERIM SPC (G.S2) | Yes | 13324.59 | 13324.59 | 555.61 | 23.98 | 119927.36 | 1 | 5 | 4.4427 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 9.0005
New Construction | CORRIDOR EL4 CORE SPC (G.C3) | CORRIDOR EL4 CORE SPC (G.C3) | Yes | 3328.42 | 3328.42 | 555.61 | 6 | 29957.28 | 1 | 5 | 1.3647 | 0 | 0.0 | 0.15 | Corridor | Alternative | Health | 9.0005
New Construction | DINING EL1 WEST PERIM SPC (G.W1) | DINING EL1 WEST PERIM SPC (G.W1) | Yes | 6303.51 | 6303.51 | 116.73 | 54 | 81936.69 | 1 | 33.33 | 1.5353 | 2.5588 | 0.0 | 0.5 | Dining_fast | Main | Office | 12.9986
New Construction | EL2 CORE PLNM (G.4) | EL2 CORE PLNM (G.4) | No | 0 | 3893.77 | 277.66 | 14.04 | 15596.62 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0055
New Construction | EL2 NORTH PLNM (G.4) | EL2 NORTH PLNM (G.4) | No | 0 | 5549.35 | 277.66 | 277.66 | 22198.24 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | EL2 SOUTH PLNM (G.4) | EL2 SOUTH PLNM (G.4) | No | 0 | 5549.38 | 277.66 | 19.98 | 22192.59 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.9991
New Construction | EL3 NORTH PLNM (G.4) | EL3 NORTH PLNM (G.4) | No | 0 | 2222.49 | 111.19 | 111.19 | 8880.6 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 3.9958
New Construction | EL3 SOUTH PLNM (G.4) | EL3 SOUTH PLNM (G.4) | No | 0 | 2222.55 | 111.19 | 19.98 | 8890.59 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | EL3 WEST PLNM (G.4) | EL3 WEST PLNM (G.4) | No | 0 | 1560.31 | 111.19 | 14.04 | 6251.26 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0064
New Construction | EL4 CORE PLNM (G.4) | EL4 CORE PLNM (G.4) | No | 0 | 3328.42 | 555.61 | 6 | 13314.35 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | EL4 NORTH PLNM (G.4) | EL4 NORTH PLNM (G.4) | No | 0 | 13352.26 | 555.61 | 24.02 | 53411.42 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | EL4 SOUTH PLNM (G.4) | EL4 SOUTH PLNM (G.4) | No | 0 | 13324.59 | 555.61 | 23.98 | 53301.05 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | KITCHEN EL1 EAST PERIM SPC (G.E2) | KITCHEN EL1 EAST PERIM SPC (G.E2) | Yes | 2701.87 | 2701.87 | 50.03 | 54 | 35120.65 | 1 | 2.5 | 3.2411 | 26.4716 | 0.0 | 0.15 | Kitchen | Customized | Kitchen | 12.9986
New Construction | OFFICE EL2 CORE SPC (G.C1) | OFFICE EL2 CORE SPC (G.C1) | Yes | 3895.75 | 3895.75 | 277.66 | 14.04 | 35057.54 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 8.9989
New Construction | OFFICE EL2 NORTH PERIM SPC (G.N3) | OFFICE EL2 NORTH PERIM SPC (G.N3) | Yes | 5549.46 | 5549.46 | 277.66 | 19.98 | 49947.45 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
New Construction | OFFICE EL2 SOUTH PERIM SPC (G.S2) | OFFICE EL2 SOUTH PERIM SPC (G.S2) | Yes | 5549.38 | 5549.38 | 277.66 | 19.98 | 49946.82 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
New Construction | OFFICE EL3 NORTH PERIM SPC (G.N3) | OFFICE EL3 NORTH PERIM SPC (G.N3) | Yes | 2222.58 | 2222.58 | 111.19 | 19.98 | 20003.95 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0003
New Construction | OFFICE EL3 SOUTH PERIM SPC (G.S2) | OFFICE EL3 SOUTH PERIM SPC (G.S2) | Yes | 2222.55 | 2222.55 | 111.19 | 19.98 | 20003.91 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
New Construction | OFFICE EL3 WEST PERIM SPC (G.W1) | OFFICE EL3 WEST PERIM SPC (G.W1) | Yes | 1560.27 | 1560.27 | 111.19 | 14.04 | 14043.21 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0005
New Construction | PATIENT EL4 NORTH PERIM SPC (G.N1) | PATIENT EL4 NORTH PERIM SPC (G.N1) | Yes | 13348.11 | 13348.11 | 555.61 | 24.02 | 120193.7 | 1 | 5 | 2.3882 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 9.0045
New Construction | PATIENTROOM EL4 SOUTH PERIM SPC (G.S2) | PATIENTROOM EL4 SOUTH PERIM SPC (G.S2) | Yes | 13324.59 | 13324.59 | 555.61 | 23.98 | 119927.36 | 1 | 5 | 2.3882 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 9.0005