## Geometry Summary (hidden)
Abbreviation | Building Type | Shape | Number of Floors | Aspect Ratio | Zone Height_1 | Zone Height_2 | Zone Height_3 | Plenum Height | Floor to Floor Height (feet) | Floor to Ceiling Height (feet)
Asm | Assembly | #VALUE! | 1 | 1 | 12.0006 | na | na | 3.0001 | 12.0006 | 15.0007
ECC | Education - Community College | #VALUE! | 3 | 5.7 | 9.0004 | 13.0006 | na | 4.0002 | 9 / 13 | 13 / 17
EPr | Education - Primary School | #VALUE! | 1 | 2 | 9.0004 | 12.0006 | na | 3.0001 | 9 / 12 | 12 / 15
ERC | Education - Relocatable Classroom | #VALUE! | 1 | 1.7 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
ESe | Education - Secondary School | #VALUE! | 2 | 2.5/1.0 | 9.0004 | 13.0006 | na | 4.0002 | 9 / 13 | 13 / 17
EUn | Education - University | #VALUE! | 4 | 2.0/15.0 | 10.0005 | 9.0004 | 14.0007 | 4.0002 | 9 / 10 / 14 | 13 / 14 / 18
Fin | Financial buildings, incl. banks | #VALUE! | 1 | 1 | 11.0005 | na | na | na | 11.0005 | 11.0005
Gro | Grocery | #VALUE! | 1 | 1 | 25.0012 | na | na | na | 25.0012 | 25.0012
Hsp | Health/Medical - Hospital | #VALUE! | 3 | 1 | 10.007 | 12.9927 | na | 2.9857 | 10 / 13 | 13 / 16
Htl | Lodging - Hotel | #VALUE! | 4 | 6.6 | 8.0004 | 10.5005 | na | 1.5001 | 8 / 11 | 10 / 12
Lib | Libraries | #VALUE! | 1 | 1 | 13.0006 | na | na | na | 13.0006 | 13.0006
MBT | Manufacturing Biotech | #VALUE! | 1 | 6 | 9.0004 | na | na | 6.0003 | 9.0004 | 15.0008
MLI | Manufacturing Light Industrial | #VALUE! | 1 | 1 | 35.0017 | na | na | na | 35.0017 | 35.0017
Mtl | Lodging - Motel | #VALUE! | 2 | 5.1 | 9.0004 | na | na | na | 9.0004 | 9.0004
Nrs | Health/Medical - Nursing Home | #VALUE! | 2 | 10.3 | 12.9986 | 9.0005 | na | 4.0055 | 9 / 13 | 13 / 17
OfL | Office - Large | #VALUE! | 3 | 1.5 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
OfS | Office - Small | #VALUE! | 2 | 1.5 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
Rel | Religious assembly buildings | #VALUE! | 1 | 2.5 | 37.5018 | 15.0007 | na | na | 38 / 15 | 38 / 15
RFF | Restaurant - Fast-Food | #VALUE! | 1 | 1 | 10.0005 | na | na | 3.0002 | 10.0005 | 13.0007
RSD | Restaurant - Sit-Down | #VALUE! | 1 | 1 | 10.0005 | na | na | 3.0001 | 10.0005 | 13.0006
Rt3 | Retail - Multistory Large | #VALUE! | 3 | 1 | 15.0007 | na | na | 5.8002 | 15.0007 | 20.8009
RtL | Retail - Single-Story Large | #VALUE! | 1 | 1 | 20.501 | na | na | na | 20.501 | 20.501
RtS | Retail - Small | #VALUE! | 1 | 1 | 10.0005 | na | na | 2.0001 | 10.0005 | 12.0006
SCn | Storage - Conditioned | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023
SUn | Storage - Unconditioned | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023
WRf | Warehouse - Refrigerated | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023

## Prototype
TRC, Updated Febuary 2026
Education - Secondary School
Characteristic | Value
Building Type | Education - Secondary School
Building Category | Nonresidential
Vintages | Two vintages: Existing and New Construction
Shape | #VALUE!
Total Floor Area (ft²) | 54463.33
Aspect Ratio | 2.5/1.0
Number of Floors | 2
Roof Type | Flat Roof
Gross Window to Wall Ratio (%) | 15.14
Shading Geometry | No Shading
Floor to Floor Height (feet) | 9 / 13
Floor to Ceiling Height (feet) | 13 / 17
Glazing Sill Height (feet) | 3

## Notes
Prototype Overview
Name | Description
Asm | Assembly
ECC | Education - Community College
EPr | Education - Primary School
ERC | Education - Relocatable Classroom
ESe | Education - Secondary School
EUn | Education - University
Fin | Financial buildings, incl. banks
Gro | Grocery
Hsp | Health/Medical - Hospital
Htl | Lodging - Hotel
Lib | Libraries
MBT | Manufacturing Biotech
MLI | Manufacturing Light Industrial
Mtl | Lodging - Motel
Nrs | Health/Medical - Nursing Home
OfL | Office - Large
OfS | Office - Small
Rel | Religious assembly buildings
RFF | Restaurant - Fast-Food
RSD | Restaurant - Sit-Down
Rt3 | Retail - Multistory Large
RtL | Retail - Single-Story Large
RtS | Retail - Small
SCn | Storage - Conditioned
SUn | Storage - Unconditioned
WRf | Warehouse - Refrigerated
Vintages
Existing | Weighted average of Title 24 requirements based on vintages from 1975 to 2022
New Construction | Title 24 2025
Run Begin Day
Begin Month | Begin Day of Month | Day of Week for Start Day
1 | 1 | Sunday
Special Days
Name | Start Date | Duration (days) | Special Day Type
New Years Day | January 1 | 1 | Holiday
Veterans Day | November 11 | 1 | Holiday
Christmas | December 25 | 1 | Holiday
Independence Day | July 4 | 1 | Holiday
MLK Day | 3rd Monday in January | 1 | Holiday
Presidents Day | 3rd Monday in February | 1 | Holiday
Memorial Day | Last Monday in May | 1 | Holiday
Labor Day | 1st Monday in September | 1 | Holiday
Columbus Day | 2nd Monday in October | 1 | Holiday
Thanksgiving | 4th Thursday in November | 1 | Holiday

## Raw_runbeginday (hidden)
Begin Month | Begin Day of Month | Day of Week for Start Day
1 | 1 | Sunday

## Raw_specialdays (hidden)
Name | Start Day | Duration | Special Day Type
New Years Day | January 1 | 1 | Holiday
Veterans Day | November 11 | 1 | Holiday
Christmas | December 25 | 1 | Holiday
Independence Day | July 4 | 1 | Holiday
MLK Day | 3rd Monday in January | 1 | Holiday
Presidents Day | 3rd Monday in February | 1 | Holiday
Memorial Day | Last Monday in May | 1 | Holiday
Labor Day | 1st Monday in September | 1 | Holiday
Columbus Day | 2nd Monday in October | 1 | Holiday
Thanksgiving | 4th Thursday in November | 1 | Holiday

## Climate Zone
Climate Zones - All Prototypes
Climate Zone | Representative City | Weather File Name
CZ01 | Eureka | CA_EUREKA_725940S_CZ2022.epw
CZ02 | Napa | CA_NAPA-CO_724955S_CZ2022.epw
CZ03 | Oakland | CA_OAKLAND-METRO-AP_724930S_CZ2022.epw
CZ04 | San Jose | CA_SAN-JOSE-IAP_724945S_CZ2022.epw
CZ05 | Santa Maria | CA_SANTA-MARIA-PUBLIC-AP_723940S_CZ2022.epw
CZ06 | Los Angeles | CA_LOS-ANGELES-IAP_722950S_CZ2022.epw
CZ07 | San Diego-Lindbergh | CA_SAN-DIEGO-LINDBERGH-FLD_722900S_CZ2022.epw
CZ08 | Long Beach-Daugherty | CA_LONG-BEACH-DAUGHERTY-FLD_722970S_CZ2022.epw
CZ09 | Los Angeles | CA_LOS-ANGELES-DOWNTOWN-USC_722874S_CZ2022.epw
CZ10 | Riverside | CA_RIVERSIDE-MUNI_722869S_CZ2022.epw
CZ11 | Red Bluff | CA_RED-BLUFF-MUNI-AP_725910S_CZ2022.epw
CZ12 | Stockton | CA_STOCKTON-METRO-AP_724920S_CZ2022.epw
CZ13 | Fresno Yosemite | CA_FRESNO-YOSEMITE-IAP_723890S_CZ2022.epw
CZ14 | Daggett Barstow | CA_DAGGETT-BARSTOW-AP_723815S_CZ2022.epw
CZ15 | El Centro | CA_EL-CENTRO-NAF_722810S_CZ2022.epw
CZ16 | Bishop | CA_BISHOP-AP_724800S_CZ2022.epw
Source: California Energy Commission, https://cecgis-caenergy.opendata.arcgis.com/datasets/CAEnergy::california-building-climate-zones/about

## Zones
Zone Summary - Education - Secondary School
Space | Zone Name | Conditioned [Y/N] | Zone Type | HVAC System Identifier (Main/Alternative/Customized) | Schedule Identifier | Area Fraction | Area (Excluding Plenums and Crawl Space) (ft²) | Volume (ft³) | Multipliers | People (Persons/1,000 ft²) | Note
CLASSROOM E1 WEST PERIM (G.W1) | CLASSROOM E1 WEST PERIM (G.W1) | Yes | Classroom_class | Alternative | Retail | 6.888% | 3751.24 | 48768.49 | 1 | 25
CLASSROOM E2 NORTH PERIM (G.N3) | CLASSROOM E2 NORTH PERIM (G.N3) | Yes | Classroom_class | Main | Retail | 3.842% | 2092.38 | 18832.36 | 1 | 25
CLASSROOM E2 SOUTH PERIM (G.S2) | CLASSROOM E2 SOUTH PERIM (G.S2) | Yes | Classroom_class | Main | Retail | 3.842% | 2092.38 | 18832.36 | 1 | 25
CLASSROOM E2 WEST PERIM (G.W1) | CLASSROOM E2 WEST PERIM (G.W1) | Yes | Classroom_class | Main | Retail | 3.042% | 1656.55 | 14909.67 | 1 | 25
CLASSROOM E4 CORE (G.C6) | CLASSROOM E4 CORE (G.C6) | Yes | Classroom_class | Main | School | 3.302% | 1798.23 | 16184.9 | 1 | 25
CLASSROOM E4 EAST PERIM (G.E2) | CLASSROOM E4 EAST PERIM (G.E2) | Yes | Classroom_class | Main | School | 2.973% | 1619.41 | 14575.41 | 1 | 25
CLASSROOM E4 NORTH PERIM (G.N3) | CLASSROOM E4 NORTH PERIM (G.N3) | Yes | Classroom_class | Main | School | 7.617% | 4148.61 | 37339.35 | 1 | 25
CLASSROOM E4 SOUTH PERIM (G.S1) | CLASSROOM E4 SOUTH PERIM (G.S1) | Yes | Classroom_class | Main | School | 7.617% | 4148.61 | 37339.35 | 1 | 25
CLASSROOM E4 WEST PERIM (G.W4) | CLASSROOM E4 WEST PERIM (G.W4) | Yes | Classroom_class | Main | School | 2.973% | 1619.41 | 14575.41 | 1 | 25
COMPUTER CLASSROOM E4 CORE SPC (G.C5) | COMPUTER CLASSROOM E4 CORE SPC (G.C5) | Yes | Computer | Customized | Computer room | 1.415% | 770.67 | 6936.36 | 1 | 1.5
DINING E3 SW PERIM (G.SW1) | DINING E3 SW PERIM (G.SW1) | Yes | Dining_fast | Alternative | Retail | 10.34% | 5634 | 73245.58 | 1 | 33.33
E2 NORTH PERIM PLNM (G.N6) | E2 NORTH PERIM PLNM (G.N6) | No | Plenum | - | Plenum | 0% | 0 | 8369.94 | 1 | 0
E2 SOUTH PERIM PLNM (G.S5) | E2 SOUTH PERIM PLNM (G.S5) | No | Plenum | - | Plenum | 0% | 0 | 8369.94 | 1 | 0
E2 WEST PERIM PLNM (G.W4) | E2 WEST PERIM PLNM (G.W4) | No | Plenum | - | Plenum | 0% | 0 | 6626.52 | 1 | 0
E4 CORE PLNM (G.C11) | E4 CORE PLNM (G.C11) | No | Plenum | - | Plenum | 0% | 0 | 3082.83 | 1 | 0
E4 CORE PLNM (G.C12) | E4 CORE PLNM (G.C12) | No | Plenum | - | Plenum | 0% | 0 | 7193.29 | 1 | 0
E4 EAST PERIM PLNM (G.E8) | E4 EAST PERIM PLNM (G.E8) | No | Plenum | - | Plenum | 0% | 0 | 6477.96 | 1 | 0
E4 NORTH PERIM PLNM (G.N9) | E4 NORTH PERIM PLNM (G.N9) | No | Plenum | - | Plenum | 0% | 0 | 16595.27 | 1 | 0
E4 SOUTH PERIM PLNM (G.S7) | E4 SOUTH PERIM PLNM (G.S7) | No | Plenum | - | Plenum | 0% | 0 | 16595.27 | 1 | 0
E4 WEST PERIM PLNM (G.W10) | E4 WEST PERIM PLNM (G.W10) | No | Plenum | - | Plenum | 0% | 0 | 6477.96 | 1 | 0
GYMNASIUM E17 WEST PERIM (G.W1) | GYMNASIUM E17 WEST PERIM (G.W1) | Yes | Gym | Alternative | Retail | 41.32% | 22502.2 | 585085.65 | 1 | 33.33
KITCHEN E3 NE PERIM (G.NE2) | KITCHEN E3 NE PERIM (G.NE2) | Yes | Kitchen | Customized | Kitchen | 4.828% | 2629.64 | 34187 | 1 | 2.5
Total (22 Space) | Total (22 Space) | Total (13 Conditioned zones, 9 Unconditioned Zones) |  |  |  |  | 54463.33

## Envelope
Envelope - Education - Secondary School
Element | Prototype | Assembly Type | Construction | Unit | Vintage | Selected T24 | Note | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Education - Secondary School | - | Stucco+Wall Continuous Insulation+Gypsum 5/8in | U-value IP | Existing | Weighted average |  | 0.393 | 0.609 | 0.577 | 0.629 | 0.615 | 0.623 | 0.73 | 0.626 | 0.621 | 0.884 | 0.497 | 0.533 | 0.509 | 0.384 | 0.378 | 0.357
External Wall | Education - Secondary School | - | Stucco+Wall Continuous Insulation+Gypsum 5/8in | U-value IP | New Construction | 2025 |  | 0.257 | 1.452 | 1.452 | 1.452 | 1.452 | 1.515 | 1.515 | 1.515 | 1.515 | 1.452 | 0.185 | 0.257 | 0.218 | 0.185 | 0.185 | 0.176
Roof | Education - Secondary School | - | Roof Membrane+Roof Continuous Insulation+Metal Decking | U-value IP | Existing | Weighted average |  | 0.067 | 0.066 | 0.067 | 0.065 | 0.067 | 0.074 | 0.073 | 0.073 | 0.07 | 0.061 | 0.063 | 0.063 | 0.063 | 0.061 | 0.059 | 0.061
Roof | Education - Secondary School | - | Roof Membrane+Roof Continuous Insulation+Metal Decking | U-value IP | New Construction | 2025 |  | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.048 | 0.048 | 0.048 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028 | 0.028
Windows | Education - Secondary School | - | Theoretical Glazing | U-value IP | Existing | Weighted average |  | 1.024 | 1.078 | 1.131 | 1.108 | 1.109 | 1.115 | 1.075 | 1.114 | 1.112 | 0.875 | 0.942 | 0.94 | 0.929 | 0.886 | 0.831 | 0.885
Windows | Education - Secondary School | - | Theoretical Glazing | U-value IP | New Construction | 2025 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
Windows | Education - Secondary School | - | Theoretical Glazing | SHGC | Existing | Weighted average |  | 0.70708 | 0.70715 | 0.73753 | 0.71836 | 0.75308 | 0.7254 | 0.72673 | 0.7241 | 0.72365 | 0.5734 | 0.64366 | 0.64394 | 0.6358 | 0.60724 | 0.57129 | 0.62767
Windows | Education - Secondary School | - | Theoretical Glazing | SHGC | New Construction | 2025 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Windows | Education - Secondary School | - | Theoretical Glazing | Visible Transmittance | Existing | Weighted average |  | 0.26089 | 0.26141 | 0.26004 | 0.26231 | 0.26223 | 0.26197 | 0.26576 | 0.26213 | 0.26228 | 0.27816 | 0.26665 | 0.26607 | 0.26793 | 0.27125 | 0.27583 | 0.27139
Windows | Education - Secondary School | - | Theoretical Glazing | Visible Transmittance | New Construction | 2025 |  | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
Infiltration - Education - Secondary School
|  |  |  | Element | Unit | Vintage | Note | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
|  |  |  | Infiltration Rate | CFM/ft2 | Existing | Infiltration rate is flow rate per exterior surface area at 10 mph wind speed, modeled proportionally to wind speed. | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801
[6 empty] | New Construction |  | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801

## Raw_envelope (hidden)
Climate Zone | Vintage | Exterior Roof Layers | Roof U-Value [Btu/h-ft2-F] | Exterior Wall Layers | Wall U-Value [Btu/h-ft2-F] | Exterior Window Layers | Window U-Value [Btu/h-ft2-F] | Window SHGC | Window VT
CZ01 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.067 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.393 | Theoretical Glazing | 1.024 | 0.70708 | 0.26089
CZ02 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.066 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.609 | Theoretical Glazing | 1.078 | 0.70715 | 0.26141
CZ03 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.067 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.577 | Theoretical Glazing | 1.131 | 0.73753 | 0.26004
CZ04 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.629 | Theoretical Glazing | 1.108 | 0.71836 | 0.26231
CZ05 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.067 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.615 | Theoretical Glazing | 1.109 | 0.75308 | 0.26223
CZ06 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.074 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.623 | Theoretical Glazing | 1.115 | 0.7254 | 0.26197
CZ07 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.073 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.73 | Theoretical Glazing | 1.075 | 0.72673 | 0.26576
CZ08 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.073 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.626 | Theoretical Glazing | 1.114 | 0.7241 | 0.26213
CZ09 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.07 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.621 | Theoretical Glazing | 1.112 | 0.72365 | 0.26228
CZ10 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.884 | Theoretical Glazing | 0.875 | 0.5734 | 0.27816
CZ11 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.063 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.497 | Theoretical Glazing | 0.942 | 0.64366 | 0.26665
CZ12 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.063 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.533 | Theoretical Glazing | 0.94 | 0.64394 | 0.26607
CZ13 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.063 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.509 | Theoretical Glazing | 0.929 | 0.6358 | 0.26793
CZ14 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.384 | Theoretical Glazing | 0.886 | 0.60724 | 0.27125
CZ15 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.059 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.378 | Theoretical Glazing | 0.831 | 0.57129 | 0.27583
CZ16 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.357 | Theoretical Glazing | 0.885 | 0.62767 | 0.27139
CZ01 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.257 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ02 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.452 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ03 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.452 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ04 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.452 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ05 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.452 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ06 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.048 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.515 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ07 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.048 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.515 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ08 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.048 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.515 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ09 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.515 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ10 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.452 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ11 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.185 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ12 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.257 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ13 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.218 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ14 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.185 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ15 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.185 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ16 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.028 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.176 | Theoretical Glazing | 0.36 | 0.25 | 0.42

## Raw_infiltrationcfmft (hidden)
Vintage | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Existing | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801
New Construction | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801

## Thermostat
Thermostat Setpoints - Education - Secondary School | [18 empty] | Zone Type
Schedule Identifier | Setpoint | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Notes | Computer room
Computer room | Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Kitchen
Computer room | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Retail
Computer room | Cooling Setpoint (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | School
Computer room | Cooling Setback (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Kitchen | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Kitchen | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Retail | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Retail | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Retail | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Retail | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
School | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
School | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
School | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
School | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Raw_thermostatsetpoints (hidden)
Climate Zone | Schedule Identifier | Heating Setpoint (F) | Heating Setback (F) | Cooling Setpoint (F) | Cooling Setback (F)
CZ01 | Computer room | 60 | 60 | 80 | 80
CZ01 | Kitchen | 70 | 60 | 75 | 85
CZ01 | Retail | 70 | 60 | 75 | 85
CZ01 | School | 70 | 60 | 75 | 85
CZ02 | Computer room | 60 | 60 | 80 | 80
CZ02 | Kitchen | 70 | 60 | 75 | 85
CZ02 | Retail | 70 | 60 | 75 | 85
CZ02 | School | 70 | 60 | 75 | 85
CZ03 | Computer room | 60 | 60 | 80 | 80
CZ03 | Kitchen | 70 | 60 | 75 | 85
CZ03 | Retail | 70 | 60 | 75 | 85
CZ03 | School | 70 | 60 | 75 | 85
CZ04 | Computer room | 60 | 60 | 80 | 80
CZ04 | Kitchen | 70 | 60 | 75 | 85
CZ04 | Retail | 70 | 60 | 75 | 85
CZ04 | School | 70 | 60 | 75 | 85
CZ05 | Computer room | 60 | 60 | 80 | 80
CZ05 | Kitchen | 70 | 60 | 75 | 85
CZ05 | Retail | 70 | 60 | 75 | 85
CZ05 | School | 70 | 60 | 75 | 85
CZ06 | Computer room | 60 | 60 | 80 | 80
CZ06 | Kitchen | 70 | 60 | 75 | 85
CZ06 | Retail | 70 | 60 | 75 | 85
CZ06 | School | 70 | 60 | 75 | 85
CZ07 | Computer room | 60 | 60 | 80 | 80
CZ07 | Kitchen | 70 | 60 | 75 | 85
CZ07 | Retail | 70 | 60 | 75 | 85
CZ07 | School | 70 | 60 | 75 | 85
CZ08 | Computer room | 60 | 60 | 80 | 80
CZ08 | Kitchen | 70 | 60 | 75 | 85
CZ08 | Retail | 70 | 60 | 75 | 85
CZ08 | School | 70 | 60 | 75 | 85
CZ09 | Computer room | 60 | 60 | 80 | 80
CZ09 | Kitchen | 70 | 60 | 75 | 85
CZ09 | Retail | 70 | 60 | 75 | 85
CZ09 | School | 70 | 60 | 75 | 85
CZ10 | Computer room | 60 | 60 | 80 | 80
CZ10 | Kitchen | 70 | 60 | 75 | 85
CZ10 | Retail | 70 | 60 | 75 | 85
CZ10 | School | 70 | 60 | 75 | 85
CZ11 | Computer room | 60 | 60 | 80 | 80
CZ11 | Kitchen | 70 | 60 | 75 | 85
CZ11 | Retail | 70 | 60 | 75 | 85
CZ11 | School | 70 | 60 | 75 | 85
CZ12 | Computer room | 60 | 60 | 80 | 80
CZ12 | Kitchen | 70 | 60 | 75 | 85
CZ12 | Retail | 70 | 60 | 75 | 85
CZ12 | School | 70 | 60 | 75 | 85
CZ13 | Computer room | 60 | 60 | 80 | 80
CZ13 | Kitchen | 70 | 60 | 75 | 85
CZ13 | Retail | 70 | 60 | 75 | 85
CZ13 | School | 70 | 60 | 75 | 85
CZ14 | Computer room | 60 | 60 | 80 | 80
CZ14 | Kitchen | 70 | 60 | 75 | 85
CZ14 | Retail | 70 | 60 | 75 | 85
CZ14 | School | 70 | 60 | 75 | 85
CZ15 | Computer room | 60 | 60 | 80 | 80
CZ15 | Kitchen | 70 | 60 | 75 | 85
CZ15 | Retail | 70 | 60 | 75 | 85
CZ15 | School | 70 | 60 | 75 | 85
CZ16 | Computer room | 60 | 60 | 80 | 80
CZ16 | Kitchen | 70 | 60 | 75 | 85
CZ16 | Retail | 70 | 60 | 75 | 85
CZ16 | School | 70 | 60 | 75 | 85

## HVAC System
HVAC system - Education - Secondary School
Vintage | System Name | Category | Heating Type* | Cooling Type* | Air Distribution | Heating Efficiency | Cooling Efficiency | Note
Existing | cDXGF | Main | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.65
Existing | cDXGF | Alternative | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.85
Existing | cDXGF | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
New Construction | cDXGF | Main | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.65
New Construction | cDXGF | Alternative | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.85
New Construction | cDXGF | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
Existing | cDXHP | Main | DX-AIR | DX-AIR | SZ-CAV | 3.738 | 3.65
Existing | cDXHP | Alternative | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.85
Existing | cDXHP | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
New Construction | cDXHP | Main | DX-AIR | DX-AIR | SZ-CAV | 3.738 | 3.65
New Construction | cDXHP | Alternative | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.85
New Construction | cDXHP | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
Existing | cAVVG | Main | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Alternative | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.85
Existing | cAVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
New Construction | cAVVG | Main | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Alternative | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.85
New Construction | cAVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
Existing | cDXOH | Main | None | DX-AIR | SZ-CAV | - | 3.65
Existing | cDXOH | Alternative | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.85
Existing | cDXOH | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
New Construction | cDXOH | Main | None | DX-AIR | SZ-CAV | - | 3.65
New Construction | cDXOH | Alternative | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.85
New Construction | cDXOH | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
Existing | cPVVG | Main | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.65
Existing | cPVVG | Alternative | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.85
Existing | cPVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
New Construction | cPVVG | Main | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.65
New Construction | cPVVG | Alternative | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.85
New Construction | cPVVG | Customized | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3
*DX Heating and cooling COPs are calculated based on coil-only input power and exclude fan power
Fan Power - Education - Secondary School
Vintage | System Name | HVAC System Identifier | Fan System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm | Note
Existing | cAVVG | Alternative | SZ-VAV | 3.877 | 0.55 | 0.9 | 0.83
Existing | cAVVG | Main | MZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cAVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cAVVG | Customized | SZ-CRAC | 5.1625 | 0.65 | 0.85 | 0.93
New Construction | cAVVG | Alternative | SZ-VAV | 3.877 | 0.55 | 0.9 | 0.83
New Construction | cAVVG | Main | MZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cAVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cAVVG | Customized | SZ-CRAC | 5.1625 | 0.65 | 0.85 | 0.93
Existing | cDXGF | Alternative | SZ-VAV | 3.877 | 0.55 | 0.9 | 0.83
Existing | cDXGF | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXGF | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXGF | Customized | SZ-CRAC | 5.1625 | 0.65 | 0.85 | 0.93
New Construction | cDXGF | Alternative | SZ-VAV | 3.877 | 0.55 | 0.9 | 0.83
New Construction | cDXGF | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXGF | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXGF | Customized | SZ-CRAC | 5.1625 | 0.65 | 0.85 | 0.93
Existing | cDXHP | Alternative | SZ-VAV | 3.877 | 0.55 | 0.9 | 0.83
Existing | cDXHP | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXHP | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXHP | Customized | SZ-CRAC | 5.1625 | 0.65 | 0.85 | 0.93
New Construction | cDXHP | Alternative | SZ-VAV | 3.877 | 0.55 | 0.9 | 0.83
New Construction | cDXHP | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXHP | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXHP | Customized | SZ-CRAC | 5.1625 | 0.65 | 0.85 | 0.93
Existing | cDXOH | Alternative | SZ-VAV | 3.877 | 0.55 | 0.9 | 0.83
Existing | cDXOH | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXOH | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXOH | Customized | SZ-CRAC | 5.1625 | 0.65 | 0.85 | 0.93
New Construction | cDXOH | Alternative | SZ-VAV | 3.877 | 0.55 | 0.9 | 0.83
New Construction | cDXOH | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXOH | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXOH | Customized | SZ-CRAC | 5.1625 | 0.65 | 0.85 | 0.93
Existing | cPVVG | Alternative | SZ-VAV | 3.877 | 0.55 | 0.9 | 0.83
Existing | cPVVG | Main | SZ-VAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cPVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cPVVG | Customized | SZ-CRAC | 5.1625 | 0.65 | 0.85 | 0.93
New Construction | cPVVG | Alternative | SZ-VAV | 3.877 | 0.55 | 0.9 | 0.83
New Construction | cPVVG | Main | SZ-VAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cPVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cPVVG | Customized | SZ-CRAC | 5.1625 | 0.65 | 0.85 | 0.93

## Raw_fanoverview (hidden)
Vintage | HVAC name | System type | HVAC System Identifier | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm
Existing | cAVVG | SZ-VAV Fans | Alternative | 3.877 | 0.55 | 0.9 | 0.83
Existing | cAVVG | MZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cAVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cAVVG | SZ-CRAC Fans | Customized | 5.1625 | 0.65 | 0.85 | 0.93
New Construction | cAVVG | SZ-VAV Fans | Alternative | 3.877 | 0.55 | 0.9 | 0.83
New Construction | cAVVG | MZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cAVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cAVVG | SZ-CRAC Fans | Customized | 5.1625 | 0.65 | 0.85 | 0.93
Existing | cDXGF | SZ-VAV Fans | Alternative | 3.877 | 0.55 | 0.9 | 0.83
Existing | cDXGF | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXGF | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXGF | SZ-CRAC Fans | Customized | 5.1625 | 0.65 | 0.85 | 0.93
New Construction | cDXGF | SZ-VAV Fans | Alternative | 3.877 | 0.55 | 0.9 | 0.83
New Construction | cDXGF | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXGF | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXGF | SZ-CRAC Fans | Customized | 5.1625 | 0.65 | 0.85 | 0.93
Existing | cDXHP | SZ-VAV Fans | Alternative | 3.877 | 0.55 | 0.9 | 0.83
Existing | cDXHP | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXHP | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXHP | SZ-CRAC Fans | Customized | 5.1625 | 0.65 | 0.85 | 0.93
New Construction | cDXHP | SZ-VAV Fans | Alternative | 3.877 | 0.55 | 0.9 | 0.83
New Construction | cDXHP | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXHP | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXHP | SZ-CRAC Fans | Customized | 5.1625 | 0.65 | 0.85 | 0.93
Existing | cDXOH | SZ-VAV Fans | Alternative | 3.877 | 0.55 | 0.9 | 0.83
Existing | cDXOH | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXOH | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXOH | SZ-CRAC Fans | Customized | 5.1625 | 0.65 | 0.85 | 0.93
New Construction | cDXOH | SZ-VAV Fans | Alternative | 3.877 | 0.55 | 0.9 | 0.83
New Construction | cDXOH | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXOH | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXOH | SZ-CRAC Fans | Customized | 5.1625 | 0.65 | 0.85 | 0.93
Existing | cPVVG | SZ-VAV Fans | Alternative | 3.877 | 0.55 | 0.9 | 0.83
Existing | cPVVG | SZ-VAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cPVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cPVVG | SZ-CRAC Fans | Customized | 5.1625 | 0.65 | 0.85 | 0.93
New Construction | cPVVG | SZ-VAV Fans | Alternative | 3.877 | 0.55 | 0.9 | 0.83
New Construction | cPVVG | SZ-VAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cPVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cPVVG | SZ-CRAC Fans | Customized | 5.1625 | 0.65 | 0.85 | 0.93

## Raw_hvac (hidden)
Vintage | System Name | HVAC System Identifier | Air Distribution | Heating Efficiency | Cooling Efficiency | Cooling Coil Type | Heating Coil Type
Existing | cAVVG | Main | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Alternative | SZ-VAV | 0.8 | 3.85 | DX-AIR | COMBUSTION
Existing | cAVVG | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cAVVG | Customized | SZ-CRAC | 0.805 | 3.4223 | DX-AIR | NONE
New Construction | cAVVG | Main | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Alternative | SZ-VAV | 0.8 | 3.85 | DX-AIR | COMBUSTION
New Construction | cAVVG | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cAVVG | Customized | SZ-CRAC | 0.805 | 3.4223 | DX-AIR | NONE
Existing | cDXGF | Main | SZ-CAV | 0.8 | 3.65
Existing | cDXGF | Alternative | SZ-VAV | 0.8 | 3.85 | DX-AIR | COMBUSTION
Existing | cDXGF | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cDXGF | Customized | SZ-CRAC | 0.8 | 3.4223 | DX-AIR | NONE
New Construction | cDXGF | Main | SZ-CAV | 0.8 | 3.65
New Construction | cDXGF | Alternative | SZ-VAV | 0.8 | 3.85 | DX-AIR | COMBUSTION
New Construction | cDXGF | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cDXGF | Customized | SZ-CRAC | 0.8 | 3.4223 | DX-AIR | NONE
Existing | cDXHP | Main | SZ-CAV | 3.738 | 3.65
Existing | cDXHP | Alternative | SZ-VAV | 0.8 | 3.85 | DX-AIR | COMBUSTION
Existing | cDXHP | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cDXHP | Customized | SZ-CRAC | 3.23 | 3.4223 | DX-AIR | NONE
New Construction | cDXHP | Main | SZ-CAV | 3.738 | 3.65
New Construction | cDXHP | Alternative | SZ-VAV | 0.8 | 3.85 | DX-AIR | COMBUSTION
New Construction | cDXHP | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cDXHP | Customized | SZ-CRAC | 3.23 | 3.4223 | DX-AIR | NONE
Existing | cDXOH | Main | SZ-CAV | - | 3.65
Existing | cDXOH | Alternative | SZ-VAV | 0.8 | 3.85 | DX-AIR | COMBUSTION
Existing | cDXOH | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cDXOH | Customized | SZ-CRAC |  | 3.4223 | DX-AIR | NONE
New Construction | cDXOH | Main | SZ-CAV | - | 3.65
New Construction | cDXOH | Alternative | SZ-VAV | 0.8 | 3.85 | DX-AIR | COMBUSTION
New Construction | cDXOH | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cDXOH | Customized | SZ-CRAC |  | 3.4223 | DX-AIR | NONE
Existing | cPVVG | Main | SZ-VAV | 0.8 | 3.65
Existing | cPVVG | Alternative | SZ-VAV | 0.8 | 3.85 | DX-AIR | COMBUSTION
Existing | cPVVG | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cPVVG | Customized | SZ-CRAC | 0.8 | 3.4223 | DX-AIR | NONE
New Construction | cPVVG | Main | SZ-VAV | 0.8 | 3.65
New Construction | cPVVG | Alternative | SZ-VAV | 0.8 | 3.85 | DX-AIR | COMBUSTION
New Construction | cPVVG | Customized | SZ-CAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cPVVG | Customized | SZ-CRAC | 0.8 | 3.4223 | DX-AIR | NONE

## Ventilation
Outdoor Airflow Rate - Education - Secondary School | [19 empty] | Zone Type
Zone Type | Floor area (ft²) | cfm/person | cfm/ft² | cfm | Notes | [14 empty] | Classroom_class
Classroom_class | 22926.82 | 0 | 0.38 | 8712.1916 | [15 empty] | Computer
Computer | 770.67 | 0 | 0.15 | 115.6005 | [15 empty] | Dining_fast
Dining_fast | 5634 | 0 | 0.5 | 2817 | [15 empty] | Gym
Gym | 22502.2 | 0 | 0.5 | 11251.1 | [15 empty] | Kitchen
Kitchen | 2629.64 | 0 | 0.15 | 394.446
OA Controller - Education - Secondary School
Element | Vintage | Unit | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Notes
Economizer Maximum Limit Dry-Bulb Temperature | Existing | °F | 75 | 73 | 75 | 73 | 75 | 71 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 75 | 75 | 75
| New Construction | °F | 75 | 73 | 75 | 73 | 75 | 71 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 75 | 75 | 75
Exhaust hood - Education - Secondary School
Type of Hood | Max Exhaust Flow Rate (cfm/ft) | Hood Length (ft) | Hood Exhaust Rate (cfm) | Note
- | - | - | -

## Raw_outdoorairflowrate (hidden)
Zone Type | Floor Area (ft2) | cfm/person | cfm/ft2
Classroom_class | 22926.82 | 0 | 0.38
Computer | 770.67 | 0 | 0.15
Dining_fast | 5634 | 0 | 0.5
Gym | 22502.2 | 0 | 0.5
Kitchen | 2629.64 | 0 | 0.15

## Raw_oacontroller (hidden)
Climate Zone | Vintage | Economizer Maximum Limit Dry-Bulb Temperature (F)
CZ01 | Existing | 75
CZ02 | Existing | 73
CZ03 | Existing | 75
CZ04 | Existing | 73
CZ05 | Existing | 75
CZ06 | Existing | 71
CZ07 | Existing | 69
CZ08 | Existing | 71
CZ09 | Existing | 71
CZ10 | Existing | 73
CZ11 | Existing | 75
CZ12 | Existing | 75
CZ13 | Existing | 75
CZ14 | Existing | 75
CZ15 | Existing | 75
CZ16 | Existing | 75
CZ01 | New Construction | 75
CZ02 | New Construction | 73
CZ03 | New Construction | 75
CZ04 | New Construction | 73
CZ05 | New Construction | 75
CZ06 | New Construction | 71
CZ07 | New Construction | 69
CZ08 | New Construction | 71
CZ09 | New Construction | 71
CZ10 | New Construction | 73
CZ11 | New Construction | 75
CZ12 | New Construction | 75
CZ13 | New Construction | 75
CZ14 | New Construction | 75
CZ15 | New Construction | 75
CZ16 | New Construction | 75

## Water Heater
Water Heater - Education - Secondary School
Vintage | Fuel type | Burner Efficiency | Maximum Heater Capacity (Btu/hr) | Tank Volume (gallon) | Tank Loss |  | Notes
[5 empty] | Off Cycle (W/K) | On Cycle (W/K)
Existing | Gas | 0.8 | 653407.65 | 137.03 | 1.6282 | 1.6282
New Construction | Gas | 0.8 | 653407.65 | 137.03 | 1.6282 | 1.6282
Peak Hot Water Consumption - Education - Secondary School
Space | Floor Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Notes
CLASSROOM E1 WEST PERIM (G.W1) | 3751.24 | 25 | 1.3504 | 33.7612 | 0.56269
CLASSROOM E2 NORTH PERIM (G.N3) | 2092.38 | 25 | 0.75326 | 18.8314 | 0.31386
CLASSROOM E2 SOUTH PERIM (G.S2) | 2092.38 | 25 | 0.75326 | 18.8314 | 0.31386
CLASSROOM E2 WEST PERIM (G.W1) | 1656.55 | 25 | 0 | 0 | 0
CLASSROOM E4 CORE (G.C6) | 1798.23 | 25 | 0.64736 | 16.1841 | 0.26973
CLASSROOM E4 EAST PERIM (G.E2) | 1619.41 | 25 | 0.58299 | 14.5747 | 0.24291
CLASSROOM E4 NORTH PERIM (G.N3) | 4148.61 | 25 | 0 | 0 | 0
CLASSROOM E4 SOUTH PERIM (G.S1) | 4148.61 | 25 | 1.4935 | 37.3375 | 0.62229
CLASSROOM E4 WEST PERIM (G.W4) | 1619.41 | 25 | 0.58299 | 14.5747 | 0.24291
COMPUTER CLASSROOM E4 CORE SPC (G.C5) | 770.67 | 1.5 | 0.27744 | 0.41616 | 0.006936
DINING E3 SW PERIM (G.SW1) | 5634 | 33.33 | 6.5136 | 217.0968 | 3.6183
E2 NORTH PERIM PLNM (G.N6) | 0 | 0 | 0 | 0 | 0
E2 SOUTH PERIM PLNM (G.S5) | 0 | 0 | 0 | 0 | 0
E2 WEST PERIM PLNM (G.W4) | 0 | 0 | 0 | 0 | 0
E4 CORE PLNM (G.C11) | 0 | 0 | 0 | 0 | 0
E4 CORE PLNM (G.C12) | 0 | 0 | 0 | 0 | 0
E4 EAST PERIM PLNM (G.E8) | 0 | 0 | 0 | 0 | 0
E4 NORTH PERIM PLNM (G.N9) | 0 | 0 | 0 | 0 | 0
E4 SOUTH PERIM PLNM (G.S7) | 0 | 0 | 0 | 0 | 0
E4 WEST PERIM PLNM (G.W10) | 0 | 0 | 0 | 0 | 0
GYMNASIUM E17 WEST PERIM (G.W1) | 22502.2 | 33.33 | 0 | 0 | 0
KITCHEN E3 NE PERIM (G.NE2) | 2629.64 | 2.5 | 3.0399 | 7.5997 | 0.12666
Total (22 Space)

## Raw_waterheater (hidden)
Vintage | Burner Efficiency | Maximum Heater Capacity (Btu/h) | Tank Volume (ft3) | Tank Loss_Off Cycle (W/K) | Tank Loss_On Cycle (W/K)
Existing | 0.8 | 653407.65 | 137.03 | 1.6282 | 1.6282
New Construction | 0.8 | 653407.65 | 137.03 | 1.6282 | 1.6282

## Raw_dhwpeakflowbyzone (hidden)
Space | Peak hot water usage (gal/hr) | Zone Name
Classroom E1 West Perim (G.W1) | 33.7612 | CLASSROOM E1 WEST PERIM (G.W1)
Classroom E2 North Perim (G.N3) | 18.8314 | CLASSROOM E2 NORTH PERIM (G.N3)
Classroom E2 South Perim (G.S2) | 18.8314 | CLASSROOM E2 SOUTH PERIM (G.S2)
Classroom E2 West Perim (G.W1) | 14.909 | CLASSROOM E1 WEST PERIM (G.W1)
Classroom E4 Core (G.C6) | 16.1841 | CLASSROOM E4 CORE (G.C6)
Classroom E4 East Perim (G.E2) | 14.5747 | CLASSROOM E4 EAST PERIM (G.E2)
Classroom E4 North Perim (G.N3) | 37.3375 | CLASSROOM E2 NORTH PERIM (G.N3)
Classroom E4 South Perim (G.S1) | 37.3375 | CLASSROOM E4 SOUTH PERIM (G.S1)
Classroom E4 West Perim (G.W4) | 14.5747 | CLASSROOM E4 WEST PERIM (G.W4)
Computer Classroom E4 Core Spc (G.C5) | 0.41616 | COMPUTER CLASSROOM E4 CORE SPC (G.C5)
Dining E3 SW Perim (G.SW1) | 217.0968 | DINING E3 SW PERIM (G.SW1)
Gymnasium E17 West Perim (G.W1) | 81.0079 | CLASSROOM E1 WEST PERIM (G.W1)
Kitchen E3 NE Perim (G.NE2) | 7.5997 | KITCHEN E3 NE PERIM (G.NE2)

## Interior Lights
Interior Lighting - Education - Secondary School
Vintage | Method | Zone type | Floor area (ft²) | Lighting Power Density (Watts/ft²) | Additional Lighting Power for Portable Lighting (Watts/ft²) | Technology | Notes
Existing | Space by space | Classroom_class | 22926.82 | 1.313 | NA | NA
Existing | Space by space | Computer | 770.67 | 1.1054 | NA | NA
Existing | Space by space | Dining_fast | 5634 | 1.2136 | NA | NA
Existing | Space by space | Gym | 22502.2 | 0.98463 | NA | NA
Existing | Space by space | Kitchen | 2629.64 | 1.6492 | NA | NA
New Construction | Space by space | Classroom_class | 22926.82 | 0.59992 | NA | NA
New Construction | Space by space | Computer | 770.67 | 0.49992 | NA | NA
New Construction | Space by space | Dining_fast | 5634 | 0.44995 | NA | NA
New Construction | Space by space | Gym | 22502.2 | 0.49992 | NA | NA
New Construction | Space by space | Kitchen | 2629.64 | 0.94987 | NA | NA

## Ext Lighting
Exterior Lighting - Education - Secondary School
Vintage | Non-Motion Controlled Luminaires (W) | Motion-Controlled Luminaires (W) | Total (W) | Notes
Existing | NA | NA | NA
New Consturction | NA | NA | NA

## Raw_interiorlights (hidden)
Vintage | Zone Type | Floor Area (ft2) | Lighting Power Density(W/ft2)
Existing | Classroom_class | 22926.82 | 1.313
Existing | Computer | 770.67 | 1.1054
Existing | Dining_fast | 5634 | 1.2136
Existing | Gym | 22502.2 | 0.98463
Existing | Kitchen | 2629.64 | 1.6492
New Construction | Classroom_class | 22926.82 | 0.59992
New Construction | Computer | 770.67 | 0.49992
New Construction | Dining_fast | 5634 | 0.44995
New Construction | Gym | 22502.2 | 0.49992
New Construction | Kitchen | 2629.64 | 0.94987

## Equipment
Equipment - Education - Secondary School
Zone Type | Floor Area (ft²) | Plug Load Intensity (W/ft²) | Gas Power Density (Btu/hr-ft²)
Classroom_class | 22926.82 | 0.99987 | 0
Computer | 770.67 | 19.9972 | 0
Dining_fast | 5634 | 0.74991 | 0
Gym | 22502.2 | 0.49992 | 0
Kitchen | 2629.64 | 7.7581 | 17.5354
Refrigeration - Education - Secondary School
Refrigeration System Name | Condenser Fan Power | Refrigeration System Working Fluid | Condenser Type
Elevator - Education - Secondary School
Vintage | No. of Elevators | Cab Lighting Power Limit | Lighting Shutoff | Cab Fan Control | Fan Power Limit | Regenerative Drive Threshold | Design load (W) | Note
Existing | - | - | - | - | - | - | -
New Construction | - | - | - | - | - | - | -

## Raw_equipment (hidden)
Vintage | Zone Type | Floor Area (ft2) | Plug Load Intensity (W/ft2)
Existing | Classroom_class | 22926.82 | 0.99987
Existing | Computer | 770.67 | 19.9972
Existing | Dining_fast | 5634 | 0.74991
Existing | Gym | 22502.2 | 0.49992
Existing | Kitchen | 2629.64 | 7.7581
New Construction | Classroom_class | 22926.82 | 0.99987
New Construction | Computer | 770.67 | 19.9972
New Construction | Dining_fast | 5634 | 0.74991
New Construction | Gym | 22502.2 | 0.49992
New Construction | Kitchen | 2629.64 | 7.7581

## Raw_gasequipment (hidden)
Vintage | Zone Name | Gas Loads (Btu/h-ft2) | Zone Type
Existing | Kitchen E3 NE Perim (G.NE2) | 17.5354 | Kitchen
New Construction | Kitchen E3 NE Perim (G.NE2) | 17.5354 | Kitchen

## Raw_refrigerationsystem (hidden)
Vintage | Refrigeration System Name | Condenser Fan Power | Working fluid | Condenser Type
No refrigeration system was found

## Schedules
Schedule by Hour - Education - Secondary School
Schedule Identifier | Space type | Type | Notes | Hour
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Cooling Setpoint Schedule | Computer room | AllDays | Cooling/Heating setpoints are in °F; others are intensity (0–100%) | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
DHW Sch | Computer room | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | Computer room | Weekdays |  | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.5 | 0.5 | 0.7 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0
Elec Equip Sch | Computer room | AllOtherDays (Through 1/31) |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Elec Equip Sch | Computer room | AllOtherDays (Through 2/28) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Elec Equip Sch | Computer room | AllOtherDays (Through 3/31) |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Elec Equip Sch | Computer room | AllOtherDays (Through 4/30) | bar: Hour 1 to Hour 24
Elec Equip Sch | Computer room | AllOtherDays (Through 5/31) |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Elec Equip Sch | Computer room | AllOtherDays (Through 6/30) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Elec Equip Sch | Computer room | AllOtherDays (Through 7/31) |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Elec Equip Sch | Computer room | AllOtherDays (Through 8/31) | bar: Hour 1 to Hour 24
Elec Equip Sch | Computer room | AllOtherDays (Through 9/30) |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Elec Equip Sch | Computer room | AllOtherDays (Through 10/31) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Elec Equip Sch | Computer room | AllOtherDays (Through 11/30) |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Elec Equip Sch | Computer room | AllOtherDays (Through 12/31) | bar: Hour 1 to Hour 24
Heating Setpoint Schedule | Computer room | AllDays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Infiltration Schedule | Computer room | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Computer room | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Computer room | Saturdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.15 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.2 | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Lighting Schedule | Computer room | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.7 | 0.8 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
OA Schedule | Computer room | AllDays | bar: Hour 1 to Hour 24
Occupant Sch | Computer room | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Occupant Sch | Computer room | Saturdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Occupant Sch | Computer room | Weekdays |  | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.25 | 0.65 | 0.65 | 0.65 | 0.65 | 0.6 | 0.6 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.25 | 0.1 | 0.05 | 0.05 | 0.05 | 0
Cooling Setpoint Schedule | Kitchen | AllOtherDays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Cooling Setpoint Schedule | Kitchen | Saturdays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Cooling Setpoint Schedule | Kitchen | Weekdays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | Kitchen | AllOtherDays |  | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
DHW Sch | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
DHW Sch | Kitchen | Weekdays |  | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
Elec Equip Sch | Kitchen | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | Kitchen | AllOtherDays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Elec Equip Sch | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Elec Equip Sch | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Heating Setpoint Schedule | Kitchen | AllOtherDays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Heating Setpoint Schedule | Kitchen | Saturdays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Heating Setpoint Schedule | Kitchen | Weekdays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | Kitchen | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Kitchen | AllOtherDays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
Lighting Schedule | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Lighting Schedule | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
OA Schedule | Kitchen | AllOtherDays |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OA Schedule | Kitchen | Saturdays |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OA Schedule | Kitchen | Weekdays |  | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Occupant Sch | Kitchen | AllOtherDays |  | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Occupant Sch | Kitchen | Saturdays |  | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
Occupant Sch | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Infiltration Schedule | Plenum | AllDays | bar: Hour 1 to Hour 24
Cooling Setpoint Schedule | Retail | AllOtherDays |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | Retail | Saturdays |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
Cooling Setpoint Schedule | Retail | Weekdays |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92
DHW Sch | Retail | AllOtherDays |  | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
DHW Sch | Retail | Saturday |  | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
DHW Sch | Retail | Weekdays |  | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08
Elec Equip Sch | Retail | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | Retail | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | Retail | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
Elec Equip Sch | Retail | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05
Heating Setpoint Schedule | Retail | AllOtherDays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | Retail | Saturdays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
Heating Setpoint Schedule | Retail | Weekdays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08
Infiltration Schedule | Retail | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Retail | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Retail | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
Lighting Schedule | Retail | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.55 | 0.55 | 0.5 | 0.2 | 0.05 | 0.05
OA Schedule | Retail | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OA Schedule | Retail | Saturdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OA Schedule | Retail | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
Occupant Sch | Retail | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Retail | Saturday |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
Occupant Sch | Retail | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
Cooling Setpoint Schedule | School | AllOtherDays (Through 1/11) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 4/3) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 4/12) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 5/22) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 5/31) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 8/7) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 8/16) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 12/11) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | AllOtherDays (Through 12/31) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Saturdays (Through 4/3) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Saturdays (Through 5/22) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Saturdays (Through 8/7) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Saturdays (Through 12/11) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Weekdays (Through 4/3) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Weekdays (Through 5/22) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Weekdays (Through 8/7) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
Cooling Setpoint Schedule | School | Weekdays (Through 12/11) |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
DHW Sch | School | AllOtherDays (Through 1/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | School | AllOtherDays (Through 4/3) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | AllOtherDays (Through 4/12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | School | AllOtherDays (Through 5/22) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | AllOtherDays (Through 5/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | School | AllOtherDays (Through 8/7) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | AllOtherDays (Through 8/16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | School | AllOtherDays (Through 12/11) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | AllOtherDays (Through 12/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | School | Saturdays (Through 4/3) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | Saturdays (Through 5/22) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | Saturdays (Through 8/7) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | Saturdays (Through 12/11) |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
DHW Sch | School | Weekdays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
DHW Sch | School | Weekdays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
DHW Sch | School | Weekdays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
DHW Sch | School | Weekdays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
Elec Equip Sch | School | AllOtherDays (Through 1/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | School | AllOtherDays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | AllOtherDays (Through 4/12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | School | AllOtherDays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | AllOtherDays (Through 5/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | School | AllOtherDays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | AllOtherDays (Through 8/16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | School | AllOtherDays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | AllOtherDays (Through 12/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | School | Saturdays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | Saturdays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | Saturdays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | Saturdays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | School | Weekdays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Elec Equip Sch | School | Weekdays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Elec Equip Sch | School | Weekdays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Elec Equip Sch | School | Weekdays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Heating Setpoint Schedule | School | AllOtherDays (Through 1/11) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 4/3) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 4/12) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 5/22) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 5/31) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 8/7) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 8/16) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 12/11) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | AllOtherDays (Through 12/31) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | Saturdays (Through 4/3) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | Saturdays (Through 5/22) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | Saturdays (Through 8/7) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | Saturdays (Through 12/11) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | School | Weekdays (Through 4/3) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
Heating Setpoint Schedule | School | Weekdays (Through 5/22) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
Heating Setpoint Schedule | School | Weekdays (Through 8/7) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
Heating Setpoint Schedule | School | Weekdays (Through 12/11) |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
Infiltration Schedule | School | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | School | AllOtherDays (Through 1/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting Schedule | School | AllOtherDays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | AllOtherDays (Through 4/12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting Schedule | School | AllOtherDays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | AllOtherDays (Through 5/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting Schedule | School | AllOtherDays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | AllOtherDays (Through 8/16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting Schedule | School | AllOtherDays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | AllOtherDays (Through 12/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lighting Schedule | School | Saturdays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | Saturdays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | Saturdays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | Saturdays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | School | Weekdays (Through 4/3) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Lighting Schedule | School | Weekdays (Through 5/22) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Lighting Schedule | School | Weekdays (Through 8/7) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
Lighting Schedule | School | Weekdays (Through 12/11) |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
OA Schedule | School | AllOtherDays (Through 1/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 4/12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 5/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 8/16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | AllOtherDays (Through 12/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | Saturdays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | Saturdays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | Saturdays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | Saturdays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | School | Weekdays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OA Schedule | School | Weekdays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OA Schedule | School | Weekdays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OA Schedule | School | Weekdays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 1/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 4/12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 5/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 8/16) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | AllOtherDays (Through 12/31) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | Saturdays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | Saturdays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | Saturdays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | Saturdays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | School | Weekdays (Through 4/3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
Occupant Sch | School | Weekdays (Through 5/22) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
Occupant Sch | School | Weekdays (Through 8/7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
Occupant Sch | School | Weekdays (Through 12/11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0

## Schedule_Figures
Schedule Figures (linked to Schedules tab)

## Raw_schedule (hidden)
Schedule Identifier | Schedule Name | Type | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Computer room | Cooling Setpoint Schedule | AllDays | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
Computer room | DHW Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Computer room | DHW Sch | Weekdays | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.5 | 0.5 | 0.7 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0
Computer room | Elec Equip Sch | AllOtherDays (Through 1/31) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Computer room | Elec Equip Sch | AllOtherDays (Through 2/28) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Computer room | Elec Equip Sch | AllOtherDays (Through 3/31) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Computer room | Elec Equip Sch | AllOtherDays (Through 4/30) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Computer room | Elec Equip Sch | AllOtherDays (Through 5/31) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Computer room | Elec Equip Sch | AllOtherDays (Through 6/30) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Computer room | Elec Equip Sch | AllOtherDays (Through 7/31) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Computer room | Elec Equip Sch | AllOtherDays (Through 8/31) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Computer room | Elec Equip Sch | AllOtherDays (Through 9/30) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Computer room | Elec Equip Sch | AllOtherDays (Through 10/31) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Computer room | Elec Equip Sch | AllOtherDays (Through 11/30) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Computer room | Elec Equip Sch | AllOtherDays (Through 12/31) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Computer room | Heating Setpoint Schedule | AllDays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Computer room | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Computer room | Lighting Schedule | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
Computer room | Lighting Schedule | Saturdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.15 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.2 | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Computer room | Lighting Schedule | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.7 | 0.8 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Computer room | OA Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Computer room | Occupant Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Computer room | Occupant Sch | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Computer room | Occupant Sch | Weekdays | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.25 | 0.65 | 0.65 | 0.65 | 0.65 | 0.6 | 0.6 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.25 | 0.1 | 0.05 | 0.05 | 0.05 | 0
Kitchen | Cooling Setpoint Schedule | AllOtherDays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | Cooling Setpoint Schedule | Saturdays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | Cooling Setpoint Schedule | Weekdays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | DHW Sch | AllOtherDays | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Kitchen | DHW Sch | Saturdays | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
Kitchen | DHW Sch | Weekdays | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
Kitchen | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Elec Equip Sch | AllOtherDays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Kitchen | Elec Equip Sch | Saturdays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Kitchen | Elec Equip Sch | Weekdays | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Kitchen | Heating Setpoint Schedule | AllOtherDays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Heating Setpoint Schedule | Saturdays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Heating Setpoint Schedule | Weekdays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Lighting Schedule | AllOtherDays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
Kitchen | Lighting Schedule | Saturdays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Kitchen | Lighting Schedule | Weekdays | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Kitchen | OA Schedule | AllOtherDays | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | OA Schedule | Saturdays | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | OA Schedule | Weekdays | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Occupant Sch | AllOtherDays | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Kitchen | Occupant Sch | Saturdays | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
Kitchen | Occupant Sch | Weekdays | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Plenum | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retail | Cooling Setpoint Schedule | AllOtherDays | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Retail | Cooling Setpoint Schedule | Saturdays | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
Retail | Cooling Setpoint Schedule | Weekdays | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92
Retail | DHW Sch | AllOtherDays | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06
Retail | DHW Sch | Saturday | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13
Retail | DHW Sch | Weekdays | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08
Retail | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retail | Elec Equip Sch | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Retail | Elec Equip Sch | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
Retail | Elec Equip Sch | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05
Retail | Heating Setpoint Schedule | AllOtherDays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Retail | Heating Setpoint Schedule | Saturdays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
Retail | Heating Setpoint Schedule | Weekdays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08
Retail | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Retail | Lighting Schedule | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Retail | Lighting Schedule | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
Retail | Lighting Schedule | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.55 | 0.55 | 0.5 | 0.2 | 0.05 | 0.05
Retail | OA Schedule | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Retail | OA Schedule | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Retail | OA Schedule | Weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
Retail | Occupant Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
Retail | Occupant Sch | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
Retail | Occupant Sch | Weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
School | Cooling Setpoint Schedule | AllOtherDays (Through 1/11) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 4/3) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 4/12) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 5/22) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 5/31) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 8/7) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 8/16) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 12/11) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | AllOtherDays (Through 12/31) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Saturdays (Through 4/3) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Saturdays (Through 5/22) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Saturdays (Through 8/7) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Saturdays (Through 12/11) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Weekdays (Through 4/3) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Weekdays (Through 5/22) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Weekdays (Through 8/7) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
School | Cooling Setpoint Schedule | Weekdays (Through 12/11) | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92
School | DHW Sch | AllOtherDays (Through 1/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | DHW Sch | AllOtherDays (Through 4/3) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | AllOtherDays (Through 4/12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | DHW Sch | AllOtherDays (Through 5/22) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | AllOtherDays (Through 5/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | DHW Sch | AllOtherDays (Through 8/7) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | AllOtherDays (Through 8/16) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | DHW Sch | AllOtherDays (Through 12/11) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | AllOtherDays (Through 12/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | DHW Sch | Saturdays (Through 4/3) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | Saturdays (Through 5/22) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | Saturdays (Through 8/7) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | Saturdays (Through 12/11) | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
School | DHW Sch | Weekdays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
School | DHW Sch | Weekdays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
School | DHW Sch | Weekdays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
School | DHW Sch | Weekdays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
School | Elec Equip Sch | AllOtherDays (Through 1/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Elec Equip Sch | AllOtherDays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | AllOtherDays (Through 4/12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Elec Equip Sch | AllOtherDays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | AllOtherDays (Through 5/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Elec Equip Sch | AllOtherDays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | AllOtherDays (Through 8/16) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Elec Equip Sch | AllOtherDays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | AllOtherDays (Through 12/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Elec Equip Sch | Saturdays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | Saturdays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | Saturdays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | Saturdays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Elec Equip Sch | Weekdays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Elec Equip Sch | Weekdays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Elec Equip Sch | Weekdays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Elec Equip Sch | Weekdays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.85 | 0.95 | 0.95 | 0.95 | 0.8 | 0.8 | 0.8 | 0.7 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Heating Setpoint Schedule | AllOtherDays (Through 1/11) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 4/3) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 4/12) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 5/22) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 5/31) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 8/7) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 8/16) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 12/11) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | AllOtherDays (Through 12/31) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | Saturdays (Through 4/3) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | Saturdays (Through 5/22) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | Saturdays (Through 8/7) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | Saturdays (Through 12/11) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
School | Heating Setpoint Schedule | Weekdays (Through 4/3) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
School | Heating Setpoint Schedule | Weekdays (Through 5/22) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
School | Heating Setpoint Schedule | Weekdays (Through 8/7) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
School | Heating Setpoint Schedule | Weekdays (Through 12/11) | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08
School | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
School | Lighting Schedule | AllOtherDays (Through 1/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Lighting Schedule | AllOtherDays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | AllOtherDays (Through 4/12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Lighting Schedule | AllOtherDays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | AllOtherDays (Through 5/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Lighting Schedule | AllOtherDays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | AllOtherDays (Through 8/16) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Lighting Schedule | AllOtherDays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | AllOtherDays (Through 12/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Lighting Schedule | Saturdays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | Saturdays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | Saturdays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | Saturdays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
School | Lighting Schedule | Weekdays (Through 4/3) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Lighting Schedule | Weekdays (Through 5/22) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Lighting Schedule | Weekdays (Through 8/7) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | Lighting Schedule | Weekdays (Through 12/11) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.3 | 0.6 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.05 | 0.05
School | OA Schedule | AllOtherDays (Through 1/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 4/12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 5/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 8/16) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | AllOtherDays (Through 12/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | Saturdays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | Saturdays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | Saturdays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | Saturdays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | OA Schedule | Weekdays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
School | OA Schedule | Weekdays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
School | OA Schedule | Weekdays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
School | OA Schedule | Weekdays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 1/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 4/12) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 5/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 8/16) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | AllOtherDays (Through 12/31) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | Saturdays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | Saturdays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | Saturdays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | Saturdays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
School | Occupant Sch | Weekdays (Through 4/3) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
School | Occupant Sch | Weekdays (Through 5/22) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
School | Occupant Sch | Weekdays (Through 8/7) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0
School | Occupant Sch | Weekdays (Through 12/11) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.75 | 0.9 | 0.9 | 0.8 | 0.8 | 0.8 | 0.8 | 0.45 | 0.15 | 0.05 | 0.15 | 0.2 | 0.2 | 0.1 | 0 | 0

## Energy Usage
Energy Consumption - Education - Secondary School
Climate Zone | HVAC Type | Vintage | Total Floorspace (Excluding Plenums and Crawl Space) (ft²) | Annual Electricity Intensity (kBtu/ft²) | Annual Gas Intensity (kBtu/ft²) | Notes
CZ01 | cAVVG | Existing | 54463.33 | 40.2265 | 36.4408
CZ01 | cAVVG | New Construction | 54463.33 | 31.6079 | 37.4625
CZ01 | cDXGF | Existing | 54463.33 | 42.8688 | 34.8279
CZ01 | cDXGF | New Construction | 54463.33 | 32.8839 | 36.2366
CZ01 | cDXHP | Existing | 54463.33 | 43.3105 | 33.0286
CZ01 | cDXHP | New Construction | 54463.33 | 33.4322 | 33.9826
CZ01 | cDXOH | Existing | 54463.33 | 42.8601 | 33.1055
CZ01 | cDXOH | New Construction | 54463.33 | 32.8587 | 34.1563
CZ01 | cPVVG | Existing | 54463.33 | 40.1815 | 35.9702
CZ01 | cPVVG | New Construction | 54463.33 | 31.0188 | 37.3022
CZ02 | cAVVG | Existing | 54463.33 | 46.7577 | 29.7304
CZ02 | cAVVG | New Construction | 54463.33 | 38.5727 | 32.428
CZ02 | cDXGF | Existing | 54463.33 | 49.2103 | 28.4618
CZ02 | cDXGF | New Construction | 54463.33 | 40.0157 | 31.0417
CZ02 | cDXHP | Existing | 54463.33 | 49.5329 | 27.237
CZ02 | cDXHP | New Construction | 54463.33 | 40.5038 | 29.1193
CZ02 | cDXOH | Existing | 54463.33 | 49.2009 | 27.2796
CZ02 | cDXOH | New Construction | 54463.33 | 39.9983 | 29.2098
CZ02 | cPVVG | Existing | 54463.33 | 46.2201 | 29.2059
CZ02 | cPVVG | New Construction | 54463.33 | 37.7534 | 31.8619
CZ03 | cAVVG | Existing | 54463.33 | 43.8561 | 25.8902
CZ03 | cAVVG | New Construction | 54463.33 | 35.5707 | 28.2781
CZ03 | cDXGF | Existing | 54463.33 | 46.5832 | 25.0345
CZ03 | cDXGF | New Construction | 54463.33 | 37.4085 | 27.3392
CZ03 | cDXHP | Existing | 54463.33 | 46.7283 | 24.4037
CZ03 | cDXHP | New Construction | 54463.33 | 37.6857 | 26.164
CZ03 | cDXOH | Existing | 54463.33 | 46.5791 | 24.4203
CZ03 | cDXOH | New Construction | 54463.33 | 37.394 | 26.2148
CZ03 | cPVVG | Existing | 54463.33 | 43.7448 | 25.5379
CZ03 | cPVVG | New Construction | 54463.33 | 35.2755 | 27.9896
CZ04 | cAVVG | Existing | 54463.33 | 47.7732 | 24.7034
CZ04 | cAVVG | New Construction | 54463.33 | 39.1354 | 26.4339
CZ04 | cDXGF | Existing | 54463.33 | 50.2957 | 23.8582
CZ04 | cDXGF | New Construction | 54463.33 | 40.7319 | 25.5176
CZ04 | cDXHP | Existing | 54463.33 | 50.4309 | 23.2722
CZ04 | cDXHP | New Construction | 54463.33 | 40.9734 | 24.4941
CZ04 | cDXOH | Existing | 54463.33 | 50.2911 | 23.2873
CZ04 | cDXOH | New Construction | 54463.33 | 40.7186 | 24.5318
CZ04 | cPVVG | Existing | 54463.33 | 47.2841 | 24.3312
CZ04 | cPVVG | New Construction | 54463.33 | 38.477 | 26.0957
CZ05 | cAVVG | Existing | 54463.33 | 44.6163 | 25.4569
CZ05 | cAVVG | New Construction | 54463.33 | 36.0651 | 27.5359
CZ05 | cDXGF | Existing | 54463.33 | 47.184 | 24.6635
CZ05 | cDXGF | New Construction | 54463.33 | 37.7911 | 26.6097
CZ05 | cDXHP | Existing | 54463.33 | 47.328 | 24.0782
CZ05 | cDXHP | New Construction | 54463.33 | 38.0542 | 25.5294
CZ05 | cDXOH | Existing | 54463.33 | 47.1741 | 24.0898
CZ05 | cDXOH | New Construction | 54463.33 | 37.7674 | 25.5682
CZ05 | cPVVG | Existing | 54463.33 | 44.4354 | 25.0901
CZ05 | cPVVG | New Construction | 54463.33 | 35.7273 | 27.1859
CZ06 | cAVVG | Existing | 54463.33 | 47.6736 | 19.3635
CZ06 | cAVVG | New Construction | 54463.33 | 38.6941 | 20.2582
CZ06 | cDXGF | Existing | 54463.33 | 49.4079 | 19.0868
CZ06 | cDXGF | New Construction | 54463.33 | 39.788 | 19.8036
CZ06 | cDXHP | Existing | 54463.33 | 49.3587 | 18.9793
CZ06 | cDXHP | New Construction | 54463.33 | 39.7767 | 19.5622
CZ06 | cDXOH | Existing | 54463.33 | 49.4066 | 18.9804
CZ06 | cDXOH | New Construction | 54463.33 | 39.7831 | 19.5711
CZ06 | cPVVG | Existing | 54463.33 | 46.7406 | 19.2187
CZ06 | cPVVG | New Construction | 54463.33 | 37.7388 | 20.0147
CZ07 | cAVVG | Existing | 54463.33 | 48.4393 | 19.1686
CZ07 | cAVVG | New Construction | 54463.33 | 39.1967 | 19.9209
CZ07 | cDXGF | Existing | 54463.33 | 49.823 | 18.8497
CZ07 | cDXGF | New Construction | 54463.33 | 40.0058 | 19.4007
CZ07 | cDXHP | Existing | 54463.33 | 49.7957 | 18.735
CZ07 | cDXHP | New Construction | 54463.33 | 40.0097 | 19.1733
CZ07 | cDXOH | Existing | 54463.33 | 49.8212 | 18.7369
CZ07 | cDXOH | New Construction | 54463.33 | 40.0015 | 19.1806
CZ07 | cPVVG | Existing | 54463.33 | 47.0925 | 18.9769
CZ07 | cPVVG | New Construction | 54463.33 | 37.9432 | 19.5953
CZ08 | cAVVG | Existing | 54463.33 | 50.2403 | 19.8352
CZ08 | cAVVG | New Construction | 54463.33 | 41.3249 | 20.7375
CZ08 | cDXGF | Existing | 54463.33 | 51.9884 | 19.4095
CZ08 | cDXGF | New Construction | 54463.33 | 42.2917 | 20.1466
CZ08 | cDXHP | Existing | 54463.33 | 52.0004 | 19.244
CZ08 | cDXHP | New Construction | 54463.33 | 42.348 | 19.8179
CZ08 | cDXOH | Existing | 54463.33 | 51.9853 | 19.2455
CZ08 | cDXOH | New Construction | 54463.33 | 42.2841 | 19.8294
CZ08 | cPVVG | Existing | 54463.33 | 49.07 | 19.5782
CZ08 | cPVVG | New Construction | 54463.33 | 40.0999 | 20.4013
CZ09 | cAVVG | Existing | 54463.33 | 52.2652 | 19.228
CZ09 | cAVVG | New Construction | 54463.33 | 42.7364 | 19.8523
CZ09 | cDXGF | Existing | 54463.33 | 54.1098 | 18.7995
CZ09 | cDXGF | New Construction | 54463.33 | 43.7086 | 19.2755
CZ09 | cDXHP | Existing | 54463.33 | 54.1047 | 18.6827
CZ09 | cDXHP | New Construction | 54463.33 | 43.7348 | 19.0335
CZ09 | cDXOH | Existing | 54463.33 | 54.1075 | 18.6844
CZ09 | cDXOH | New Construction | 54463.33 | 43.7025 | 19.0401
CZ09 | cPVVG | Existing | 54463.33 | 50.9957 | 18.9419
CZ09 | cPVVG | New Construction | 54463.33 | 41.4411 | 19.4888
CZ10 | cAVVG | Existing | 54463.33 | 55.7914 | 21.6792
CZ10 | cAVVG | New Construction | 54463.33 | 46.28 | 22.3787
CZ10 | cDXGF | Existing | 54463.33 | 57.4702 | 20.9726
CZ10 | cDXGF | New Construction | 54463.33 | 47.2071 | 21.6384
CZ10 | cDXHP | Existing | 54463.33 | 57.6052 | 20.483
CZ10 | cDXHP | New Construction | 54463.33 | 47.398 | 20.9181
CZ10 | cDXOH | Existing | 54463.33 | 57.4614 | 20.4942
CZ10 | cDXOH | New Construction | 54463.33 | 47.1906 | 20.9364
CZ10 | cPVVG | Existing | 54463.33 | 54.3271 | 21.3133
CZ10 | cPVVG | New Construction | 54463.33 | 44.8511 | 22.0173
CZ11 | cAVVG | Existing | 54463.33 | 56.6625 | 27.5393
CZ11 | cAVVG | New Construction | 54463.33 | 42.89 | 26.6233
CZ11 | cDXGF | Existing | 54463.33 | 58.7016 | 26.2311
CZ11 | cDXGF | New Construction | 54463.33 | 43.3816 | 25.7812
CZ11 | cDXHP | Existing | 54463.33 | 59.0464 | 25.0287
CZ11 | cDXHP | New Construction | 54463.33 | 43.7351 | 24.5135
CZ11 | cDXOH | Existing | 54463.33 | 58.7022 | 25.0794
CZ11 | cDXOH | New Construction | 54463.33 | 43.3565 | 24.6055
CZ11 | cPVVG | Existing | 54463.33 | 55.366 | 27.0002
CZ11 | cPVVG | New Construction | 54463.33 | 41.4655 | 26.3574
CZ12 | cAVVG | Existing | 54463.33 | 53.3502 | 27.3231
CZ12 | cAVVG | New Construction | 54463.33 | 40.9281 | 26.8622
CZ12 | cDXGF | Existing | 54463.33 | 55.0245 | 26.2063
CZ12 | cDXGF | New Construction | 54463.33 | 41.2754 | 26.2045
CZ12 | cDXHP | Existing | 54463.33 | 55.3274 | 25.1163
CZ12 | cDXHP | New Construction | 54463.33 | 41.6139 | 24.9543
CZ12 | cDXOH | Existing | 54463.33 | 55.0223 | 25.162
CZ12 | cDXOH | New Construction | 54463.33 | 41.2496 | 25.0415
CZ12 | cPVVG | Existing | 54463.33 | 52.0163 | 26.859
CZ12 | cPVVG | New Construction | 54463.33 | 39.4129 | 26.7237
CZ13 | cAVVG | Existing | 54463.33 | 57.8464 | 24.6646
CZ13 | cAVVG | New Construction | 54463.33 | 44.1166 | 24.5098
CZ13 | cDXGF | Existing | 54463.33 | 59.568 | 23.721
CZ13 | cDXGF | New Construction | 54463.33 | 44.3979 | 23.8498
CZ13 | cDXHP | Existing | 54463.33 | 59.7902 | 22.9277
CZ13 | cDXHP | New Construction | 54463.33 | 44.6539 | 22.8978
CZ13 | cDXOH | Existing | 54463.33 | 59.5651 | 22.9623
CZ13 | cDXOH | New Construction | 54463.33 | 44.3771 | 22.971
CZ13 | cPVVG | Existing | 54463.33 | 56.3245 | 24.2671
CZ13 | cPVVG | New Construction | 54463.33 | 42.5138 | 24.3047
CZ14 | cAVVG | Existing | 54463.33 | 62.059 | 21.0445
CZ14 | cAVVG | New Construction | 54463.33 | 47.9576 | 21.0138
CZ14 | cDXGF | Existing | 54463.33 | 64.0012 | 20.3666
CZ14 | cDXGF | New Construction | 54463.33 | 48.3135 | 20.4542
CZ14 | cDXHP | Existing | 54463.33 | 64.1385 | 19.9506
CZ14 | cDXHP | New Construction | 54463.33 | 48.4706 | 19.9357
CZ14 | cDXOH | Existing | 54463.33 | 63.9961 | 19.9621
CZ14 | cDXOH | New Construction | 54463.33 | 48.2974 | 19.9645
CZ14 | cPVVG | Existing | 54463.33 | 60.4969 | 20.7032
CZ14 | cPVVG | New Construction | 54463.33 | 46.3112 | 20.7619
CZ15 | cAVVG | Existing | 54463.33 | 70.0413 | 16.6278
CZ15 | cAVVG | New Construction | 54463.33 | 54.5668 | 16.6585
CZ15 | cDXGF | Existing | 54463.33 | 70.6993 | 16.2686
CZ15 | cDXGF | New Construction | 54463.33 | 53.6793 | 16.2527
CZ15 | cDXHP | Existing | 54463.33 | 70.7353 | 16.1431
CZ15 | cDXHP | New Construction | 54463.33 | 53.732 | 16.0699
CZ15 | cDXOH | Existing | 54463.33 | 70.6955 | 16.1452
CZ15 | cDXOH | New Construction | 54463.33 | 53.6644 | 16.0754
CZ15 | cPVVG | Existing | 54463.33 | 67.3955 | 16.3852
CZ15 | cPVVG | New Construction | 54463.33 | 51.9314 | 16.37
CZ16 | cAVVG | Existing | 54463.33 | 55.8071 | 31.58
CZ16 | cAVVG | New Construction | 54463.33 | 42.8762 | 30.6849
CZ16 | cDXGF | Existing | 54463.33 | 57.8692 | 30.1061
CZ16 | cDXGF | New Construction | 54463.33 | 43.393 | 29.8872
CZ16 | cDXHP | Existing | 54463.33 | 58.4743 | 28.4818
CZ16 | cDXHP | New Construction | 54463.33 | 44.028 | 28.0856
CZ16 | cDXOH | Existing | 54463.33 | 57.888 | 28.5494
CZ16 | cDXOH | New Construction | 54463.33 | 43.3663 | 28.2083
CZ16 | cPVVG | Existing | 54463.33 | 54.4584 | 30.9937
CZ16 | cPVVG | New Construction | 54463.33 | 41.3118 | 30.57

## Energy Usage_Figures
Energy Figures (from 'Energy Usage' Tab)
cAVVG ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cAVVG ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 40.2265 | 31.6079 | CZ01 | 36.4408 | 37.4625
CZ02 | 46.7577 | 38.5727 | CZ02 | 29.7304 | 32.428
CZ03 | 43.8561 | 35.5707 | CZ03 | 25.8902 | 28.2781
CZ04 | 47.7732 | 39.1354 | CZ04 | 24.7034 | 26.4339
CZ05 | 44.6163 | 36.0651 | CZ05 | 25.4569 | 27.5359
CZ06 | 47.6736 | 38.6941 | CZ06 | 19.3635 | 20.2582
CZ07 | 48.4393 | 39.1967 | CZ07 | 19.1686 | 19.9209
CZ08 | 50.2403 | 41.3249 | CZ08 | 19.8352 | 20.7375
CZ09 | 52.2652 | 42.7364 | CZ09 | 19.228 | 19.8523
CZ10 | 55.7914 | 46.28 | CZ10 | 21.6792 | 22.3787
CZ11 | 56.6625 | 42.89 | CZ11 | 27.5393 | 26.6233
CZ12 | 53.3502 | 40.9281 | CZ12 | 27.3231 | 26.8622
CZ13 | 57.8464 | 44.1166 | CZ13 | 24.6646 | 24.5098
CZ14 | 62.059 | 47.9576 | CZ14 | 21.0445 | 21.0138
CZ15 | 70.0413 | 54.5668 | CZ15 | 16.6278 | 16.6585
CZ16 | 55.8071 | 42.8762 | CZ16 | 31.58 | 30.6849
cDXGF ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXGF ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 42.8688 | 32.8839 | CZ01 | 34.8279 | 36.2366
CZ02 | 49.2103 | 40.0157 | CZ02 | 28.4618 | 31.0417
CZ03 | 46.5832 | 37.4085 | CZ03 | 25.0345 | 27.3392
CZ04 | 50.2957 | 40.7319 | CZ04 | 23.8582 | 25.5176
CZ05 | 47.184 | 37.7911 | CZ05 | 24.6635 | 26.6097
CZ06 | 49.4079 | 39.788 | CZ06 | 19.0868 | 19.8036
CZ07 | 49.823 | 40.0058 | CZ07 | 18.8497 | 19.4007
CZ08 | 51.9884 | 42.2917 | CZ08 | 19.4095 | 20.1466
CZ09 | 54.1098 | 43.7086 | CZ09 | 18.7995 | 19.2755
CZ10 | 57.4702 | 47.2071 | CZ10 | 20.9726 | 21.6384
CZ11 | 58.7016 | 43.3816 | CZ11 | 26.2311 | 25.7812
CZ12 | 55.0245 | 41.2754 | CZ12 | 26.2063 | 26.2045
CZ13 | 59.568 | 44.3979 | CZ13 | 23.721 | 23.8498
CZ14 | 64.0012 | 48.3135 | CZ14 | 20.3666 | 20.4542
CZ15 | 70.6993 | 53.6793 | CZ15 | 16.2686 | 16.2527
CZ16 | 57.8692 | 43.393 | CZ16 | 30.1061 | 29.8872
cDXHP ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXHP ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 43.3105 | 33.4322 | CZ01 | 33.0286 | 33.9826
CZ02 | 49.5329 | 40.5038 | CZ02 | 27.237 | 29.1193
CZ03 | 46.7283 | 37.6857 | CZ03 | 24.4037 | 26.164
CZ04 | 50.4309 | 40.9734 | CZ04 | 23.2722 | 24.4941
CZ05 | 47.328 | 38.0542 | CZ05 | 24.0782 | 25.5294
CZ06 | 49.3587 | 39.7767 | CZ06 | 18.9793 | 19.5622
CZ07 | 49.7957 | 40.0097 | CZ07 | 18.735 | 19.1733
CZ08 | 52.0004 | 42.348 | CZ08 | 19.244 | 19.8179
CZ09 | 54.1047 | 43.7348 | CZ09 | 18.6827 | 19.0335
CZ10 | 57.6052 | 47.398 | CZ10 | 20.483 | 20.9181
CZ11 | 59.0464 | 43.7351 | CZ11 | 25.0287 | 24.5135
CZ12 | 55.3274 | 41.6139 | CZ12 | 25.1163 | 24.9543
CZ13 | 59.7902 | 44.6539 | CZ13 | 22.9277 | 22.8978
CZ14 | 64.1385 | 48.4706 | CZ14 | 19.9506 | 19.9357
CZ15 | 70.7353 | 53.732 | CZ15 | 16.1431 | 16.0699
CZ16 | 58.4743 | 44.028 | CZ16 | 28.4818 | 28.0856
cDXOH ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXOH ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 42.8601 | 32.8587 | CZ01 | 33.1055 | 34.1563
CZ02 | 49.2009 | 39.9983 | CZ02 | 27.2796 | 29.2098
CZ03 | 46.5791 | 37.394 | CZ03 | 24.4203 | 26.2148
CZ04 | 50.2911 | 40.7186 | CZ04 | 23.2873 | 24.5318
CZ05 | 47.1741 | 37.7674 | CZ05 | 24.0898 | 25.5682
CZ06 | 49.4066 | 39.7831 | CZ06 | 18.9804 | 19.5711
CZ07 | 49.8212 | 40.0015 | CZ07 | 18.7369 | 19.1806
CZ08 | 51.9853 | 42.2841 | CZ08 | 19.2455 | 19.8294
CZ09 | 54.1075 | 43.7025 | CZ09 | 18.6844 | 19.0401
CZ10 | 57.4614 | 47.1906 | CZ10 | 20.4942 | 20.9364
CZ11 | 58.7022 | 43.3565 | CZ11 | 25.0794 | 24.6055
CZ12 | 55.0223 | 41.2496 | CZ12 | 25.162 | 25.0415
CZ13 | 59.5651 | 44.3771 | CZ13 | 22.9623 | 22.971
CZ14 | 63.9961 | 48.2974 | CZ14 | 19.9621 | 19.9645
CZ15 | 70.6955 | 53.6644 | CZ15 | 16.1452 | 16.0754
CZ16 | 57.888 | 43.3663 | CZ16 | 28.5494 | 28.2083
cPVVG ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cPVVG ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 40.1815 | 31.0188 | CZ01 | 35.9702 | 37.3022
CZ02 | 46.2201 | 37.7534 | CZ02 | 29.2059 | 31.8619
CZ03 | 43.7448 | 35.2755 | CZ03 | 25.5379 | 27.9896
CZ04 | 47.2841 | 38.477 | CZ04 | 24.3312 | 26.0957
CZ05 | 44.4354 | 35.7273 | CZ05 | 25.0901 | 27.1859
CZ06 | 46.7406 | 37.7388 | CZ06 | 19.2187 | 20.0147
CZ07 | 47.0925 | 37.9432 | CZ07 | 18.9769 | 19.5953
CZ08 | 49.07 | 40.0999 | CZ08 | 19.5782 | 20.4013
CZ09 | 50.9957 | 41.4411 | CZ09 | 18.9419 | 19.4888
CZ10 | 54.3271 | 44.8511 | CZ10 | 21.3133 | 22.0173
CZ11 | 55.366 | 41.4655 | CZ11 | 27.0002 | 26.3574
CZ12 | 52.0163 | 39.4129 | CZ12 | 26.859 | 26.7237
CZ13 | 56.3245 | 42.5138 | CZ13 | 24.2671 | 24.3047
CZ14 | 60.4969 | 46.3112 | CZ14 | 20.7032 | 20.7619
CZ15 | 67.3955 | 51.9314 | CZ15 | 16.3852 | 16.37
CZ16 | 54.4584 | 41.3118 | CZ16 | 30.9937 | 30.57

## Raw_totalendusesannual (hidden)
Vintage | Climate Zone | HVAC System | Electricity (kBtu) | Natural Gas (kBtu)
Existing | CZ01 | cAVVG | 2190868.74 | 1984688.69
Existing | CZ02 | cAVVG | 2546577.91 | 1619218.6
Existing | CZ03 | cAVVG | 2388547.87 | 1410067.65
Existing | CZ04 | cAVVG | 2601884.93 | 1345428.98
Existing | CZ05 | cAVVG | 2429953.56 | 1386468.19
Existing | CZ06 | cAVVG | 2596461.66 | 1054601.5
Existing | CZ07 | cAVVG | 2638165.13 | 1043986.84
Existing | CZ08 | cAVVG | 2736255.27 | 1080289.76
Existing | CZ09 | cAVVG | 2846535.57 | 1047223.38
Existing | CZ10 | cAVVG | 3038588.07 | 1180723.26
Existing | CZ11 | cAVVG | 3086030.78 | 1499880.77
Existing | CZ12 | cAVVG | 2905628.76 | 1488109.72
Existing | CZ13 | cAVVG | 3150506.41 | 1343314.54
Existing | CZ14 | cAVVG | 3379940.76 | 1146154.57
Existing | CZ15 | cAVVG | 3814684.06 | 905604.03
Existing | CZ16 | cAVVG | 3039440.99 | 1719949.97
New Construction | CZ01 | cAVVG | 1721470.83 | 2040332.36
New Construction | CZ02 | cAVVG | 2100795.15 | 1766134.66
New Construction | CZ03 | cAVVG | 1937297.23 | 1540121.01
New Construction | CZ04 | cAVVG | 2131443.81 | 1439676.12
New Construction | CZ05 | cAVVG | 1964224.14 | 1499698.78
New Construction | CZ06 | cAVVG | 2107408.92 | 1103329.4
New Construction | CZ07 | cAVVG | 2134781.84 | 1084957.19
New Construction | CZ08 | cAVVG | 2250689.93 | 1129432.6
New Construction | CZ09 | cAVVG | 2327569.19 | 1081221.3
New Construction | CZ10 | cAVVG | 2520565.56 | 1218816.77
New Construction | CZ11 | cAVVG | 2335932.64 | 1449995.19
New Construction | CZ12 | cAVVG | 2229082.85 | 1463006.41
New Construction | CZ13 | cAVVG | 2402734.97 | 1334884.69
New Construction | CZ14 | cAVVG | 2611932.89 | 1144479.17
New Construction | CZ15 | cAVVG | 2971889.29 | 907275.37
New Construction | CZ16 | cAVVG | 2335180.3 | 1671199.75
Existing | CZ01 | cDXGF | 2334779.17 | 1896844.63
Existing | CZ02 | cDXGF | 2680159.16 | 1550124.05
Existing | CZ03 | cDXGF | 2537075.53 | 1363461.17
Existing | CZ04 | cDXGF | 2739269.35 | 1299396.42
Existing | CZ05 | cDXGF | 2569796.44 | 1343257.49
Existing | CZ06 | cDXGF | 2690916.69 | 1039528.52
Existing | CZ07 | cDXGF | 2713527.07 | 1026618.25
Existing | CZ08 | cDXGF | 2831462.22 | 1057104.67
Existing | CZ09 | cDXGF | 2947000.51 | 1023885
Existing | CZ10 | cDXGF | 3130019.56 | 1142237.8
Existing | CZ11 | cDXGF | 3197084.9 | 1428634.35
Existing | CZ12 | cDXGF | 2996818.42 | 1427282.93
Existing | CZ13 | cDXGF | 3244269.99 | 1291924.89
Existing | CZ14 | cDXGF | 3485716.94 | 1109232.21
Existing | CZ15 | cDXGF | 3850518.52 | 886039.56
Existing | CZ16 | cDXGF | 3151746.88 | 1639677.73
New Construction | CZ01 | cDXGF | 1790968.03 | 1973565.3
New Construction | CZ02 | cDXGF | 2179386.1 | 1690635.77
New Construction | CZ03 | cDXGF | 2037389 | 1488984.49
New Construction | CZ04 | cDXGF | 2218396.14 | 1389770.98
New Construction | CZ05 | cDXGF | 2058229.76 | 1449251.12
New Construction | CZ06 | cDXGF | 2166986.56 | 1078568.38
New Construction | CZ07 | cDXGF | 2178849.82 | 1056626.74
New Construction | CZ08 | cDXGF | 2303347.63 | 1097250.94
New Construction | CZ09 | cDXGF | 2380517.48 | 1049805.81
New Construction | CZ10 | cDXGF | 2571054.11 | 1178500.55
New Construction | CZ11 | cDXGF | 2362704.31 | 1404127.46
New Construction | CZ12 | cDXGF | 2247994.87 | 1427183.12
New Construction | CZ13 | cDXGF | 2418056.62 | 1298940.34
New Construction | CZ14 | cDXGF | 2631315.42 | 1114003.38
New Construction | CZ15 | cDXGF | 2923551.56 | 885176.9
New Construction | CZ16 | cDXGF | 2363328.66 | 1627758.42
Existing | CZ01 | cDXHP | 2358834.22 | 1798847.24
Existing | CZ02 | cDXHP | 2697728.13 | 1483416.93
Existing | CZ03 | cDXHP | 2544980.45 | 1329104.14
Existing | CZ04 | cDXHP | 2746636.84 | 1267484.04
Existing | CZ05 | cDXHP | 2577643.05 | 1311379.72
Existing | CZ06 | cDXHP | 2688238.24 | 1033673.72
Existing | CZ07 | cDXHP | 2712038.88 | 1020370.47
Existing | CZ08 | cDXHP | 2832115.81 | 1048090.32
Existing | CZ09 | cDXHP | 2946722.32 | 1017524.56
Existing | CZ10 | cDXHP | 3137371.04 | 1115573.13
Existing | CZ11 | cDXHP | 3215862.37 | 1363145.13
Existing | CZ12 | cDXHP | 3013314.08 | 1367917.57
Existing | CZ13 | cDXHP | 3256372.41 | 1248720.39
Existing | CZ14 | cDXHP | 3493193.78 | 1086573.44
Existing | CZ15 | cDXHP | 3852481.8 | 879205.24
Existing | CZ16 | cDXHP | 3184706.5 | 1551215.47
New Construction | CZ01 | cDXHP | 1820827.39 | 1850803.26
New Construction | CZ02 | cDXHP | 2205969.42 | 1585936.36
New Construction | CZ03 | cDXHP | 2052490.38 | 1424977.44
New Construction | CZ04 | cDXHP | 2231546.76 | 1334029.03
New Construction | CZ05 | cDXHP | 2072556.24 | 1390416.34
New Construction | CZ06 | cDXHP | 2166372.8 | 1065421.23
New Construction | CZ07 | cDXHP | 2179058.92 | 1044239.44
New Construction | CZ08 | cDXHP | 2306412.12 | 1079346.84
New Construction | CZ09 | cDXHP | 2381945.28 | 1036628.16
New Construction | CZ10 | cDXHP | 2581451.22 | 1139270.18
New Construction | CZ11 | cDXHP | 2381958.46 | 1335086.85
New Construction | CZ12 | cDXHP | 2266432.32 | 1359096.91
New Construction | CZ13 | cDXHP | 2432001.82 | 1247088.86
New Construction | CZ14 | cDXHP | 2639870.42 | 1085765.39
New Construction | CZ15 | cDXHP | 2926423.36 | 875221.52
New Construction | CZ16 | cDXHP | 2397913.18 | 1529633.11
Existing | CZ01 | cDXOH | 2334304.03 | 1803033.44
Existing | CZ02 | cDXOH | 2679642.15 | 1485738.43
Existing | CZ03 | cDXOH | 2536855.05 | 1330012.7
Existing | CZ04 | cDXOH | 2739022.05 | 1268302.38
Existing | CZ05 | cDXOH | 2569260.03 | 1312013.35
Existing | CZ06 | cDXOH | 2690849.78 | 1033734.05
Existing | CZ07 | cDXOH | 2713430.62 | 1020474.9
Existing | CZ08 | cDXOH | 2831293.47 | 1048174.26
Existing | CZ09 | cDXOH | 2946873.93 | 1017614.38
Existing | CZ10 | cDXOH | 3129539.19 | 1116182.57
Existing | CZ11 | cDXOH | 3197118.44 | 1365909.59
Existing | CZ12 | cDXOH | 2996697.22 | 1370408.1
Existing | CZ13 | cDXOH | 3244115.04 | 1250605.86
Existing | CZ14 | cDXOH | 3485443.26 | 1087203.84
Existing | CZ15 | cDXOH | 3850312.65 | 879323.57
Existing | CZ16 | cDXOH | 3152775.06 | 1554897.09
New Construction | CZ01 | cDXOH | 1789595.52 | 1860265.88
New Construction | CZ02 | cDXOH | 2178442.97 | 1590861.39
New Construction | CZ03 | cDXOH | 2036601.86 | 1427744.23
New Construction | CZ04 | cDXOH | 2217668.29 | 1336082.56
New Construction | CZ05 | cDXOH | 2056940.09 | 1392528.64
New Construction | CZ06 | cDXOH | 2166717.85 | 1065909.94
New Construction | CZ07 | cDXOH | 2178616.35 | 1044641.34
New Construction | CZ08 | cDXOH | 2302930.47 | 1079974.81
New Construction | CZ09 | cDXOH | 2380181.23 | 1036988.05
New Construction | CZ10 | cDXOH | 2570158 | 1140267.68
New Construction | CZ11 | cDXOH | 2361341.61 | 1340099.91
New Construction | CZ12 | cDXOH | 2246591.59 | 1363845.14
New Construction | CZ13 | cDXOH | 2416922.01 | 1251077.91
New Construction | CZ14 | cDXOH | 2630434.53 | 1087331.2
New Construction | CZ15 | cDXOH | 2922741.68 | 875521.07
New Construction | CZ16 | cDXOH | 2361875.68 | 1536319.16
Existing | CZ01 | cPVVG | 2188418.2 | 1959058.47
Existing | CZ02 | cPVVG | 2517298.14 | 1590653.02
Existing | CZ03 | cPVVG | 2382486.09 | 1390879.94
Existing | CZ04 | cPVVG | 2575252.14 | 1325156.63
Existing | CZ05 | cPVVG | 2420099.76 | 1366490.56
Existing | CZ06 | cPVVG | 2545650.79 | 1046712.07
Existing | CZ07 | cPVVG | 2564811.69 | 1033546.39
Existing | CZ08 | cPVVG | 2672517.39 | 1066292.58
Existing | CZ09 | cPVVG | 2777395.52 | 1031640.83
Existing | CZ10 | cPVVG | 2958837.18 | 1160793.28
Existing | CZ11 | cPVVG | 3015415.6 | 1470521.69
Existing | CZ12 | cPVVG | 2832979.01 | 1462833
Existing | CZ13 | cPVVG | 3067622.07 | 1321667.15
Existing | CZ14 | cPVVG | 3294860.38 | 1127563.36
Existing | CZ15 | cPVVG | 3670582.3 | 892391.01
Existing | CZ16 | cPVVG | 2965984.04 | 1688019.88
New Construction | CZ01 | cPVVG | 1689386.76 | 2031601.55
New Construction | CZ02 | cPVVG | 2056178.12 | 1735305.73
New Construction | CZ03 | cPVVG | 1921222.4 | 1524404.17
New Construction | CZ04 | cPVVG | 2095585.18 | 1421258.79
New Construction | CZ05 | cPVVG | 1945827.59 | 1480632.18
New Construction | CZ06 | cPVVG | 2055380.18 | 1090068.01
New Construction | CZ07 | cPVVG | 2066512.21 | 1067224.01
New Construction | CZ08 | cPVVG | 2183971.69 | 1111120.38
New Construction | CZ09 | cPVVG | 2257019.59 | 1061422.36
New Construction | CZ10 | cPVVG | 2442739.93 | 1199133.36
New Construction | CZ11 | cPVVG | 2258349.71 | 1435514.07
New Construction | CZ12 | cPVVG | 2146555.73 | 1455463.36
New Construction | CZ13 | cPVVG | 2315445.39 | 1323717.48
New Construction | CZ14 | cPVVG | 2522263.19 | 1130759.54
New Construction | CZ15 | cPVVG | 2828357.52 | 891565.1
New Construction | CZ16 | cPVVG | 2249976.08 | 1664944.8

## Energy Usage by End Use
Energy Consumption by End Use - Education - Secondary School
Climate Zone | HVAC System | Vintage | End Use | Electricity (kBtu) | Natural Gas (kBtu) | Note
CZ01 | cAVVG | Existing | Heating | 0 | 901184.08
CZ01 | cAVVG | Existing | Cooling | 50388.63 | 0
CZ01 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ01 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ01 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ01 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ01 | cAVVG | Existing | Fans | 584052.98 | 0
CZ01 | cAVVG | Existing | Pumps | 813.36 | 0
CZ01 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ01 | cAVVG | Existing | Humidification | 0 | 0
CZ01 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ01 | cAVVG | Existing | Water Systems | 0 | 864659.77
CZ01 | cAVVG | Existing | Refrigeration | 0 | 0
CZ01 | cAVVG | Existing | Generators | 0 | 0
CZ01 | cAVVG | Existing | Total End Uses | 2190868.74 | 1984688.69
CZ02 | cAVVG | Existing | Heating | 0 | 606079.51
CZ02 | cAVVG | Existing | Cooling | 323450.33 | 0
CZ02 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ02 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ02 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ02 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ02 | cAVVG | Existing | Fans | 662644.09 | 0
CZ02 | cAVVG | Existing | Pumps | 4869.72 | 0
CZ02 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ02 | cAVVG | Existing | Humidification | 0 | 0
CZ02 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ02 | cAVVG | Existing | Water Systems | 0 | 794294.24
CZ02 | cAVVG | Existing | Refrigeration | 0 | 0
CZ02 | cAVVG | Existing | Generators | 0 | 0
CZ02 | cAVVG | Existing | Total End Uses | 2546577.91 | 1619218.6
CZ03 | cAVVG | Existing | Heating | 0 | 399919.85
CZ03 | cAVVG | Existing | Cooling | 209976.31 | 0
CZ03 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ03 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ03 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ03 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ03 | cAVVG | Existing | Fans | 618307.61 | 0
CZ03 | cAVVG | Existing | Pumps | 4650.18 | 0
CZ03 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ03 | cAVVG | Existing | Humidification | 0 | 0
CZ03 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ03 | cAVVG | Existing | Water Systems | 0 | 791302.95
CZ03 | cAVVG | Existing | Refrigeration | 0 | 0
CZ03 | cAVVG | Existing | Generators | 0 | 0
CZ03 | cAVVG | Existing | Total End Uses | 2388547.87 | 1410067.65
CZ04 | cAVVG | Existing | Heating | 0 | 362607.76
CZ04 | cAVVG | Existing | Cooling | 386496.96 | 0
CZ04 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ04 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ04 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ04 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ04 | cAVVG | Existing | Fans | 654258.33 | 0
CZ04 | cAVVG | Existing | Pumps | 5515.87 | 0
CZ04 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ04 | cAVVG | Existing | Humidification | 0 | 0
CZ04 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ04 | cAVVG | Existing | Water Systems | 0 | 763976.36
CZ04 | cAVVG | Existing | Refrigeration | 0 | 0
CZ04 | cAVVG | Existing | Generators | 0 | 0
CZ04 | cAVVG | Existing | Total End Uses | 2601884.93 | 1345428.98
CZ05 | cAVVG | Existing | Heating | 0 | 376268.13
CZ05 | cAVVG | Existing | Cooling | 259227.44 | 0
CZ05 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ05 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ05 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ05 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ05 | cAVVG | Existing | Fans | 610056.75 | 0
CZ05 | cAVVG | Existing | Pumps | 5055.6 | 0
CZ05 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ05 | cAVVG | Existing | Humidification | 0 | 0
CZ05 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ05 | cAVVG | Existing | Water Systems | 0 | 791355.21
CZ05 | cAVVG | Existing | Refrigeration | 0 | 0
CZ05 | cAVVG | Existing | Generators | 0 | 0
CZ05 | cAVVG | Existing | Total End Uses | 2429953.56 | 1386468.19
CZ06 | cAVVG | Existing | Heating | 0 | 106833.85
CZ06 | cAVVG | Existing | Cooling | 417418.94 | 0
CZ06 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ06 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ06 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ06 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ06 | cAVVG | Existing | Fans | 615260.64 | 0
CZ06 | cAVVG | Existing | Pumps | 8168.31 | 0
CZ06 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ06 | cAVVG | Existing | Humidification | 0 | 0
CZ06 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ06 | cAVVG | Existing | Water Systems | 0 | 728922.8
CZ06 | cAVVG | Existing | Refrigeration | 0 | 0
CZ06 | cAVVG | Existing | Generators | 0 | 0
CZ06 | cAVVG | Existing | Total End Uses | 2596461.66 | 1054601.5
CZ07 | cAVVG | Existing | Heating | 0 | 105611.92
CZ07 | cAVVG | Existing | Cooling | 456156.68 | 0
CZ07 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ07 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ07 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ07 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ07 | cAVVG | Existing | Fans | 617620.56 | 0
CZ07 | cAVVG | Existing | Pumps | 8774.12 | 0
CZ07 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ07 | cAVVG | Existing | Humidification | 0 | 0
CZ07 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ07 | cAVVG | Existing | Water Systems | 0 | 719530.06
CZ07 | cAVVG | Existing | Refrigeration | 0 | 0
CZ07 | cAVVG | Existing | Generators | 0 | 0
CZ07 | cAVVG | Existing | Total End Uses | 2638165.13 | 1043986.84
CZ08 | cAVVG | Existing | Heating | 0 | 142970.63
CZ08 | cAVVG | Existing | Cooling | 538510.36 | 0
CZ08 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ08 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ08 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ08 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ08 | cAVVG | Existing | Fans | 634358.83 | 0
CZ08 | cAVVG | Existing | Pumps | 7772.3 | 0
CZ08 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ08 | cAVVG | Existing | Humidification | 0 | 0
CZ08 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ08 | cAVVG | Existing | Water Systems | 0 | 718474.27
CZ08 | cAVVG | Existing | Refrigeration | 0 | 0
CZ08 | cAVVG | Existing | Generators | 0 | 0
CZ08 | cAVVG | Existing | Total End Uses | 2736255.27 | 1080289.76
CZ09 | cAVVG | Existing | Heating | 0 | 119899.1
CZ09 | cAVVG | Existing | Cooling | 614823.2 | 0
CZ09 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ09 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ09 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ09 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ09 | cAVVG | Existing | Fans | 667919 | 0
CZ09 | cAVVG | Existing | Pumps | 8179.6 | 0
CZ09 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ09 | cAVVG | Existing | Humidification | 0 | 0
CZ09 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ09 | cAVVG | Existing | Water Systems | 0 | 708479.43
CZ09 | cAVVG | Existing | Refrigeration | 0 | 0
CZ09 | cAVVG | Existing | Generators | 0 | 0
CZ09 | cAVVG | Existing | Total End Uses | 2846535.57 | 1047223.38
CZ10 | cAVVG | Existing | Heating | 0 | 259402.75
CZ10 | cAVVG | Existing | Cooling | 774477.43 | 0
CZ10 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ10 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ10 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ10 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ10 | cAVVG | Existing | Fans | 700530.99 | 0
CZ10 | cAVVG | Existing | Pumps | 7965.88 | 0
CZ10 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ10 | cAVVG | Existing | Humidification | 0 | 0
CZ10 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ10 | cAVVG | Existing | Water Systems | 0 | 702475.66
CZ10 | cAVVG | Existing | Refrigeration | 0 | 0
CZ10 | cAVVG | Existing | Generators | 0 | 0
CZ10 | cAVVG | Existing | Total End Uses | 3038588.07 | 1180723.26
CZ11 | cAVVG | Existing | Heating | 0 | 563053.27
CZ11 | cAVVG | Existing | Cooling | 788700.58 | 0
CZ11 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ11 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ11 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ11 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ11 | cAVVG | Existing | Fans | 734616.42 | 0
CZ11 | cAVVG | Existing | Pumps | 7100.01 | 0
CZ11 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ11 | cAVVG | Existing | Humidification | 0 | 0
CZ11 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ11 | cAVVG | Existing | Water Systems | 0 | 717982.65
CZ11 | cAVVG | Existing | Refrigeration | 0 | 0
CZ11 | cAVVG | Existing | Generators | 0 | 0
CZ11 | cAVVG | Existing | Total End Uses | 3086030.78 | 1499880.77
CZ12 | cAVVG | Existing | Heating | 0 | 530827.47
CZ12 | cAVVG | Existing | Cooling | 654669.99 | 0
CZ12 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ12 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ12 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ12 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ12 | cAVVG | Existing | Fans | 688430.16 | 0
CZ12 | cAVVG | Existing | Pumps | 6914.84 | 0
CZ12 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ12 | cAVVG | Existing | Humidification | 0 | 0
CZ12 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ12 | cAVVG | Existing | Water Systems | 0 | 738437.39
CZ12 | cAVVG | Existing | Refrigeration | 0 | 0
CZ12 | cAVVG | Existing | Generators | 0 | 0
CZ12 | cAVVG | Existing | Total End Uses | 2905628.76 | 1488109.72
CZ13 | cAVVG | Existing | Heating | 0 | 427453.44
CZ13 | cAVVG | Existing | Cooling | 875601.38 | 0
CZ13 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ13 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ13 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ13 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ13 | cAVVG | Existing | Fans | 711270.97 | 0
CZ13 | cAVVG | Existing | Pumps | 8020.29 | 0
CZ13 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ13 | cAVVG | Existing | Humidification | 0 | 0
CZ13 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ13 | cAVVG | Existing | Water Systems | 0 | 697016.25
CZ13 | cAVVG | Existing | Refrigeration | 0 | 0
CZ13 | cAVVG | Existing | Generators | 0 | 0
CZ13 | cAVVG | Existing | Total End Uses | 3150506.41 | 1343314.54
CZ14 | cAVVG | Existing | Heating | 0 | 265792.25
CZ14 | cAVVG | Existing | Cooling | 1079000.5 | 0
CZ14 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ14 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ14 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ14 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ14 | cAVVG | Existing | Fans | 737586.68 | 0
CZ14 | cAVVG | Existing | Pumps | 7739.81 | 0
CZ14 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ14 | cAVVG | Existing | Humidification | 0 | 0
CZ14 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ14 | cAVVG | Existing | Water Systems | 0 | 661517.48
CZ14 | cAVVG | Existing | Refrigeration | 0 | 0
CZ14 | cAVVG | Existing | Generators | 0 | 0
CZ14 | cAVVG | Existing | Total End Uses | 3379940.76 | 1146154.57
CZ15 | cAVVG | Existing | Heating | 0 | 99638.52
CZ15 | cAVVG | Existing | Cooling | 1536652.66 | 0
CZ15 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ15 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ15 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ15 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ15 | cAVVG | Existing | Fans | 711061.69 | 0
CZ15 | cAVVG | Existing | Pumps | 11355.94 | 0
CZ15 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ15 | cAVVG | Existing | Humidification | 0 | 0
CZ15 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ15 | cAVVG | Existing | Water Systems | 0 | 587120.66
CZ15 | cAVVG | Existing | Refrigeration | 0 | 0
CZ15 | cAVVG | Existing | Generators | 0 | 0
CZ15 | cAVVG | Existing | Total End Uses | 3814684.06 | 905604.03
CZ16 | cAVVG | Existing | Heating | 0 | 720403.09
CZ16 | cAVVG | Existing | Cooling | 679749.43 | 0
CZ16 | cAVVG | Existing | Interior Lighting | 673572.97 | 0
CZ16 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ16 | cAVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ16 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ16 | cAVVG | Existing | Fans | 796671.46 | 0
CZ16 | cAVVG | Existing | Pumps | 7406.32 | 0
CZ16 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ16 | cAVVG | Existing | Humidification | 0 | 0
CZ16 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ16 | cAVVG | Existing | Water Systems | 0 | 780702.03
CZ16 | cAVVG | Existing | Refrigeration | 0 | 0
CZ16 | cAVVG | Existing | Generators | 0 | 0
CZ16 | cAVVG | Existing | Total End Uses | 3039440.99 | 1719949.97
CZ01 | cAVVG | New Construction | Heating | 0 | 956981.74
CZ01 | cAVVG | New Construction | Cooling | 40833.91 | 0
CZ01 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ01 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ01 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ01 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ01 | cAVVG | New Construction | Fans | 475517.06 | 0
CZ01 | cAVVG | New Construction | Pumps | 628.4 | 0
CZ01 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ01 | cAVVG | New Construction | Humidification | 0 | 0
CZ01 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ01 | cAVVG | New Construction | Water Systems | 0 | 864505.76
CZ01 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ01 | cAVVG | New Construction | Generators | 0 | 0
CZ01 | cAVVG | New Construction | Total End Uses | 1721470.83 | 2040332.36
CZ02 | cAVVG | New Construction | Heating | 0 | 753225.8
CZ02 | cAVVG | New Construction | Cooling | 267416.63 | 0
CZ02 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ02 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ02 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ02 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ02 | cAVVG | New Construction | Fans | 624873.21 | 0
CZ02 | cAVVG | New Construction | Pumps | 4013.86 | 0
CZ02 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ02 | cAVVG | New Construction | Humidification | 0 | 0
CZ02 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ02 | cAVVG | New Construction | Water Systems | 0 | 794064.01
CZ02 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ02 | cAVVG | New Construction | Generators | 0 | 0
CZ02 | cAVVG | New Construction | Total End Uses | 2100795.15 | 1766134.66
CZ03 | cAVVG | New Construction | Heating | 0 | 530150.17
CZ03 | cAVVG | New Construction | Cooling | 161545 | 0
CZ03 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ03 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ03 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ03 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ03 | cAVVG | New Construction | Fans | 567911.93 | 0
CZ03 | cAVVG | New Construction | Pumps | 3348.84 | 0
CZ03 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ03 | cAVVG | New Construction | Humidification | 0 | 0
CZ03 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ03 | cAVVG | New Construction | Water Systems | 0 | 791125.99
CZ03 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ03 | cAVVG | New Construction | Generators | 0 | 0
CZ03 | cAVVG | New Construction | Total End Uses | 1937297.23 | 1540121.01
CZ04 | cAVVG | New Construction | Heating | 0 | 457189.07
CZ04 | cAVVG | New Construction | Cooling | 320739.77 | 0
CZ04 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ04 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ04 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ04 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ04 | cAVVG | New Construction | Fans | 601684.41 | 0
CZ04 | cAVVG | New Construction | Pumps | 4528.18 | 0
CZ04 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ04 | cAVVG | New Construction | Humidification | 0 | 0
CZ04 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ04 | cAVVG | New Construction | Water Systems | 0 | 763642.19
CZ04 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ04 | cAVVG | New Construction | Generators | 0 | 0
CZ04 | cAVVG | New Construction | Total End Uses | 2131443.81 | 1439676.12
CZ05 | cAVVG | New Construction | Heating | 0 | 489736.91
CZ05 | cAVVG | New Construction | Cooling | 200974.31 | 0
CZ05 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ05 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ05 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ05 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ05 | cAVVG | New Construction | Fans | 555045.57 | 0
CZ05 | cAVVG | New Construction | Pumps | 3712.8 | 0
CZ05 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ05 | cAVVG | New Construction | Humidification | 0 | 0
CZ05 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ05 | cAVVG | New Construction | Water Systems | 0 | 791117.02
CZ05 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ05 | cAVVG | New Construction | Generators | 0 | 0
CZ05 | cAVVG | New Construction | Total End Uses | 1964224.14 | 1499698.78
CZ06 | cAVVG | New Construction | Heating | 0 | 155839.48
CZ06 | cAVVG | New Construction | Cooling | 337097.5 | 0
CZ06 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ06 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ06 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ06 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ06 | cAVVG | New Construction | Fans | 559343.07 | 0
CZ06 | cAVVG | New Construction | Pumps | 6476.9 | 0
CZ06 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ06 | cAVVG | New Construction | Humidification | 0 | 0
CZ06 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ06 | cAVVG | New Construction | Water Systems | 0 | 728645.06
CZ06 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ06 | cAVVG | New Construction | Generators | 0 | 0
CZ06 | cAVVG | New Construction | Total End Uses | 2107408.92 | 1103329.4
CZ07 | cAVVG | New Construction | Heating | 0 | 146905.52
CZ07 | cAVVG | New Construction | Cooling | 372079.36 | 0
CZ07 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ07 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ07 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ07 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ07 | cAVVG | New Construction | Fans | 552128.9 | 0
CZ07 | cAVVG | New Construction | Pumps | 6082.13 | 0
CZ07 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ07 | cAVVG | New Construction | Humidification | 0 | 0
CZ07 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ07 | cAVVG | New Construction | Water Systems | 0 | 719206.82
CZ07 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ07 | cAVVG | New Construction | Generators | 0 | 0
CZ07 | cAVVG | New Construction | Total End Uses | 2134781.84 | 1084957.19
CZ08 | cAVVG | New Construction | Heating | 0 | 192401.17
CZ08 | cAVVG | New Construction | Cooling | 454148.84 | 0
CZ08 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ08 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ08 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ08 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ08 | cAVVG | New Construction | Fans | 585742.42 | 0
CZ08 | cAVVG | New Construction | Pumps | 6307.22 | 0
CZ08 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ08 | cAVVG | New Construction | Humidification | 0 | 0
CZ08 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ08 | cAVVG | New Construction | Water Systems | 0 | 718186.58
CZ08 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ08 | cAVVG | New Construction | Generators | 0 | 0
CZ08 | cAVVG | New Construction | Total End Uses | 2250689.93 | 1129432.6
CZ09 | cAVVG | New Construction | Heating | 0 | 154236.35
CZ09 | cAVVG | New Construction | Cooling | 513024.08 | 0
CZ09 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ09 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ09 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ09 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ09 | cAVVG | New Construction | Fans | 603547.03 | 0
CZ09 | cAVVG | New Construction | Pumps | 6506.62 | 0
CZ09 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ09 | cAVVG | New Construction | Humidification | 0 | 0
CZ09 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ09 | cAVVG | New Construction | Water Systems | 0 | 708140.1
CZ09 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ09 | cAVVG | New Construction | Generators | 0 | 0
CZ09 | cAVVG | New Construction | Total End Uses | 2327569.19 | 1081221.3
CZ10 | cAVVG | New Construction | Heating | 0 | 297904.1
CZ10 | cAVVG | New Construction | Cooling | 680789.64 | 0
CZ10 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ10 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ10 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ10 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ10 | cAVVG | New Construction | Fans | 628650.85 | 0
CZ10 | cAVVG | New Construction | Pumps | 6633.62 | 0
CZ10 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ10 | cAVVG | New Construction | Humidification | 0 | 0
CZ10 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ10 | cAVVG | New Construction | Water Systems | 0 | 702067.83
CZ10 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ10 | cAVVG | New Construction | Generators | 0 | 0
CZ10 | cAVVG | New Construction | Total End Uses | 2520565.56 | 1218816.77
CZ11 | cAVVG | New Construction | Heating | 0 | 513806.34
CZ11 | cAVVG | New Construction | Cooling | 606691.08 | 0
CZ11 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ11 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ11 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ11 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ11 | cAVVG | New Construction | Fans | 519629.82 | 0
CZ11 | cAVVG | New Construction | Pumps | 5120.28 | 0
CZ11 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ11 | cAVVG | New Construction | Humidification | 0 | 0
CZ11 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ11 | cAVVG | New Construction | Water Systems | 0 | 717344
CZ11 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ11 | cAVVG | New Construction | Generators | 0 | 0
CZ11 | cAVVG | New Construction | Total End Uses | 2335932.64 | 1449995.19
CZ12 | cAVVG | New Construction | Heating | 0 | 506240.6
CZ12 | cAVVG | New Construction | Cooling | 507337.98 | 0
CZ12 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ12 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ12 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ12 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ12 | cAVVG | New Construction | Fans | 512044.37 | 0
CZ12 | cAVVG | New Construction | Pumps | 5209.05 | 0
CZ12 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ12 | cAVVG | New Construction | Humidification | 0 | 0
CZ12 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ12 | cAVVG | New Construction | Water Systems | 0 | 737920.96
CZ12 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ12 | cAVVG | New Construction | Generators | 0 | 0
CZ12 | cAVVG | New Construction | Total End Uses | 2229082.85 | 1463006.41
CZ13 | cAVVG | New Construction | Heating | 0 | 419491.77
CZ13 | cAVVG | New Construction | Cooling | 673658.06 | 0
CZ13 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ13 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ13 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ13 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ13 | cAVVG | New Construction | Fans | 518807.27 | 0
CZ13 | cAVVG | New Construction | Pumps | 5778.19 | 0
CZ13 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ13 | cAVVG | New Construction | Humidification | 0 | 0
CZ13 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ13 | cAVVG | New Construction | Water Systems | 0 | 696548.06
CZ13 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ13 | cAVVG | New Construction | Generators | 0 | 0
CZ13 | cAVVG | New Construction | Total End Uses | 2402734.97 | 1334884.69
CZ14 | cAVVG | New Construction | Heating | 0 | 264740.83
CZ14 | cAVVG | New Construction | Cooling | 854375.83 | 0
CZ14 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ14 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ14 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ14 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ14 | cAVVG | New Construction | Fans | 547536.71 | 0
CZ14 | cAVVG | New Construction | Pumps | 5528.9 | 0
CZ14 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ14 | cAVVG | New Construction | Humidification | 0 | 0
CZ14 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ14 | cAVVG | New Construction | Water Systems | 0 | 660893.49
CZ14 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ14 | cAVVG | New Construction | Generators | 0 | 0
CZ14 | cAVVG | New Construction | Total End Uses | 2611932.89 | 1144479.17
CZ15 | cAVVG | New Construction | Heating | 0 | 101818.15
CZ15 | cAVVG | New Construction | Cooling | 1222946.93 | 0
CZ15 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ15 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ15 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ15 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ15 | cAVVG | New Construction | Fans | 536171.53 | 0
CZ15 | cAVVG | New Construction | Pumps | 8279.39 | 0
CZ15 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ15 | cAVVG | New Construction | Humidification | 0 | 0
CZ15 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ15 | cAVVG | New Construction | Water Systems | 0 | 586612.37
CZ15 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ15 | cAVVG | New Construction | Generators | 0 | 0
CZ15 | cAVVG | New Construction | Total End Uses | 2971889.29 | 907275.37
CZ16 | cAVVG | New Construction | Heating | 0 | 672125.23
CZ16 | cAVVG | New Construction | Cooling | 540384.47 | 0
CZ16 | cAVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ16 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ16 | cAVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ16 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ16 | cAVVG | New Construction | Fans | 585044.75 | 0
CZ16 | cAVVG | New Construction | Pumps | 5259.63 | 0
CZ16 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ16 | cAVVG | New Construction | Humidification | 0 | 0
CZ16 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ16 | cAVVG | New Construction | Water Systems | 0 | 780229.66
CZ16 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ16 | cAVVG | New Construction | Generators | 0 | 0
CZ16 | cAVVG | New Construction | Total End Uses | 2335180.3 | 1671199.75
CZ01 | cDXGF | Existing | Heating | 0 | 813325.03
CZ01 | cDXGF | Existing | Cooling | 47280.63 | 0
CZ01 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ01 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ01 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXGF | Existing | Fans | 731884.77 | 0
CZ01 | cDXGF | Existing | Pumps | 0 | 0
CZ01 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ01 | cDXGF | Existing | Humidification | 0 | 0
CZ01 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ01 | cDXGF | Existing | Water Systems | 0 | 864674.75
CZ01 | cDXGF | Existing | Refrigeration | 0 | 0
CZ01 | cDXGF | Existing | Generators | 0 | 0
CZ01 | cDXGF | Existing | Total End Uses | 2334779.17 | 1896844.63
CZ02 | cDXGF | Existing | Heating | 0 | 536988.41
CZ02 | cDXGF | Existing | Cooling | 294972.88 | 0
CZ02 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ02 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ02 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXGF | Existing | Fans | 829572.51 | 0
CZ02 | cDXGF | Existing | Pumps | 0 | 0
CZ02 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ02 | cDXGF | Existing | Humidification | 0 | 0
CZ02 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ02 | cDXGF | Existing | Water Systems | 0 | 794290.78
CZ02 | cDXGF | Existing | Refrigeration | 0 | 0
CZ02 | cDXGF | Existing | Generators | 0 | 0
CZ02 | cDXGF | Existing | Total End Uses | 2680159.16 | 1550124.05
CZ03 | cDXGF | Existing | Heating | 0 | 353326.92
CZ03 | cDXGF | Existing | Cooling | 187228.14 | 0
CZ03 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ03 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ03 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXGF | Existing | Fans | 794233.61 | 0
CZ03 | cDXGF | Existing | Pumps | 0 | 0
CZ03 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ03 | cDXGF | Existing | Humidification | 0 | 0
CZ03 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ03 | cDXGF | Existing | Water Systems | 0 | 791289.4
CZ03 | cDXGF | Existing | Refrigeration | 0 | 0
CZ03 | cDXGF | Existing | Generators | 0 | 0
CZ03 | cDXGF | Existing | Total End Uses | 2537075.53 | 1363461.17
CZ04 | cDXGF | Existing | Heating | 0 | 316572.12
CZ04 | cDXGF | Existing | Cooling | 355821.14 | 0
CZ04 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ04 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ04 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXGF | Existing | Fans | 827834.44 | 0
CZ04 | cDXGF | Existing | Pumps | 0 | 0
CZ04 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ04 | cDXGF | Existing | Humidification | 0 | 0
CZ04 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ04 | cDXGF | Existing | Water Systems | 0 | 763979.44
CZ04 | cDXGF | Existing | Refrigeration | 0 | 0
CZ04 | cDXGF | Existing | Generators | 0 | 0
CZ04 | cDXGF | Existing | Total End Uses | 2739269.35 | 1299396.42
CZ05 | cDXGF | Existing | Heating | 0 | 333094.88
CZ05 | cDXGF | Existing | Cooling | 237215.82 | 0
CZ05 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ05 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ05 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXGF | Existing | Fans | 776966.85 | 0
CZ05 | cDXGF | Existing | Pumps | 0 | 0
CZ05 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ05 | cDXGF | Existing | Humidification | 0 | 0
CZ05 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ05 | cDXGF | Existing | Water Systems | 0 | 791317.75
CZ05 | cDXGF | Existing | Refrigeration | 0 | 0
CZ05 | cDXGF | Existing | Generators | 0 | 0
CZ05 | cDXGF | Existing | Total End Uses | 2569796.44 | 1343257.49
CZ06 | cDXGF | Existing | Heating | 0 | 91809.33
CZ06 | cDXGF | Existing | Cooling | 375716.59 | 0
CZ06 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ06 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ06 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXGF | Existing | Fans | 759586.33 | 0
CZ06 | cDXGF | Existing | Pumps | 0 | 0
CZ06 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ06 | cDXGF | Existing | Humidification | 0 | 0
CZ06 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ06 | cDXGF | Existing | Water Systems | 0 | 728874.34
CZ06 | cDXGF | Existing | Refrigeration | 0 | 0
CZ06 | cDXGF | Existing | Generators | 0 | 0
CZ06 | cDXGF | Existing | Total End Uses | 2690916.69 | 1039528.52
CZ07 | cDXGF | Existing | Heating | 0 | 88313.79
CZ07 | cDXGF | Existing | Cooling | 407232.31 | 0
CZ07 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ07 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ07 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXGF | Existing | Fans | 750680.99 | 0
CZ07 | cDXGF | Existing | Pumps | 0 | 0
CZ07 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ07 | cDXGF | Existing | Humidification | 0 | 0
CZ07 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ07 | cDXGF | Existing | Water Systems | 0 | 719459.61
CZ07 | cDXGF | Existing | Refrigeration | 0 | 0
CZ07 | cDXGF | Existing | Generators | 0 | 0
CZ07 | cDXGF | Existing | Total End Uses | 2713527.07 | 1026618.25
CZ08 | cDXGF | Existing | Heating | 0 | 119811.29
CZ08 | cDXGF | Existing | Cooling | 488061.88 | 0
CZ08 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ08 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ08 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXGF | Existing | Fans | 787786.57 | 0
CZ08 | cDXGF | Existing | Pumps | 0 | 0
CZ08 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ08 | cDXGF | Existing | Humidification | 0 | 0
CZ08 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ08 | cDXGF | Existing | Water Systems | 0 | 718448.52
CZ08 | cDXGF | Existing | Refrigeration | 0 | 0
CZ08 | cDXGF | Existing | Generators | 0 | 0
CZ08 | cDXGF | Existing | Total End Uses | 2831462.22 | 1057104.67
CZ09 | cDXGF | Existing | Heating | 0 | 96608.36
CZ09 | cDXGF | Existing | Cooling | 563038.46 | 0
CZ09 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ09 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ09 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXGF | Existing | Fans | 828348.28 | 0
CZ09 | cDXGF | Existing | Pumps | 0 | 0
CZ09 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ09 | cDXGF | Existing | Humidification | 0 | 0
CZ09 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ09 | cDXGF | Existing | Water Systems | 0 | 708431.79
CZ09 | cDXGF | Existing | Refrigeration | 0 | 0
CZ09 | cDXGF | Existing | Generators | 0 | 0
CZ09 | cDXGF | Existing | Total End Uses | 2947000.51 | 1023885
CZ10 | cDXGF | Existing | Heating | 0 | 220938
CZ10 | cDXGF | Existing | Cooling | 718476.67 | 0
CZ10 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ10 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ10 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXGF | Existing | Fans | 855929.12 | 0
CZ10 | cDXGF | Existing | Pumps | 0 | 0
CZ10 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ10 | cDXGF | Existing | Humidification | 0 | 0
CZ10 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ10 | cDXGF | Existing | Water Systems | 0 | 702454.95
CZ10 | cDXGF | Existing | Refrigeration | 0 | 0
CZ10 | cDXGF | Existing | Generators | 0 | 0
CZ10 | cDXGF | Existing | Total End Uses | 3130019.56 | 1142237.8
CZ11 | cDXGF | Existing | Heating | 0 | 491859.03
CZ11 | cDXGF | Existing | Cooling | 739478.17 | 0
CZ11 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ11 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ11 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXGF | Existing | Fans | 901992.96 | 0
CZ11 | cDXGF | Existing | Pumps | 0 | 0
CZ11 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ11 | cDXGF | Existing | Humidification | 0 | 0
CZ11 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ11 | cDXGF | Existing | Water Systems | 0 | 717930.47
CZ11 | cDXGF | Existing | Refrigeration | 0 | 0
CZ11 | cDXGF | Existing | Generators | 0 | 0
CZ11 | cDXGF | Existing | Total End Uses | 3197084.9 | 1428634.35
CZ12 | cDXGF | Existing | Heating | 0 | 470012.55
CZ12 | cDXGF | Existing | Cooling | 607207.62 | 0
CZ12 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ12 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ12 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXGF | Existing | Fans | 833997.04 | 0
CZ12 | cDXGF | Existing | Pumps | 0 | 0
CZ12 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ12 | cDXGF | Existing | Humidification | 0 | 0
CZ12 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ12 | cDXGF | Existing | Water Systems | 0 | 738425.53
CZ12 | cDXGF | Existing | Refrigeration | 0 | 0
CZ12 | cDXGF | Existing | Generators | 0 | 0
CZ12 | cDXGF | Existing | Total End Uses | 2996818.42 | 1427282.93
CZ13 | cDXGF | Existing | Heating | 0 | 376041.86
CZ13 | cDXGF | Existing | Cooling | 820268.38 | 0
CZ13 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ13 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ13 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXGF | Existing | Fans | 868387.85 | 0
CZ13 | cDXGF | Existing | Pumps | 0 | 0
CZ13 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ13 | cDXGF | Existing | Humidification | 0 | 0
CZ13 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ13 | cDXGF | Existing | Water Systems | 0 | 697038.18
CZ13 | cDXGF | Existing | Refrigeration | 0 | 0
CZ13 | cDXGF | Existing | Generators | 0 | 0
CZ13 | cDXGF | Existing | Total End Uses | 3244269.99 | 1291924.89
CZ14 | cDXGF | Existing | Heating | 0 | 228915.34
CZ14 | cDXGF | Existing | Cooling | 1023978.29 | 0
CZ14 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ14 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ14 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXGF | Existing | Fans | 906124.87 | 0
CZ14 | cDXGF | Existing | Pumps | 0 | 0
CZ14 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ14 | cDXGF | Existing | Humidification | 0 | 0
CZ14 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ14 | cDXGF | Existing | Water Systems | 0 | 661472.01
CZ14 | cDXGF | Existing | Refrigeration | 0 | 0
CZ14 | cDXGF | Existing | Generators | 0 | 0
CZ14 | cDXGF | Existing | Total End Uses | 3485716.94 | 1109232.21
CZ15 | cDXGF | Existing | Heating | 0 | 80070.45
CZ15 | cDXGF | Existing | Cooling | 1434435.64 | 0
CZ15 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ15 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ15 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXGF | Existing | Fans | 860469.11 | 0
CZ15 | cDXGF | Existing | Pumps | 0 | 0
CZ15 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ15 | cDXGF | Existing | Humidification | 0 | 0
CZ15 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ15 | cDXGF | Existing | Water Systems | 0 | 587124.26
CZ15 | cDXGF | Existing | Refrigeration | 0 | 0
CZ15 | cDXGF | Existing | Generators | 0 | 0
CZ15 | cDXGF | Existing | Total End Uses | 3850518.52 | 886039.56
CZ16 | cDXGF | Existing | Heating | 0 | 640152.32
CZ16 | cDXGF | Existing | Cooling | 645607.73 | 0
CZ16 | cDXGF | Existing | Interior Lighting | 673572.97 | 0
CZ16 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXGF | Existing | Interior Equipment | 882040.8 | 218844.85
CZ16 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXGF | Existing | Fans | 950525.38 | 0
CZ16 | cDXGF | Existing | Pumps | 0 | 0
CZ16 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ16 | cDXGF | Existing | Humidification | 0 | 0
CZ16 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ16 | cDXGF | Existing | Water Systems | 0 | 780680.55
CZ16 | cDXGF | Existing | Refrigeration | 0 | 0
CZ16 | cDXGF | Existing | Generators | 0 | 0
CZ16 | cDXGF | Existing | Total End Uses | 3151746.88 | 1639677.73
CZ01 | cDXGF | New Construction | Heating | 0 | 890275.21
CZ01 | cDXGF | New Construction | Cooling | 37923.27 | 0
CZ01 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ01 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ01 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXGF | New Construction | Fans | 548553.3 | 0
CZ01 | cDXGF | New Construction | Pumps | 0 | 0
CZ01 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXGF | New Construction | Humidification | 0 | 0
CZ01 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXGF | New Construction | Water Systems | 0 | 864445.23
CZ01 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ01 | cDXGF | New Construction | Generators | 0 | 0
CZ01 | cDXGF | New Construction | Total End Uses | 1790968.03 | 1973565.3
CZ02 | cDXGF | New Construction | Heating | 0 | 677812.95
CZ02 | cDXGF | New Construction | Cooling | 240400.18 | 0
CZ02 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ02 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ02 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXGF | New Construction | Fans | 734494.48 | 0
CZ02 | cDXGF | New Construction | Pumps | 0 | 0
CZ02 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXGF | New Construction | Humidification | 0 | 0
CZ02 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXGF | New Construction | Water Systems | 0 | 793977.97
CZ02 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ02 | cDXGF | New Construction | Generators | 0 | 0
CZ02 | cDXGF | New Construction | Total End Uses | 2179386.1 | 1690635.77
CZ03 | cDXGF | New Construction | Heating | 0 | 479098.99
CZ03 | cDXGF | New Construction | Cooling | 142483.25 | 0
CZ03 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ03 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ03 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXGF | New Construction | Fans | 690414.3 | 0
CZ03 | cDXGF | New Construction | Pumps | 0 | 0
CZ03 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXGF | New Construction | Humidification | 0 | 0
CZ03 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXGF | New Construction | Water Systems | 0 | 791040.65
CZ03 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ03 | cDXGF | New Construction | Generators | 0 | 0
CZ03 | cDXGF | New Construction | Total End Uses | 2037389 | 1488984.49
CZ04 | cDXGF | New Construction | Heating | 0 | 407279.57
CZ04 | cDXGF | New Construction | Cooling | 292048.48 | 0
CZ04 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ04 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ04 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXGF | New Construction | Fans | 721856.2 | 0
CZ04 | cDXGF | New Construction | Pumps | 0 | 0
CZ04 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXGF | New Construction | Humidification | 0 | 0
CZ04 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXGF | New Construction | Water Systems | 0 | 763646.56
CZ04 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ04 | cDXGF | New Construction | Generators | 0 | 0
CZ04 | cDXGF | New Construction | Total End Uses | 2218396.14 | 1389770.98
CZ05 | cDXGF | New Construction | Heating | 0 | 439309.95
CZ05 | cDXGF | New Construction | Cooling | 181877.48 | 0
CZ05 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ05 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ05 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXGF | New Construction | Fans | 671860.83 | 0
CZ05 | cDXGF | New Construction | Pumps | 0 | 0
CZ05 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXGF | New Construction | Humidification | 0 | 0
CZ05 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXGF | New Construction | Water Systems | 0 | 791096.32
CZ05 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ05 | cDXGF | New Construction | Generators | 0 | 0
CZ05 | cDXGF | New Construction | Total End Uses | 2058229.76 | 1449251.12
CZ06 | cDXGF | New Construction | Heating | 0 | 131205.18
CZ06 | cDXGF | New Construction | Cooling | 298577.14 | 0
CZ06 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ06 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ06 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXGF | New Construction | Fans | 663917.97 | 0
CZ06 | cDXGF | New Construction | Pumps | 0 | 0
CZ06 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXGF | New Construction | Humidification | 0 | 0
CZ06 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXGF | New Construction | Water Systems | 0 | 728518.35
CZ06 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ06 | cDXGF | New Construction | Generators | 0 | 0
CZ06 | cDXGF | New Construction | Total End Uses | 2166986.56 | 1078568.38
CZ07 | cDXGF | New Construction | Heating | 0 | 118757.2
CZ07 | cDXGF | New Construction | Cooling | 328007.5 | 0
CZ07 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ07 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ07 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXGF | New Construction | Fans | 646350.87 | 0
CZ07 | cDXGF | New Construction | Pumps | 0 | 0
CZ07 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXGF | New Construction | Humidification | 0 | 0
CZ07 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXGF | New Construction | Water Systems | 0 | 719024.68
CZ07 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ07 | cDXGF | New Construction | Generators | 0 | 0
CZ07 | cDXGF | New Construction | Total End Uses | 2178849.82 | 1056626.74
CZ08 | cDXGF | New Construction | Heating | 0 | 160398.91
CZ08 | cDXGF | New Construction | Cooling | 406678.53 | 0
CZ08 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ08 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ08 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXGF | New Construction | Fans | 692177.64 | 0
CZ08 | cDXGF | New Construction | Pumps | 0 | 0
CZ08 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXGF | New Construction | Humidification | 0 | 0
CZ08 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXGF | New Construction | Water Systems | 0 | 718007.17
CZ08 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ08 | cDXGF | New Construction | Generators | 0 | 0
CZ08 | cDXGF | New Construction | Total End Uses | 2303347.63 | 1097250.94
CZ09 | cDXGF | New Construction | Heating | 0 | 122947.2
CZ09 | cDXGF | New Construction | Cooling | 465129.21 | 0
CZ09 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ09 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ09 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXGF | New Construction | Fans | 710896.82 | 0
CZ09 | cDXGF | New Construction | Pumps | 0 | 0
CZ09 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXGF | New Construction | Humidification | 0 | 0
CZ09 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXGF | New Construction | Water Systems | 0 | 708013.76
CZ09 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ09 | cDXGF | New Construction | Generators | 0 | 0
CZ09 | cDXGF | New Construction | Total End Uses | 2380517.48 | 1049805.81
CZ10 | cDXGF | New Construction | Heating | 0 | 257552.94
CZ10 | cDXGF | New Construction | Cooling | 629430.66 | 0
CZ10 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ10 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ10 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXGF | New Construction | Fans | 737132 | 0
CZ10 | cDXGF | New Construction | Pumps | 0 | 0
CZ10 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXGF | New Construction | Humidification | 0 | 0
CZ10 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXGF | New Construction | Water Systems | 0 | 702102.75
CZ10 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ10 | cDXGF | New Construction | Generators | 0 | 0
CZ10 | cDXGF | New Construction | Total End Uses | 2571054.11 | 1178500.55
CZ11 | cDXGF | New Construction | Heating | 0 | 467898.63
CZ11 | cDXGF | New Construction | Cooling | 563300.09 | 0
CZ11 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ11 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ11 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXGF | New Construction | Fans | 594912.76 | 0
CZ11 | cDXGF | New Construction | Pumps | 0 | 0
CZ11 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXGF | New Construction | Humidification | 0 | 0
CZ11 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXGF | New Construction | Water Systems | 0 | 717383.99
CZ11 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ11 | cDXGF | New Construction | Generators | 0 | 0
CZ11 | cDXGF | New Construction | Total End Uses | 2362704.31 | 1404127.46
CZ12 | cDXGF | New Construction | Heating | 0 | 470375.4
CZ12 | cDXGF | New Construction | Cooling | 466195.03 | 0
CZ12 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ12 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ12 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXGF | New Construction | Fans | 577308.39 | 0
CZ12 | cDXGF | New Construction | Pumps | 0 | 0
CZ12 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXGF | New Construction | Humidification | 0 | 0
CZ12 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXGF | New Construction | Water Systems | 0 | 737962.87
CZ12 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ12 | cDXGF | New Construction | Generators | 0 | 0
CZ12 | cDXGF | New Construction | Total End Uses | 2247994.87 | 1427183.12
CZ13 | cDXGF | New Construction | Heating | 0 | 383675.47
CZ13 | cDXGF | New Construction | Cooling | 625779.49 | 0
CZ13 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ13 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ13 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXGF | New Construction | Fans | 587785.68 | 0
CZ13 | cDXGF | New Construction | Pumps | 0 | 0
CZ13 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXGF | New Construction | Humidification | 0 | 0
CZ13 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXGF | New Construction | Water Systems | 0 | 696420.02
CZ13 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ13 | cDXGF | New Construction | Generators | 0 | 0
CZ13 | cDXGF | New Construction | Total End Uses | 2418056.62 | 1298940.34
CZ14 | cDXGF | New Construction | Heating | 0 | 234337.11
CZ14 | cDXGF | New Construction | Cooling | 803182.26 | 0
CZ14 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ14 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ14 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXGF | New Construction | Fans | 623641.71 | 0
CZ14 | cDXGF | New Construction | Pumps | 0 | 0
CZ14 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXGF | New Construction | Humidification | 0 | 0
CZ14 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXGF | New Construction | Water Systems | 0 | 660821.42
CZ14 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ14 | cDXGF | New Construction | Generators | 0 | 0
CZ14 | cDXGF | New Construction | Total End Uses | 2631315.42 | 1114003.38
CZ15 | cDXGF | New Construction | Heating | 0 | 79747.67
CZ15 | cDXGF | New Construction | Cooling | 1125929.99 | 0
CZ15 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ15 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ15 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXGF | New Construction | Fans | 593130.13 | 0
CZ15 | cDXGF | New Construction | Pumps | 0 | 0
CZ15 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXGF | New Construction | Humidification | 0 | 0
CZ15 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXGF | New Construction | Water Systems | 0 | 586584.38
CZ15 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ15 | cDXGF | New Construction | Generators | 0 | 0
CZ15 | cDXGF | New Construction | Total End Uses | 2923551.56 | 885176.9
CZ16 | cDXGF | New Construction | Heating | 0 | 628668.78
CZ16 | cDXGF | New Construction | Cooling | 508921.27 | 0
CZ16 | cDXGF | New Construction | Interior Lighting | 322450.66 | 0
CZ16 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXGF | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ16 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXGF | New Construction | Fans | 649915.94 | 0
CZ16 | cDXGF | New Construction | Pumps | 0 | 0
CZ16 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXGF | New Construction | Humidification | 0 | 0
CZ16 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXGF | New Construction | Water Systems | 0 | 780244.79
CZ16 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ16 | cDXGF | New Construction | Generators | 0 | 0
CZ16 | cDXGF | New Construction | Total End Uses | 2363328.66 | 1627758.42
CZ01 | cDXHP | Existing | Heating | 24498.76 | 715325.26
CZ01 | cDXHP | Existing | Cooling | 46831.51 | 0
CZ01 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ01 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ01 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXHP | Existing | Fans | 731890.18 | 0
CZ01 | cDXHP | Existing | Pumps | 0 | 0
CZ01 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ01 | cDXHP | Existing | Humidification | 0 | 0
CZ01 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ01 | cDXHP | Existing | Water Systems | 0 | 864677.13
CZ01 | cDXHP | Existing | Refrigeration | 0 | 0
CZ01 | cDXHP | Existing | Generators | 0 | 0
CZ01 | cDXHP | Existing | Total End Uses | 2358834.22 | 1798847.24
CZ02 | cDXHP | Existing | Heating | 18950.65 | 470281.31
CZ02 | cDXHP | Existing | Cooling | 293592.44 | 0
CZ02 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ02 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ02 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXHP | Existing | Fans | 829571.27 | 0
CZ02 | cDXHP | Existing | Pumps | 0 | 0
CZ02 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ02 | cDXHP | Existing | Humidification | 0 | 0
CZ02 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ02 | cDXHP | Existing | Water Systems | 0 | 794290.77
CZ02 | cDXHP | Existing | Refrigeration | 0 | 0
CZ02 | cDXHP | Existing | Generators | 0 | 0
CZ02 | cDXHP | Existing | Total End Uses | 2697728.13 | 1483416.93
CZ03 | cDXHP | Existing | Heating | 8722.32 | 318969.98
CZ03 | cDXHP | Existing | Cooling | 186410.86 | 0
CZ03 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ03 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ03 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXHP | Existing | Fans | 794233.51 | 0
CZ03 | cDXHP | Existing | Pumps | 0 | 0
CZ03 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ03 | cDXHP | Existing | Humidification | 0 | 0
CZ03 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ03 | cDXHP | Existing | Water Systems | 0 | 791289.31
CZ03 | cDXHP | Existing | Refrigeration | 0 | 0
CZ03 | cDXHP | Existing | Generators | 0 | 0
CZ03 | cDXHP | Existing | Total End Uses | 2544980.45 | 1329104.14
CZ04 | cDXHP | Existing | Heating | 8157.06 | 284659.77
CZ04 | cDXHP | Existing | Cooling | 355031.19 | 0
CZ04 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ04 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ04 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXHP | Existing | Fans | 827834.82 | 0
CZ04 | cDXHP | Existing | Pumps | 0 | 0
CZ04 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ04 | cDXHP | Existing | Humidification | 0 | 0
CZ04 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ04 | cDXHP | Existing | Water Systems | 0 | 763979.42
CZ04 | cDXHP | Existing | Refrigeration | 0 | 0
CZ04 | cDXHP | Existing | Generators | 0 | 0
CZ04 | cDXHP | Existing | Total End Uses | 2746636.84 | 1267484.04
CZ05 | cDXHP | Existing | Heating | 8599.03 | 301217.2
CZ05 | cDXHP | Existing | Cooling | 236465.25 | 0
CZ05 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ05 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ05 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXHP | Existing | Fans | 776965 | 0
CZ05 | cDXHP | Existing | Pumps | 0 | 0
CZ05 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ05 | cDXHP | Existing | Humidification | 0 | 0
CZ05 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ05 | cDXHP | Existing | Water Systems | 0 | 791317.67
CZ05 | cDXHP | Existing | Refrigeration | 0 | 0
CZ05 | cDXHP | Existing | Generators | 0 | 0
CZ05 | cDXHP | Existing | Total End Uses | 2577643.05 | 1311379.72
CZ06 | cDXHP | Existing | Heating | 1405.26 | 85954.62
CZ06 | cDXHP | Existing | Cooling | 371641.79 | 0
CZ06 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ06 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ06 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXHP | Existing | Fans | 759577.43 | 0
CZ06 | cDXHP | Existing | Pumps | 0 | 0
CZ06 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ06 | cDXHP | Existing | Humidification | 0 | 0
CZ06 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ06 | cDXHP | Existing | Water Systems | 0 | 728874.25
CZ06 | cDXHP | Existing | Refrigeration | 0 | 0
CZ06 | cDXHP | Existing | Generators | 0 | 0
CZ06 | cDXHP | Existing | Total End Uses | 2688238.24 | 1033673.72
CZ07 | cDXHP | Existing | Heating | 1504.18 | 82066.07
CZ07 | cDXHP | Existing | Cooling | 404240.99 | 0
CZ07 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ07 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ07 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXHP | Existing | Fans | 750679.94 | 0
CZ07 | cDXHP | Existing | Pumps | 0 | 0
CZ07 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ07 | cDXHP | Existing | Humidification | 0 | 0
CZ07 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ07 | cDXHP | Existing | Water Systems | 0 | 719459.55
CZ07 | cDXHP | Existing | Refrigeration | 0 | 0
CZ07 | cDXHP | Existing | Generators | 0 | 0
CZ07 | cDXHP | Existing | Total End Uses | 2712038.88 | 1020370.47
CZ08 | cDXHP | Existing | Heating | 2208.45 | 110796.92
CZ08 | cDXHP | Existing | Cooling | 486508.22 | 0
CZ08 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ08 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ08 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXHP | Existing | Fans | 787785.37 | 0
CZ08 | cDXHP | Existing | Pumps | 0 | 0
CZ08 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ08 | cDXHP | Existing | Humidification | 0 | 0
CZ08 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ08 | cDXHP | Existing | Water Systems | 0 | 718448.55
CZ08 | cDXHP | Existing | Refrigeration | 0 | 0
CZ08 | cDXHP | Existing | Generators | 0 | 0
CZ08 | cDXHP | Existing | Total End Uses | 2832115.81 | 1048090.32
CZ09 | cDXHP | Existing | Heating | 1547.89 | 90247.91
CZ09 | cDXHP | Existing | Cooling | 561212.3 | 0
CZ09 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ09 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ09 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXHP | Existing | Fans | 828348.35 | 0
CZ09 | cDXHP | Existing | Pumps | 0 | 0
CZ09 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ09 | cDXHP | Existing | Humidification | 0 | 0
CZ09 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ09 | cDXHP | Existing | Water Systems | 0 | 708431.8
CZ09 | cDXHP | Existing | Refrigeration | 0 | 0
CZ09 | cDXHP | Existing | Generators | 0 | 0
CZ09 | cDXHP | Existing | Total End Uses | 2946722.32 | 1017524.56
CZ10 | cDXHP | Existing | Heating | 7666.46 | 194273.33
CZ10 | cDXHP | Existing | Cooling | 718161.77 | 0
CZ10 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ10 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ10 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXHP | Existing | Fans | 855929.04 | 0
CZ10 | cDXHP | Existing | Pumps | 0 | 0
CZ10 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ10 | cDXHP | Existing | Humidification | 0 | 0
CZ10 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ10 | cDXHP | Existing | Water Systems | 0 | 702454.95
CZ10 | cDXHP | Existing | Refrigeration | 0 | 0
CZ10 | cDXHP | Existing | Generators | 0 | 0
CZ10 | cDXHP | Existing | Total End Uses | 3137371.04 | 1115573.13
CZ11 | cDXHP | Existing | Heating | 18105.69 | 426368.93
CZ11 | cDXHP | Existing | Cooling | 740169.85 | 0
CZ11 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ11 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ11 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXHP | Existing | Fans | 901973.06 | 0
CZ11 | cDXHP | Existing | Pumps | 0 | 0
CZ11 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ11 | cDXHP | Existing | Humidification | 0 | 0
CZ11 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ11 | cDXHP | Existing | Water Systems | 0 | 717931.34
CZ11 | cDXHP | Existing | Refrigeration | 0 | 0
CZ11 | cDXHP | Existing | Generators | 0 | 0
CZ11 | cDXHP | Existing | Total End Uses | 3215862.37 | 1363145.13
CZ12 | cDXHP | Existing | Heating | 16720.04 | 410647.11
CZ12 | cDXHP | Existing | Cooling | 606983.38 | 0
CZ12 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ12 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ12 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXHP | Existing | Fans | 833996.89 | 0
CZ12 | cDXHP | Existing | Pumps | 0 | 0
CZ12 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ12 | cDXHP | Existing | Humidification | 0 | 0
CZ12 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ12 | cDXHP | Existing | Water Systems | 0 | 738425.6
CZ12 | cDXHP | Existing | Refrigeration | 0 | 0
CZ12 | cDXHP | Existing | Generators | 0 | 0
CZ12 | cDXHP | Existing | Total End Uses | 3013314.08 | 1367917.57
CZ13 | cDXHP | Existing | Heating | 11986.89 | 332837.35
CZ13 | cDXHP | Existing | Cooling | 820388.12 | 0
CZ13 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ13 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ13 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXHP | Existing | Fans | 868383.63 | 0
CZ13 | cDXHP | Existing | Pumps | 0 | 0
CZ13 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ13 | cDXHP | Existing | Humidification | 0 | 0
CZ13 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ13 | cDXHP | Existing | Water Systems | 0 | 697038.18
CZ13 | cDXHP | Existing | Refrigeration | 0 | 0
CZ13 | cDXHP | Existing | Generators | 0 | 0
CZ13 | cDXHP | Existing | Total End Uses | 3256372.41 | 1248720.39
CZ14 | cDXHP | Existing | Heating | 6726.05 | 206256.27
CZ14 | cDXHP | Existing | Cooling | 1024733.88 | 0
CZ14 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ14 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ14 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXHP | Existing | Fans | 906120.08 | 0
CZ14 | cDXHP | Existing | Pumps | 0 | 0
CZ14 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ14 | cDXHP | Existing | Humidification | 0 | 0
CZ14 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ14 | cDXHP | Existing | Water Systems | 0 | 661472.32
CZ14 | cDXHP | Existing | Refrigeration | 0 | 0
CZ14 | cDXHP | Existing | Generators | 0 | 0
CZ14 | cDXHP | Existing | Total End Uses | 3493193.78 | 1086573.44
CZ15 | cDXHP | Existing | Heating | 1887.11 | 73238.93
CZ15 | cDXHP | Existing | Cooling | 1434503.51 | 0
CZ15 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ15 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ15 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXHP | Existing | Fans | 860477.41 | 0
CZ15 | cDXHP | Existing | Pumps | 0 | 0
CZ15 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ15 | cDXHP | Existing | Humidification | 0 | 0
CZ15 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ15 | cDXHP | Existing | Water Systems | 0 | 587121.45
CZ15 | cDXHP | Existing | Refrigeration | 0 | 0
CZ15 | cDXHP | Existing | Generators | 0 | 0
CZ15 | cDXHP | Existing | Total End Uses | 3852481.8 | 879205.24
CZ16 | cDXHP | Existing | Heating | 31595.03 | 551691.66
CZ16 | cDXHP | Existing | Cooling | 646985.28 | 0
CZ16 | cDXHP | Existing | Interior Lighting | 673572.97 | 0
CZ16 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXHP | Existing | Interior Equipment | 882040.8 | 218844.85
CZ16 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXHP | Existing | Fans | 950512.43 | 0
CZ16 | cDXHP | Existing | Pumps | 0 | 0
CZ16 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ16 | cDXHP | Existing | Humidification | 0 | 0
CZ16 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ16 | cDXHP | Existing | Water Systems | 0 | 780678.96
CZ16 | cDXHP | Existing | Refrigeration | 0 | 0
CZ16 | cDXHP | Existing | Generators | 0 | 0
CZ16 | cDXHP | Existing | Total End Uses | 3184706.5 | 1551215.47
CZ01 | cDXHP | New Construction | Heating | 30288.92 | 767513.17
CZ01 | cDXHP | New Construction | Cooling | 37493.71 | 0
CZ01 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ01 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ01 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXHP | New Construction | Fans | 548553.31 | 0
CZ01 | cDXHP | New Construction | Pumps | 0 | 0
CZ01 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXHP | New Construction | Humidification | 0 | 0
CZ01 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXHP | New Construction | Water Systems | 0 | 864445.23
CZ01 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ01 | cDXHP | New Construction | Generators | 0 | 0
CZ01 | cDXHP | New Construction | Total End Uses | 1820827.39 | 1850803.26
CZ02 | cDXHP | New Construction | Heating | 27695.33 | 573107.64
CZ02 | cDXHP | New Construction | Cooling | 239272.9 | 0
CZ02 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ02 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ02 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXHP | New Construction | Fans | 734509.73 | 0
CZ02 | cDXHP | New Construction | Pumps | 0 | 0
CZ02 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXHP | New Construction | Humidification | 0 | 0
CZ02 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXHP | New Construction | Water Systems | 0 | 793983.87
CZ02 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ02 | cDXHP | New Construction | Generators | 0 | 0
CZ02 | cDXHP | New Construction | Total End Uses | 2205969.42 | 1585936.36
CZ03 | cDXHP | New Construction | Heating | 15653.61 | 415091.94
CZ03 | cDXHP | New Construction | Cooling | 141930.94 | 0
CZ03 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ03 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ03 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXHP | New Construction | Fans | 690414.38 | 0
CZ03 | cDXHP | New Construction | Pumps | 0 | 0
CZ03 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXHP | New Construction | Humidification | 0 | 0
CZ03 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXHP | New Construction | Water Systems | 0 | 791040.65
CZ03 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ03 | cDXHP | New Construction | Generators | 0 | 0
CZ03 | cDXHP | New Construction | Total End Uses | 2052490.38 | 1424977.44
CZ04 | cDXHP | New Construction | Heating | 13739.54 | 351537.77
CZ04 | cDXHP | New Construction | Cooling | 291459.74 | 0
CZ04 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ04 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ04 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXHP | New Construction | Fans | 721856.03 | 0
CZ04 | cDXHP | New Construction | Pumps | 0 | 0
CZ04 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXHP | New Construction | Humidification | 0 | 0
CZ04 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXHP | New Construction | Water Systems | 0 | 763646.42
CZ04 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ04 | cDXHP | New Construction | Generators | 0 | 0
CZ04 | cDXHP | New Construction | Total End Uses | 2231546.76 | 1334029.03
CZ05 | cDXHP | New Construction | Heating | 14854.18 | 380474.25
CZ05 | cDXHP | New Construction | Cooling | 181348.36 | 0
CZ05 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ05 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ05 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXHP | New Construction | Fans | 671862.24 | 0
CZ05 | cDXHP | New Construction | Pumps | 0 | 0
CZ05 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXHP | New Construction | Humidification | 0 | 0
CZ05 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXHP | New Construction | Water Systems | 0 | 791097.24
CZ05 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ05 | cDXHP | New Construction | Generators | 0 | 0
CZ05 | cDXHP | New Construction | Total End Uses | 2072556.24 | 1390416.34
CZ06 | cDXHP | New Construction | Heating | 3100.93 | 118057.87
CZ06 | cDXHP | New Construction | Cooling | 294863.17 | 0
CZ06 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ06 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ06 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXHP | New Construction | Fans | 663917.25 | 0
CZ06 | cDXHP | New Construction | Pumps | 0 | 0
CZ06 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXHP | New Construction | Humidification | 0 | 0
CZ06 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXHP | New Construction | Water Systems | 0 | 728518.5
CZ06 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ06 | cDXHP | New Construction | Generators | 0 | 0
CZ06 | cDXHP | New Construction | Total End Uses | 2166372.8 | 1065421.23
CZ07 | cDXHP | New Construction | Heating | 2928.55 | 106369.72
CZ07 | cDXHP | New Construction | Cooling | 325288.5 | 0
CZ07 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ07 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ07 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXHP | New Construction | Fans | 646350.42 | 0
CZ07 | cDXHP | New Construction | Pumps | 0 | 0
CZ07 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXHP | New Construction | Humidification | 0 | 0
CZ07 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXHP | New Construction | Water Systems | 0 | 719024.87
CZ07 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ07 | cDXHP | New Construction | Generators | 0 | 0
CZ07 | cDXHP | New Construction | Total End Uses | 2179058.92 | 1044239.44
CZ08 | cDXHP | New Construction | Heating | 4300.26 | 142494.74
CZ08 | cDXHP | New Construction | Cooling | 405442.86 | 0
CZ08 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ08 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ08 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXHP | New Construction | Fans | 692177.55 | 0
CZ08 | cDXHP | New Construction | Pumps | 0 | 0
CZ08 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXHP | New Construction | Humidification | 0 | 0
CZ08 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXHP | New Construction | Water Systems | 0 | 718007.25
CZ08 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ08 | cDXHP | New Construction | Generators | 0 | 0
CZ08 | cDXHP | New Construction | Total End Uses | 2306412.12 | 1079346.84
CZ09 | cDXHP | New Construction | Heating | 3150.22 | 109769.56
CZ09 | cDXHP | New Construction | Cooling | 463407.09 | 0
CZ09 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ09 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ09 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXHP | New Construction | Fans | 710896.52 | 0
CZ09 | cDXHP | New Construction | Pumps | 0 | 0
CZ09 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXHP | New Construction | Humidification | 0 | 0
CZ09 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXHP | New Construction | Water Systems | 0 | 708013.76
CZ09 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ09 | cDXHP | New Construction | Generators | 0 | 0
CZ09 | cDXHP | New Construction | Total End Uses | 2381945.28 | 1036628.16
CZ10 | cDXHP | New Construction | Heating | 10597.83 | 218322.78
CZ10 | cDXHP | New Construction | Cooling | 629232.07 | 0
CZ10 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ10 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ10 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXHP | New Construction | Fans | 737129.86 | 0
CZ10 | cDXHP | New Construction | Pumps | 0 | 0
CZ10 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXHP | New Construction | Humidification | 0 | 0
CZ10 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXHP | New Construction | Water Systems | 0 | 702102.54
CZ10 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ10 | cDXHP | New Construction | Generators | 0 | 0
CZ10 | cDXHP | New Construction | Total End Uses | 2581451.22 | 1139270.18
CZ11 | cDXHP | New Construction | Heating | 18619.06 | 398860.06
CZ11 | cDXHP | New Construction | Cooling | 563976.42 | 0
CZ11 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ11 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ11 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXHP | New Construction | Fans | 594871.53 | 0
CZ11 | cDXHP | New Construction | Pumps | 0 | 0
CZ11 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXHP | New Construction | Humidification | 0 | 0
CZ11 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXHP | New Construction | Water Systems | 0 | 717381.94
CZ11 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ11 | cDXHP | New Construction | Generators | 0 | 0
CZ11 | cDXHP | New Construction | Total End Uses | 2381958.46 | 1335086.85
CZ12 | cDXHP | New Construction | Heating | 18412.26 | 402352.63
CZ12 | cDXHP | New Construction | Cooling | 466228.18 | 0
CZ12 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ12 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ12 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXHP | New Construction | Fans | 577300.42 | 0
CZ12 | cDXHP | New Construction | Pumps | 0 | 0
CZ12 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXHP | New Construction | Humidification | 0 | 0
CZ12 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXHP | New Construction | Water Systems | 0 | 737899.43
CZ12 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ12 | cDXHP | New Construction | Generators | 0 | 0
CZ12 | cDXHP | New Construction | Total End Uses | 2266432.32 | 1359096.91
CZ13 | cDXHP | New Construction | Heating | 13849.93 | 331823.4
CZ13 | cDXHP | New Construction | Cooling | 625879.88 | 0
CZ13 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ13 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ13 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXHP | New Construction | Fans | 587780.55 | 0
CZ13 | cDXHP | New Construction | Pumps | 0 | 0
CZ13 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXHP | New Construction | Humidification | 0 | 0
CZ13 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXHP | New Construction | Water Systems | 0 | 696420.61
CZ13 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ13 | cDXHP | New Construction | Generators | 0 | 0
CZ13 | cDXHP | New Construction | Total End Uses | 2432001.82 | 1247088.86
CZ14 | cDXHP | New Construction | Heating | 7999.98 | 206099.41
CZ14 | cDXHP | New Construction | Cooling | 803772.88 | 0
CZ14 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ14 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ14 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXHP | New Construction | Fans | 623606.1 | 0
CZ14 | cDXHP | New Construction | Pumps | 0 | 0
CZ14 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXHP | New Construction | Humidification | 0 | 0
CZ14 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXHP | New Construction | Water Systems | 0 | 660821.12
CZ14 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ14 | cDXHP | New Construction | Generators | 0 | 0
CZ14 | cDXHP | New Construction | Total End Uses | 2639870.42 | 1085765.39
CZ15 | cDXHP | New Construction | Heating | 2626.34 | 69868.15
CZ15 | cDXHP | New Construction | Cooling | 1126194.06 | 0
CZ15 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ15 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ15 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXHP | New Construction | Fans | 593111.5 | 0
CZ15 | cDXHP | New Construction | Pumps | 0 | 0
CZ15 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXHP | New Construction | Humidification | 0 | 0
CZ15 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXHP | New Construction | Water Systems | 0 | 586508.51
CZ15 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ15 | cDXHP | New Construction | Generators | 0 | 0
CZ15 | cDXHP | New Construction | Total End Uses | 2926423.36 | 875221.52
CZ16 | cDXHP | New Construction | Heating | 33118.92 | 530575.32
CZ16 | cDXHP | New Construction | Cooling | 510394.41 | 0
CZ16 | cDXHP | New Construction | Interior Lighting | 322450.66 | 0
CZ16 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXHP | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ16 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXHP | New Construction | Fans | 649908.4 | 0
CZ16 | cDXHP | New Construction | Pumps | 0 | 0
CZ16 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXHP | New Construction | Humidification | 0 | 0
CZ16 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXHP | New Construction | Water Systems | 0 | 780212.93
CZ16 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ16 | cDXHP | New Construction | Generators | 0 | 0
CZ16 | cDXHP | New Construction | Total End Uses | 2397913.18 | 1529633.11
CZ01 | cDXOH | Existing | Heating | 0 | 719534.6
CZ01 | cDXOH | Existing | Cooling | 46500.35 | 0
CZ01 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ01 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ01 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXOH | Existing | Fans | 732189.91 | 0
CZ01 | cDXOH | Existing | Pumps | 0 | 0
CZ01 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ01 | cDXOH | Existing | Humidification | 0 | 0
CZ01 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ01 | cDXOH | Existing | Water Systems | 0 | 864653.99
CZ01 | cDXOH | Existing | Refrigeration | 0 | 0
CZ01 | cDXOH | Existing | Generators | 0 | 0
CZ01 | cDXOH | Existing | Total End Uses | 2334304.03 | 1803033.44
CZ02 | cDXOH | Existing | Heating | 0 | 472603.69
CZ02 | cDXOH | Existing | Cooling | 294155.86 | 0
CZ02 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ02 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ02 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXOH | Existing | Fans | 829872.52 | 0
CZ02 | cDXOH | Existing | Pumps | 0 | 0
CZ02 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ02 | cDXOH | Existing | Humidification | 0 | 0
CZ02 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ02 | cDXOH | Existing | Water Systems | 0 | 794289.89
CZ02 | cDXOH | Existing | Refrigeration | 0 | 0
CZ02 | cDXOH | Existing | Generators | 0 | 0
CZ02 | cDXOH | Existing | Total End Uses | 2679642.15 | 1485738.43
CZ03 | cDXOH | Existing | Heating | 0 | 319873.18
CZ03 | cDXOH | Existing | Cooling | 186874.45 | 0
CZ03 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ03 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ03 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXOH | Existing | Fans | 794366.82 | 0
CZ03 | cDXOH | Existing | Pumps | 0 | 0
CZ03 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ03 | cDXOH | Existing | Humidification | 0 | 0
CZ03 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ03 | cDXOH | Existing | Water Systems | 0 | 791294.67
CZ03 | cDXOH | Existing | Refrigeration | 0 | 0
CZ03 | cDXOH | Existing | Generators | 0 | 0
CZ03 | cDXOH | Existing | Total End Uses | 2536855.05 | 1330012.7
CZ04 | cDXOH | Existing | Heating | 0 | 285506.15
CZ04 | cDXOH | Existing | Cooling | 355409.49 | 0
CZ04 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ04 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ04 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXOH | Existing | Fans | 827998.78 | 0
CZ04 | cDXOH | Existing | Pumps | 0 | 0
CZ04 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ04 | cDXOH | Existing | Humidification | 0 | 0
CZ04 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ04 | cDXOH | Existing | Water Systems | 0 | 763951.38
CZ04 | cDXOH | Existing | Refrigeration | 0 | 0
CZ04 | cDXOH | Existing | Generators | 0 | 0
CZ04 | cDXOH | Existing | Total End Uses | 2739022.05 | 1268302.38
CZ05 | cDXOH | Existing | Heating | 0 | 301857.61
CZ05 | cDXOH | Existing | Cooling | 236642.81 | 0
CZ05 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ05 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ05 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXOH | Existing | Fans | 777003.45 | 0
CZ05 | cDXOH | Existing | Pumps | 0 | 0
CZ05 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ05 | cDXOH | Existing | Humidification | 0 | 0
CZ05 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ05 | cDXOH | Existing | Water Systems | 0 | 791310.89
CZ05 | cDXOH | Existing | Refrigeration | 0 | 0
CZ05 | cDXOH | Existing | Generators | 0 | 0
CZ05 | cDXOH | Existing | Total End Uses | 2569260.03 | 1312013.35
CZ06 | cDXOH | Existing | Heating | 0 | 86021.45
CZ06 | cDXOH | Existing | Cooling | 375619.19 | 0
CZ06 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ06 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ06 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXOH | Existing | Fans | 759616.82 | 0
CZ06 | cDXOH | Existing | Pumps | 0 | 0
CZ06 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ06 | cDXOH | Existing | Humidification | 0 | 0
CZ06 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ06 | cDXOH | Existing | Water Systems | 0 | 728867.74
CZ06 | cDXOH | Existing | Refrigeration | 0 | 0
CZ06 | cDXOH | Existing | Generators | 0 | 0
CZ06 | cDXOH | Existing | Total End Uses | 2690849.78 | 1033734.05
CZ07 | cDXOH | Existing | Heating | 0 | 82137.52
CZ07 | cDXOH | Existing | Cooling | 407130.91 | 0
CZ07 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ07 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ07 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXOH | Existing | Fans | 750685.94 | 0
CZ07 | cDXOH | Existing | Pumps | 0 | 0
CZ07 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ07 | cDXOH | Existing | Humidification | 0 | 0
CZ07 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ07 | cDXOH | Existing | Water Systems | 0 | 719492.53
CZ07 | cDXOH | Existing | Refrigeration | 0 | 0
CZ07 | cDXOH | Existing | Generators | 0 | 0
CZ07 | cDXOH | Existing | Total End Uses | 2713430.62 | 1020474.9
CZ08 | cDXOH | Existing | Heating | 0 | 110880.81
CZ08 | cDXOH | Existing | Cooling | 487895.15 | 0
CZ08 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ08 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ08 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXOH | Existing | Fans | 787784.55 | 0
CZ08 | cDXOH | Existing | Pumps | 0 | 0
CZ08 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ08 | cDXOH | Existing | Humidification | 0 | 0
CZ08 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ08 | cDXOH | Existing | Water Systems | 0 | 718448.6
CZ08 | cDXOH | Existing | Refrigeration | 0 | 0
CZ08 | cDXOH | Existing | Generators | 0 | 0
CZ08 | cDXOH | Existing | Total End Uses | 2831293.47 | 1048174.26
CZ09 | cDXOH | Existing | Heating | 0 | 90337.69
CZ09 | cDXOH | Existing | Cooling | 562916.09 | 0
CZ09 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ09 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ09 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXOH | Existing | Fans | 828344.07 | 0
CZ09 | cDXOH | Existing | Pumps | 0 | 0
CZ09 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ09 | cDXOH | Existing | Humidification | 0 | 0
CZ09 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ09 | cDXOH | Existing | Water Systems | 0 | 708431.84
CZ09 | cDXOH | Existing | Refrigeration | 0 | 0
CZ09 | cDXOH | Existing | Generators | 0 | 0
CZ09 | cDXOH | Existing | Total End Uses | 2946873.93 | 1017614.38
CZ10 | cDXOH | Existing | Heating | 0 | 194877.82
CZ10 | cDXOH | Existing | Cooling | 717941.31 | 0
CZ10 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ10 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ10 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXOH | Existing | Fans | 855984.11 | 0
CZ10 | cDXOH | Existing | Pumps | 0 | 0
CZ10 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ10 | cDXOH | Existing | Humidification | 0 | 0
CZ10 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ10 | cDXOH | Existing | Water Systems | 0 | 702459.89
CZ10 | cDXOH | Existing | Refrigeration | 0 | 0
CZ10 | cDXOH | Existing | Generators | 0 | 0
CZ10 | cDXOH | Existing | Total End Uses | 3129539.19 | 1116182.57
CZ11 | cDXOH | Existing | Heating | 0 | 429109.17
CZ11 | cDXOH | Existing | Cooling | 738792.92 | 0
CZ11 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ11 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ11 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXOH | Existing | Fans | 902711.75 | 0
CZ11 | cDXOH | Existing | Pumps | 0 | 0
CZ11 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ11 | cDXOH | Existing | Humidification | 0 | 0
CZ11 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ11 | cDXOH | Existing | Water Systems | 0 | 717955.57
CZ11 | cDXOH | Existing | Refrigeration | 0 | 0
CZ11 | cDXOH | Existing | Generators | 0 | 0
CZ11 | cDXOH | Existing | Total End Uses | 3197118.44 | 1365909.59
CZ12 | cDXOH | Existing | Heating | 0 | 413132.97
CZ12 | cDXOH | Existing | Cooling | 606547.5 | 0
CZ12 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ12 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ12 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXOH | Existing | Fans | 834535.96 | 0
CZ12 | cDXOH | Existing | Pumps | 0 | 0
CZ12 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ12 | cDXOH | Existing | Humidification | 0 | 0
CZ12 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ12 | cDXOH | Existing | Water Systems | 0 | 738430.28
CZ12 | cDXOH | Existing | Refrigeration | 0 | 0
CZ12 | cDXOH | Existing | Generators | 0 | 0
CZ12 | cDXOH | Existing | Total End Uses | 2996697.22 | 1370408.1
CZ13 | cDXOH | Existing | Heating | 0 | 334719.17
CZ13 | cDXOH | Existing | Cooling | 819849.39 | 0
CZ13 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ13 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ13 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXOH | Existing | Fans | 868651.87 | 0
CZ13 | cDXOH | Existing | Pumps | 0 | 0
CZ13 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ13 | cDXOH | Existing | Humidification | 0 | 0
CZ13 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ13 | cDXOH | Existing | Water Systems | 0 | 697041.84
CZ13 | cDXOH | Existing | Refrigeration | 0 | 0
CZ13 | cDXOH | Existing | Generators | 0 | 0
CZ13 | cDXOH | Existing | Total End Uses | 3244115.04 | 1250605.86
CZ14 | cDXOH | Existing | Heating | 0 | 206883.1
CZ14 | cDXOH | Existing | Cooling | 1023584 | 0
CZ14 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ14 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ14 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXOH | Existing | Fans | 906245.49 | 0
CZ14 | cDXOH | Existing | Pumps | 0 | 0
CZ14 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ14 | cDXOH | Existing | Humidification | 0 | 0
CZ14 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ14 | cDXOH | Existing | Water Systems | 0 | 661475.89
CZ14 | cDXOH | Existing | Refrigeration | 0 | 0
CZ14 | cDXOH | Existing | Generators | 0 | 0
CZ14 | cDXOH | Existing | Total End Uses | 3485443.26 | 1087203.84
CZ15 | cDXOH | Existing | Heating | 0 | 73352.72
CZ15 | cDXOH | Existing | Cooling | 1434208.16 | 0
CZ15 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ15 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ15 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXOH | Existing | Fans | 860490.72 | 0
CZ15 | cDXOH | Existing | Pumps | 0 | 0
CZ15 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ15 | cDXOH | Existing | Humidification | 0 | 0
CZ15 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ15 | cDXOH | Existing | Water Systems | 0 | 587126
CZ15 | cDXOH | Existing | Refrigeration | 0 | 0
CZ15 | cDXOH | Existing | Generators | 0 | 0
CZ15 | cDXOH | Existing | Total End Uses | 3850312.65 | 879323.57
CZ16 | cDXOH | Existing | Heating | 0 | 555364.61
CZ16 | cDXOH | Existing | Cooling | 644204.53 | 0
CZ16 | cDXOH | Existing | Interior Lighting | 673572.97 | 0
CZ16 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXOH | Existing | Interior Equipment | 882040.8 | 218844.85
CZ16 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXOH | Existing | Fans | 952956.76 | 0
CZ16 | cDXOH | Existing | Pumps | 0 | 0
CZ16 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ16 | cDXOH | Existing | Humidification | 0 | 0
CZ16 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ16 | cDXOH | Existing | Water Systems | 0 | 780687.63
CZ16 | cDXOH | Existing | Refrigeration | 0 | 0
CZ16 | cDXOH | Existing | Generators | 0 | 0
CZ16 | cDXOH | Existing | Total End Uses | 3152775.06 | 1554897.09
CZ01 | cDXOH | New Construction | Heating | 0 | 776906.54
CZ01 | cDXOH | New Construction | Cooling | 36322.47 | 0
CZ01 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ01 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ01 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXOH | New Construction | Fans | 548781.6 | 0
CZ01 | cDXOH | New Construction | Pumps | 0 | 0
CZ01 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXOH | New Construction | Humidification | 0 | 0
CZ01 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXOH | New Construction | Water Systems | 0 | 864514.48
CZ01 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ01 | cDXOH | New Construction | Generators | 0 | 0
CZ01 | cDXOH | New Construction | Total End Uses | 1789595.52 | 1860265.88
CZ02 | cDXOH | New Construction | Heating | 0 | 577997.83
CZ02 | cDXOH | New Construction | Cooling | 238748.32 | 0
CZ02 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ02 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ02 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXOH | New Construction | Fans | 735203.19 | 0
CZ02 | cDXOH | New Construction | Pumps | 0 | 0
CZ02 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXOH | New Construction | Humidification | 0 | 0
CZ02 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXOH | New Construction | Water Systems | 0 | 794018.72
CZ02 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ02 | cDXOH | New Construction | Generators | 0 | 0
CZ02 | cDXOH | New Construction | Total End Uses | 2178442.97 | 1590861.39
CZ03 | cDXOH | New Construction | Heating | 0 | 417879
CZ03 | cDXOH | New Construction | Cooling | 141616.88 | 0
CZ03 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ03 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ03 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXOH | New Construction | Fans | 690493.53 | 0
CZ03 | cDXOH | New Construction | Pumps | 0 | 0
CZ03 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXOH | New Construction | Humidification | 0 | 0
CZ03 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXOH | New Construction | Water Systems | 0 | 791020.37
CZ03 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ03 | cDXOH | New Construction | Generators | 0 | 0
CZ03 | cDXOH | New Construction | Total End Uses | 2036601.86 | 1427744.23
CZ04 | cDXOH | New Construction | Heating | 0 | 353611.77
CZ04 | cDXOH | New Construction | Cooling | 291096.24 | 0
CZ04 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ04 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ04 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXOH | New Construction | Fans | 722080.6 | 0
CZ04 | cDXOH | New Construction | Pumps | 0 | 0
CZ04 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXOH | New Construction | Humidification | 0 | 0
CZ04 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXOH | New Construction | Water Systems | 0 | 763625.94
CZ04 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ04 | cDXOH | New Construction | Generators | 0 | 0
CZ04 | cDXOH | New Construction | Total End Uses | 2217668.29 | 1336082.56
CZ05 | cDXOH | New Construction | Heating | 0 | 382591.08
CZ05 | cDXOH | New Construction | Cooling | 180452 | 0
CZ05 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ05 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ05 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXOH | New Construction | Fans | 671996.64 | 0
CZ05 | cDXOH | New Construction | Pumps | 0 | 0
CZ05 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXOH | New Construction | Humidification | 0 | 0
CZ05 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXOH | New Construction | Water Systems | 0 | 791092.71
CZ05 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ05 | cDXOH | New Construction | Generators | 0 | 0
CZ05 | cDXOH | New Construction | Total End Uses | 2056940.09 | 1392528.64
CZ06 | cDXOH | New Construction | Heating | 0 | 118502.94
CZ06 | cDXOH | New Construction | Cooling | 298268.47 | 0
CZ06 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ06 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ06 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXOH | New Construction | Fans | 663957.93 | 0
CZ06 | cDXOH | New Construction | Pumps | 0 | 0
CZ06 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXOH | New Construction | Humidification | 0 | 0
CZ06 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXOH | New Construction | Water Systems | 0 | 728562.14
CZ06 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ06 | cDXOH | New Construction | Generators | 0 | 0
CZ06 | cDXOH | New Construction | Total End Uses | 2166717.85 | 1065909.94
CZ07 | cDXOH | New Construction | Heating | 0 | 106816.25
CZ07 | cDXOH | New Construction | Cooling | 327704.69 | 0
CZ07 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ07 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ07 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXOH | New Construction | Fans | 646420.21 | 0
CZ07 | cDXOH | New Construction | Pumps | 0 | 0
CZ07 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXOH | New Construction | Humidification | 0 | 0
CZ07 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXOH | New Construction | Water Systems | 0 | 718980.24
CZ07 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ07 | cDXOH | New Construction | Generators | 0 | 0
CZ07 | cDXOH | New Construction | Total End Uses | 2178616.35 | 1044641.34
CZ08 | cDXOH | New Construction | Heating | 0 | 143032.74
CZ08 | cDXOH | New Construction | Cooling | 406184.48 | 0
CZ08 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ08 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ08 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXOH | New Construction | Fans | 692254.53 | 0
CZ08 | cDXOH | New Construction | Pumps | 0 | 0
CZ08 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXOH | New Construction | Humidification | 0 | 0
CZ08 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXOH | New Construction | Water Systems | 0 | 718097.22
CZ08 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ08 | cDXOH | New Construction | Generators | 0 | 0
CZ08 | cDXOH | New Construction | Total End Uses | 2302930.47 | 1079974.81
CZ09 | cDXOH | New Construction | Heating | 0 | 110091.5
CZ09 | cDXOH | New Construction | Cooling | 464721.97 | 0
CZ09 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ09 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ09 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXOH | New Construction | Fans | 710967.81 | 0
CZ09 | cDXOH | New Construction | Pumps | 0 | 0
CZ09 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXOH | New Construction | Humidification | 0 | 0
CZ09 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXOH | New Construction | Water Systems | 0 | 708051.69
CZ09 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ09 | cDXOH | New Construction | Generators | 0 | 0
CZ09 | cDXOH | New Construction | Total End Uses | 2380181.23 | 1036988.05
CZ10 | cDXOH | New Construction | Heating | 0 | 219418.96
CZ10 | cDXOH | New Construction | Cooling | 628362.78 | 0
CZ10 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ10 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ10 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXOH | New Construction | Fans | 737303.77 | 0
CZ10 | cDXOH | New Construction | Pumps | 0 | 0
CZ10 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXOH | New Construction | Humidification | 0 | 0
CZ10 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXOH | New Construction | Water Systems | 0 | 702003.87
CZ10 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ10 | cDXOH | New Construction | Generators | 0 | 0
CZ10 | cDXOH | New Construction | Total End Uses | 2570158 | 1140267.68
CZ11 | cDXOH | New Construction | Heating | 0 | 403805.57
CZ11 | cDXOH | New Construction | Cooling | 561840.87 | 0
CZ11 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ11 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ11 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXOH | New Construction | Fans | 595009.29 | 0
CZ11 | cDXOH | New Construction | Pumps | 0 | 0
CZ11 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXOH | New Construction | Humidification | 0 | 0
CZ11 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXOH | New Construction | Water Systems | 0 | 717449.49
CZ11 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ11 | cDXOH | New Construction | Generators | 0 | 0
CZ11 | cDXOH | New Construction | Total End Uses | 2361341.61 | 1340099.91
CZ12 | cDXOH | New Construction | Heating | 0 | 406916.35
CZ12 | cDXOH | New Construction | Cooling | 464686.75 | 0
CZ12 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ12 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ12 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXOH | New Construction | Fans | 577413.4 | 0
CZ12 | cDXOH | New Construction | Pumps | 0 | 0
CZ12 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXOH | New Construction | Humidification | 0 | 0
CZ12 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXOH | New Construction | Water Systems | 0 | 738083.93
CZ12 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ12 | cDXOH | New Construction | Generators | 0 | 0
CZ12 | cDXOH | New Construction | Total End Uses | 2246591.59 | 1363845.14
CZ13 | cDXOH | New Construction | Heating | 0 | 335705.73
CZ13 | cDXOH | New Construction | Cooling | 624674.37 | 0
CZ13 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ13 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ13 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXOH | New Construction | Fans | 587756.19 | 0
CZ13 | cDXOH | New Construction | Pumps | 0 | 0
CZ13 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXOH | New Construction | Humidification | 0 | 0
CZ13 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXOH | New Construction | Water Systems | 0 | 696527.32
CZ13 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ13 | cDXOH | New Construction | Generators | 0 | 0
CZ13 | cDXOH | New Construction | Total End Uses | 2416922.01 | 1251077.91
CZ14 | cDXOH | New Construction | Heating | 0 | 207614.55
CZ14 | cDXOH | New Construction | Cooling | 802135.63 | 0
CZ14 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ14 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ14 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXOH | New Construction | Fans | 623807.45 | 0
CZ14 | cDXOH | New Construction | Pumps | 0 | 0
CZ14 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXOH | New Construction | Humidification | 0 | 0
CZ14 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXOH | New Construction | Water Systems | 0 | 660871.8
CZ14 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ14 | cDXOH | New Construction | Generators | 0 | 0
CZ14 | cDXOH | New Construction | Total End Uses | 2630434.53 | 1087331.2
CZ15 | cDXOH | New Construction | Heating | 0 | 70123.05
CZ15 | cDXOH | New Construction | Cooling | 1125090.15 | 0
CZ15 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ15 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ15 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXOH | New Construction | Fans | 593160.08 | 0
CZ15 | cDXOH | New Construction | Pumps | 0 | 0
CZ15 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXOH | New Construction | Humidification | 0 | 0
CZ15 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXOH | New Construction | Water Systems | 0 | 586553.17
CZ15 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ15 | cDXOH | New Construction | Generators | 0 | 0
CZ15 | cDXOH | New Construction | Total End Uses | 2922741.68 | 875521.07
CZ16 | cDXOH | New Construction | Heating | 0 | 537230.01
CZ16 | cDXOH | New Construction | Cooling | 506150.34 | 0
CZ16 | cDXOH | New Construction | Interior Lighting | 322450.66 | 0
CZ16 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXOH | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ16 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXOH | New Construction | Fans | 651233.9 | 0
CZ16 | cDXOH | New Construction | Pumps | 0 | 0
CZ16 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXOH | New Construction | Humidification | 0 | 0
CZ16 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXOH | New Construction | Water Systems | 0 | 780244.29
CZ16 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ16 | cDXOH | New Construction | Generators | 0 | 0
CZ16 | cDXOH | New Construction | Total End Uses | 2361875.68 | 1536319.16
CZ01 | cPVVG | Existing | Heating | 0 | 875550.55
CZ01 | cPVVG | Existing | Cooling | 48744.82 | 0
CZ01 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ01 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ01 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ01 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ01 | cPVVG | Existing | Fans | 584059.61 | 0
CZ01 | cPVVG | Existing | Pumps | 0 | 0
CZ01 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ01 | cPVVG | Existing | Humidification | 0 | 0
CZ01 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ01 | cPVVG | Existing | Water Systems | 0 | 864663.07
CZ01 | cPVVG | Existing | Refrigeration | 0 | 0
CZ01 | cPVVG | Existing | Generators | 0 | 0
CZ01 | cPVVG | Existing | Total End Uses | 2188418.2 | 1959058.47
CZ02 | cPVVG | Existing | Heating | 0 | 577520.7
CZ02 | cPVVG | Existing | Cooling | 291475.74 | 0
CZ02 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ02 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ02 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ02 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ02 | cPVVG | Existing | Fans | 670208.63 | 0
CZ02 | cPVVG | Existing | Pumps | 0 | 0
CZ02 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ02 | cPVVG | Existing | Humidification | 0 | 0
CZ02 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ02 | cPVVG | Existing | Water Systems | 0 | 794287.47
CZ02 | cPVVG | Existing | Refrigeration | 0 | 0
CZ02 | cPVVG | Existing | Generators | 0 | 0
CZ02 | cPVVG | Existing | Total End Uses | 2517298.14 | 1590653.02
CZ03 | cPVVG | Existing | Heating | 0 | 380739.66
CZ03 | cPVVG | Existing | Cooling | 190186.32 | 0
CZ03 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ03 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ03 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ03 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ03 | cPVVG | Existing | Fans | 636686 | 0
CZ03 | cPVVG | Existing | Pumps | 0 | 0
CZ03 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ03 | cPVVG | Existing | Humidification | 0 | 0
CZ03 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ03 | cPVVG | Existing | Water Systems | 0 | 791295.43
CZ03 | cPVVG | Existing | Refrigeration | 0 | 0
CZ03 | cPVVG | Existing | Generators | 0 | 0
CZ03 | cPVVG | Existing | Total End Uses | 2382486.09 | 1390879.94
CZ04 | cPVVG | Existing | Heating | 0 | 342343.26
CZ04 | cPVVG | Existing | Cooling | 351900.24 | 0
CZ04 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ04 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ04 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ04 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ04 | cPVVG | Existing | Fans | 667738.13 | 0
CZ04 | cPVVG | Existing | Pumps | 0 | 0
CZ04 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ04 | cPVVG | Existing | Humidification | 0 | 0
CZ04 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ04 | cPVVG | Existing | Water Systems | 0 | 763968.52
CZ04 | cPVVG | Existing | Refrigeration | 0 | 0
CZ04 | cPVVG | Existing | Generators | 0 | 0
CZ04 | cPVVG | Existing | Total End Uses | 2575252.14 | 1325156.63
CZ05 | cPVVG | Existing | Heating | 0 | 356318.72
CZ05 | cPVVG | Existing | Cooling | 238398.69 | 0
CZ05 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ05 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ05 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ05 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ05 | cPVVG | Existing | Fans | 626087.3 | 0
CZ05 | cPVVG | Existing | Pumps | 0 | 0
CZ05 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ05 | cPVVG | Existing | Humidification | 0 | 0
CZ05 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ05 | cPVVG | Existing | Water Systems | 0 | 791326.98
CZ05 | cPVVG | Existing | Refrigeration | 0 | 0
CZ05 | cPVVG | Existing | Generators | 0 | 0
CZ05 | cPVVG | Existing | Total End Uses | 2420099.76 | 1366490.56
CZ06 | cPVVG | Existing | Heating | 0 | 98980.8
CZ06 | cPVVG | Existing | Cooling | 376690.45 | 0
CZ06 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ06 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ06 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ06 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ06 | cPVVG | Existing | Fans | 613346.57 | 0
CZ06 | cPVVG | Existing | Pumps | 0 | 0
CZ06 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ06 | cPVVG | Existing | Humidification | 0 | 0
CZ06 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ06 | cPVVG | Existing | Water Systems | 0 | 728886.42
CZ06 | cPVVG | Existing | Refrigeration | 0 | 0
CZ06 | cPVVG | Existing | Generators | 0 | 0
CZ06 | cPVVG | Existing | Total End Uses | 2545650.79 | 1046712.07
CZ07 | cPVVG | Existing | Heating | 0 | 95204.27
CZ07 | cPVVG | Existing | Cooling | 402786.55 | 0
CZ07 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ07 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ07 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ07 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ07 | cPVVG | Existing | Fans | 606411.36 | 0
CZ07 | cPVVG | Existing | Pumps | 0 | 0
CZ07 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ07 | cPVVG | Existing | Humidification | 0 | 0
CZ07 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ07 | cPVVG | Existing | Water Systems | 0 | 719497.26
CZ07 | cPVVG | Existing | Refrigeration | 0 | 0
CZ07 | cPVVG | Existing | Generators | 0 | 0
CZ07 | cPVVG | Existing | Total End Uses | 2564811.69 | 1033546.39
CZ08 | cPVVG | Existing | Heating | 0 | 129001.05
CZ08 | cPVVG | Existing | Cooling | 482401.99 | 0
CZ08 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ08 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ08 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ08 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ08 | cPVVG | Existing | Fans | 634501.63 | 0
CZ08 | cPVVG | Existing | Pumps | 0 | 0
CZ08 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ08 | cPVVG | Existing | Humidification | 0 | 0
CZ08 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ08 | cPVVG | Existing | Water Systems | 0 | 718446.68
CZ08 | cPVVG | Existing | Refrigeration | 0 | 0
CZ08 | cPVVG | Existing | Generators | 0 | 0
CZ08 | cPVVG | Existing | Total End Uses | 2672517.39 | 1066292.58
CZ09 | cPVVG | Existing | Heating | 0 | 104353.58
CZ09 | cPVVG | Existing | Cooling | 553619.19 | 0
CZ09 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ09 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ09 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ09 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ09 | cPVVG | Existing | Fans | 668162.55 | 0
CZ09 | cPVVG | Existing | Pumps | 0 | 0
CZ09 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ09 | cPVVG | Existing | Humidification | 0 | 0
CZ09 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ09 | cPVVG | Existing | Water Systems | 0 | 708442.39
CZ09 | cPVVG | Existing | Refrigeration | 0 | 0
CZ09 | cPVVG | Existing | Generators | 0 | 0
CZ09 | cPVVG | Existing | Total End Uses | 2777395.52 | 1031640.83
CZ10 | cPVVG | Existing | Heating | 0 | 239480.7
CZ10 | cPVVG | Existing | Cooling | 705916.33 | 0
CZ10 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ10 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ10 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ10 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ10 | cPVVG | Existing | Fans | 697307.09 | 0
CZ10 | cPVVG | Existing | Pumps | 0 | 0
CZ10 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ10 | cPVVG | Existing | Humidification | 0 | 0
CZ10 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ10 | cPVVG | Existing | Water Systems | 0 | 702467.74
CZ10 | cPVVG | Existing | Refrigeration | 0 | 0
CZ10 | cPVVG | Existing | Generators | 0 | 0
CZ10 | cPVVG | Existing | Total End Uses | 2958837.18 | 1160793.28
CZ11 | cPVVG | Existing | Heating | 0 | 533728.22
CZ11 | cPVVG | Existing | Cooling | 725756.4 | 0
CZ11 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ11 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ11 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ11 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ11 | cPVVG | Existing | Fans | 734045.43 | 0
CZ11 | cPVVG | Existing | Pumps | 0 | 0
CZ11 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ11 | cPVVG | Existing | Humidification | 0 | 0
CZ11 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ11 | cPVVG | Existing | Water Systems | 0 | 717948.62
CZ11 | cPVVG | Existing | Refrigeration | 0 | 0
CZ11 | cPVVG | Existing | Generators | 0 | 0
CZ11 | cPVVG | Existing | Total End Uses | 3015415.6 | 1470521.69
CZ12 | cPVVG | Existing | Heating | 0 | 505568.32
CZ12 | cPVVG | Existing | Cooling | 597667.68 | 0
CZ12 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ12 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ12 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ12 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ12 | cPVVG | Existing | Fans | 679697.56 | 0
CZ12 | cPVVG | Existing | Pumps | 0 | 0
CZ12 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ12 | cPVVG | Existing | Humidification | 0 | 0
CZ12 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ12 | cPVVG | Existing | Water Systems | 0 | 738419.83
CZ12 | cPVVG | Existing | Refrigeration | 0 | 0
CZ12 | cPVVG | Existing | Generators | 0 | 0
CZ12 | cPVVG | Existing | Total End Uses | 2832979.01 | 1462833
CZ13 | cPVVG | Existing | Heating | 0 | 405823.29
CZ13 | cPVVG | Existing | Cooling | 805964.78 | 0
CZ13 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ13 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ13 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ13 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ13 | cPVVG | Existing | Fans | 706043.52 | 0
CZ13 | cPVVG | Existing | Pumps | 0 | 0
CZ13 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ13 | cPVVG | Existing | Humidification | 0 | 0
CZ13 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ13 | cPVVG | Existing | Water Systems | 0 | 696999.02
CZ13 | cPVVG | Existing | Refrigeration | 0 | 0
CZ13 | cPVVG | Existing | Generators | 0 | 0
CZ13 | cPVVG | Existing | Total End Uses | 3067622.07 | 1321667.15
CZ14 | cPVVG | Existing | Heating | 0 | 247248.51
CZ14 | cPVVG | Existing | Cooling | 1003264.77 | 0
CZ14 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ14 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ14 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ14 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ14 | cPVVG | Existing | Fans | 735981.83 | 0
CZ14 | cPVVG | Existing | Pumps | 0 | 0
CZ14 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ14 | cPVVG | Existing | Humidification | 0 | 0
CZ14 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ14 | cPVVG | Existing | Water Systems | 0 | 661470
CZ14 | cPVVG | Existing | Refrigeration | 0 | 0
CZ14 | cPVVG | Existing | Generators | 0 | 0
CZ14 | cPVVG | Existing | Total End Uses | 3294860.38 | 1127563.36
CZ15 | cPVVG | Existing | Heating | 0 | 86420.88
CZ15 | cPVVG | Existing | Cooling | 1409318.42 | 0
CZ15 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ15 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ15 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ15 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ15 | cPVVG | Existing | Fans | 705650.1 | 0
CZ15 | cPVVG | Existing | Pumps | 0 | 0
CZ15 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ15 | cPVVG | Existing | Humidification | 0 | 0
CZ15 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ15 | cPVVG | Existing | Water Systems | 0 | 587125.27
CZ15 | cPVVG | Existing | Refrigeration | 0 | 0
CZ15 | cPVVG | Existing | Generators | 0 | 0
CZ15 | cPVVG | Existing | Total End Uses | 3670582.3 | 892391.01
CZ16 | cPVVG | Existing | Heating | 0 | 688499.43
CZ16 | cPVVG | Existing | Cooling | 633307 | 0
CZ16 | cPVVG | Existing | Interior Lighting | 673572.97 | 0
CZ16 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ16 | cPVVG | Existing | Interior Equipment | 882040.8 | 218844.85
CZ16 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ16 | cPVVG | Existing | Fans | 777063.27 | 0
CZ16 | cPVVG | Existing | Pumps | 0 | 0
CZ16 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ16 | cPVVG | Existing | Humidification | 0 | 0
CZ16 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ16 | cPVVG | Existing | Water Systems | 0 | 780675.6
CZ16 | cPVVG | Existing | Refrigeration | 0 | 0
CZ16 | cPVVG | Existing | Generators | 0 | 0
CZ16 | cPVVG | Existing | Total End Uses | 2965984.04 | 1688019.88
CZ01 | cPVVG | New Construction | Heating | 0 | 948227.48
CZ01 | cPVVG | New Construction | Cooling | 38492.08 | 0
CZ01 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ01 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ01 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ01 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ01 | cPVVG | New Construction | Fans | 446403.22 | 0
CZ01 | cPVVG | New Construction | Pumps | 0 | 0
CZ01 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ01 | cPVVG | New Construction | Humidification | 0 | 0
CZ01 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ01 | cPVVG | New Construction | Water Systems | 0 | 864529.21
CZ01 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ01 | cPVVG | New Construction | Generators | 0 | 0
CZ01 | cPVVG | New Construction | Total End Uses | 1689386.76 | 2031601.55
CZ02 | cPVVG | New Construction | Heating | 0 | 722479.31
CZ02 | cPVVG | New Construction | Cooling | 237044.37 | 0
CZ02 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ02 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ02 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ02 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ02 | cPVVG | New Construction | Fans | 614642.3 | 0
CZ02 | cPVVG | New Construction | Pumps | 0 | 0
CZ02 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ02 | cPVVG | New Construction | Humidification | 0 | 0
CZ02 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ02 | cPVVG | New Construction | Water Systems | 0 | 793981.57
CZ02 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ02 | cPVVG | New Construction | Generators | 0 | 0
CZ02 | cPVVG | New Construction | Total End Uses | 2056178.12 | 1735305.73
CZ03 | cPVVG | New Construction | Heating | 0 | 514495.55
CZ03 | cPVVG | New Construction | Cooling | 143319.24 | 0
CZ03 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ03 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ03 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ03 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ03 | cPVVG | New Construction | Fans | 573411.7 | 0
CZ03 | cPVVG | New Construction | Pumps | 0 | 0
CZ03 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ03 | cPVVG | New Construction | Humidification | 0 | 0
CZ03 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ03 | cPVVG | New Construction | Water Systems | 0 | 791063.76
CZ03 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ03 | cPVVG | New Construction | Generators | 0 | 0
CZ03 | cPVVG | New Construction | Total End Uses | 1921222.4 | 1524404.17
CZ04 | cPVVG | New Construction | Heating | 0 | 438836.7
CZ04 | cPVVG | New Construction | Cooling | 288240.72 | 0
CZ04 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ04 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ04 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ04 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ04 | cPVVG | New Construction | Fans | 602853.01 | 0
CZ04 | cPVVG | New Construction | Pumps | 0 | 0
CZ04 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ04 | cPVVG | New Construction | Humidification | 0 | 0
CZ04 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ04 | cPVVG | New Construction | Water Systems | 0 | 763577.24
CZ04 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ04 | cPVVG | New Construction | Generators | 0 | 0
CZ04 | cPVVG | New Construction | Total End Uses | 2095585.18 | 1421258.79
CZ05 | cPVVG | New Construction | Heating | 0 | 470673.93
CZ05 | cPVVG | New Construction | Cooling | 181321.07 | 0
CZ05 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ05 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ05 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ05 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ05 | cPVVG | New Construction | Fans | 560015.07 | 0
CZ05 | cPVVG | New Construction | Pumps | 0 | 0
CZ05 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ05 | cPVVG | New Construction | Humidification | 0 | 0
CZ05 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ05 | cPVVG | New Construction | Water Systems | 0 | 791113.39
CZ05 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ05 | cPVVG | New Construction | Generators | 0 | 0
CZ05 | cPVVG | New Construction | Total End Uses | 1945827.59 | 1480632.18
CZ06 | cPVVG | New Construction | Heating | 0 | 142741.15
CZ06 | cPVVG | New Construction | Cooling | 297308.73 | 0
CZ06 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ06 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ06 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ06 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ06 | cPVVG | New Construction | Fans | 553580 | 0
CZ06 | cPVVG | New Construction | Pumps | 0 | 0
CZ06 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ06 | cPVVG | New Construction | Humidification | 0 | 0
CZ06 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ06 | cPVVG | New Construction | Water Systems | 0 | 728482.02
CZ06 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ06 | cPVVG | New Construction | Generators | 0 | 0
CZ06 | cPVVG | New Construction | Total End Uses | 2055380.18 | 1090068.01
CZ07 | cPVVG | New Construction | Heating | 0 | 129312.4
CZ07 | cPVVG | New Construction | Cooling | 323353.4 | 0
CZ07 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ07 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ07 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ07 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ07 | cPVVG | New Construction | Fans | 538667.36 | 0
CZ07 | cPVVG | New Construction | Pumps | 0 | 0
CZ07 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ07 | cPVVG | New Construction | Humidification | 0 | 0
CZ07 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ07 | cPVVG | New Construction | Water Systems | 0 | 719066.75
CZ07 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ07 | cPVVG | New Construction | Generators | 0 | 0
CZ07 | cPVVG | New Construction | Total End Uses | 2066512.21 | 1067224.01
CZ08 | cPVVG | New Construction | Heating | 0 | 174201.89
CZ08 | cPVVG | New Construction | Cooling | 401788.01 | 0
CZ08 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ08 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ08 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ08 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ08 | cPVVG | New Construction | Fans | 577692.22 | 0
CZ08 | cPVVG | New Construction | Pumps | 0 | 0
CZ08 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ08 | cPVVG | New Construction | Humidification | 0 | 0
CZ08 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ08 | cPVVG | New Construction | Water Systems | 0 | 718073.63
CZ08 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ08 | cPVVG | New Construction | Generators | 0 | 0
CZ08 | cPVVG | New Construction | Total End Uses | 2183971.69 | 1111120.38
CZ09 | cPVVG | New Construction | Heating | 0 | 134539.91
CZ09 | cPVVG | New Construction | Cooling | 457656.1 | 0
CZ09 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ09 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ09 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ09 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ09 | cPVVG | New Construction | Fans | 594872.04 | 0
CZ09 | cPVVG | New Construction | Pumps | 0 | 0
CZ09 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ09 | cPVVG | New Construction | Humidification | 0 | 0
CZ09 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ09 | cPVVG | New Construction | Water Systems | 0 | 708037.59
CZ09 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ09 | cPVVG | New Construction | Generators | 0 | 0
CZ09 | cPVVG | New Construction | Total End Uses | 2257019.59 | 1061422.36
CZ10 | cPVVG | New Construction | Heating | 0 | 278255.53
CZ10 | cPVVG | New Construction | Cooling | 620052.3 | 0
CZ10 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ10 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ10 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ10 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ10 | cPVVG | New Construction | Fans | 618196.18 | 0
CZ10 | cPVVG | New Construction | Pumps | 0 | 0
CZ10 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ10 | cPVVG | New Construction | Humidification | 0 | 0
CZ10 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ10 | cPVVG | New Construction | Water Systems | 0 | 702032.98
CZ10 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ10 | cPVVG | New Construction | Generators | 0 | 0
CZ10 | cPVVG | New Construction | Total End Uses | 2442739.93 | 1199133.36
CZ11 | cPVVG | New Construction | Heating | 0 | 499258.91
CZ11 | cPVVG | New Construction | Cooling | 556525.39 | 0
CZ11 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ11 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ11 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ11 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ11 | cPVVG | New Construction | Fans | 497332.87 | 0
CZ11 | cPVVG | New Construction | Pumps | 0 | 0
CZ11 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ11 | cPVVG | New Construction | Humidification | 0 | 0
CZ11 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ11 | cPVVG | New Construction | Water Systems | 0 | 717410.31
CZ11 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ11 | cPVVG | New Construction | Generators | 0 | 0
CZ11 | cPVVG | New Construction | Total End Uses | 2258349.71 | 1435514.07
CZ12 | cPVVG | New Construction | Heating | 0 | 498800.01
CZ12 | cPVVG | New Construction | Cooling | 460589.98 | 0
CZ12 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ12 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ12 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ12 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ12 | cPVVG | New Construction | Fans | 481474.3 | 0
CZ12 | cPVVG | New Construction | Pumps | 0 | 0
CZ12 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ12 | cPVVG | New Construction | Humidification | 0 | 0
CZ12 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ12 | cPVVG | New Construction | Water Systems | 0 | 737818.5
CZ12 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ12 | cPVVG | New Construction | Generators | 0 | 0
CZ12 | cPVVG | New Construction | Total End Uses | 2146555.73 | 1455463.36
CZ13 | cPVVG | New Construction | Heating | 0 | 408375.53
CZ13 | cPVVG | New Construction | Cooling | 618662.15 | 0
CZ13 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ13 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ13 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ13 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ13 | cPVVG | New Construction | Fans | 492291.78 | 0
CZ13 | cPVVG | New Construction | Pumps | 0 | 0
CZ13 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ13 | cPVVG | New Construction | Humidification | 0 | 0
CZ13 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ13 | cPVVG | New Construction | Water Systems | 0 | 696497.11
CZ13 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ13 | cPVVG | New Construction | Generators | 0 | 0
CZ13 | cPVVG | New Construction | Total End Uses | 2315445.39 | 1323717.48
CZ14 | cPVVG | New Construction | Heating | 0 | 250976.62
CZ14 | cPVVG | New Construction | Cooling | 792726.26 | 0
CZ14 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ14 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ14 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ14 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ14 | cPVVG | New Construction | Fans | 525045.47 | 0
CZ14 | cPVVG | New Construction | Pumps | 0 | 0
CZ14 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ14 | cPVVG | New Construction | Humidification | 0 | 0
CZ14 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ14 | cPVVG | New Construction | Water Systems | 0 | 660938.07
CZ14 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ14 | cPVVG | New Construction | Generators | 0 | 0
CZ14 | cPVVG | New Construction | Total End Uses | 2522263.19 | 1130759.54
CZ15 | cPVVG | New Construction | Heating | 0 | 86144.81
CZ15 | cPVVG | New Construction | Cooling | 1114029.67 | 0
CZ15 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ15 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ15 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ15 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ15 | cPVVG | New Construction | Fans | 509836.4 | 0
CZ15 | cPVVG | New Construction | Pumps | 0 | 0
CZ15 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ15 | cPVVG | New Construction | Humidification | 0 | 0
CZ15 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ15 | cPVVG | New Construction | Water Systems | 0 | 586575.43
CZ15 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ15 | cPVVG | New Construction | Generators | 0 | 0
CZ15 | cPVVG | New Construction | Total End Uses | 2828357.52 | 891565.1
CZ16 | cPVVG | New Construction | Heating | 0 | 665992.14
CZ16 | cPVVG | New Construction | Cooling | 502058.96 | 0
CZ16 | cPVVG | New Construction | Interior Lighting | 322450.66 | 0
CZ16 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ16 | cPVVG | New Construction | Interior Equipment | 882040.8 | 218844.85
CZ16 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ16 | cPVVG | New Construction | Fans | 543425.67 | 0
CZ16 | cPVVG | New Construction | Pumps | 0 | 0
CZ16 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ16 | cPVVG | New Construction | Humidification | 0 | 0
CZ16 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ16 | cPVVG | New Construction | Water Systems | 0 | 780107.81
CZ16 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ16 | cPVVG | New Construction | Generators | 0 | 0
CZ16 | cPVVG | New Construction | Total End Uses | 2249976.08 | 1664944.8

## Raw_endusebreakdownannual (hidden)
Vintage | Climate Zone | HVAC System | End Use | Electricity [kBtu] | Natural Gas [kBtu]
Existing | CZ01 | cAVVG | Heating | 0 | 901184.08
Existing | CZ01 | cAVVG | Cooling | 50388.63 | 0
Existing | CZ01 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ01 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ01 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ01 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ01 | cAVVG | Fans | 584052.98 | 0
Existing | CZ01 | cAVVG | Pumps | 813.36 | 0
Existing | CZ01 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ01 | cAVVG | Humidification | 0 | 0
Existing | CZ01 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ01 | cAVVG | Water Systems | 0 | 864659.77
Existing | CZ01 | cAVVG | Refrigeration | 0 | 0
Existing | CZ01 | cAVVG | Generators | 0 | 0
Existing | CZ01 | cAVVG | Total End Uses | 2190868.74 | 1984688.69
Existing | CZ02 | cAVVG | Heating | 0 | 606079.51
Existing | CZ02 | cAVVG | Cooling | 323450.33 | 0
Existing | CZ02 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ02 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ02 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ02 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ02 | cAVVG | Fans | 662644.09 | 0
Existing | CZ02 | cAVVG | Pumps | 4869.72 | 0
Existing | CZ02 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ02 | cAVVG | Humidification | 0 | 0
Existing | CZ02 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ02 | cAVVG | Water Systems | 0 | 794294.24
Existing | CZ02 | cAVVG | Refrigeration | 0 | 0
Existing | CZ02 | cAVVG | Generators | 0 | 0
Existing | CZ02 | cAVVG | Total End Uses | 2546577.91 | 1619218.6
Existing | CZ03 | cAVVG | Heating | 0 | 399919.85
Existing | CZ03 | cAVVG | Cooling | 209976.31 | 0
Existing | CZ03 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ03 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ03 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ03 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ03 | cAVVG | Fans | 618307.61 | 0
Existing | CZ03 | cAVVG | Pumps | 4650.18 | 0
Existing | CZ03 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ03 | cAVVG | Humidification | 0 | 0
Existing | CZ03 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ03 | cAVVG | Water Systems | 0 | 791302.95
Existing | CZ03 | cAVVG | Refrigeration | 0 | 0
Existing | CZ03 | cAVVG | Generators | 0 | 0
Existing | CZ03 | cAVVG | Total End Uses | 2388547.87 | 1410067.65
Existing | CZ04 | cAVVG | Heating | 0 | 362607.76
Existing | CZ04 | cAVVG | Cooling | 386496.96 | 0
Existing | CZ04 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ04 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ04 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ04 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ04 | cAVVG | Fans | 654258.33 | 0
Existing | CZ04 | cAVVG | Pumps | 5515.87 | 0
Existing | CZ04 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ04 | cAVVG | Humidification | 0 | 0
Existing | CZ04 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ04 | cAVVG | Water Systems | 0 | 763976.36
Existing | CZ04 | cAVVG | Refrigeration | 0 | 0
Existing | CZ04 | cAVVG | Generators | 0 | 0
Existing | CZ04 | cAVVG | Total End Uses | 2601884.93 | 1345428.98
Existing | CZ05 | cAVVG | Heating | 0 | 376268.13
Existing | CZ05 | cAVVG | Cooling | 259227.44 | 0
Existing | CZ05 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ05 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ05 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ05 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ05 | cAVVG | Fans | 610056.75 | 0
Existing | CZ05 | cAVVG | Pumps | 5055.6 | 0
Existing | CZ05 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ05 | cAVVG | Humidification | 0 | 0
Existing | CZ05 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ05 | cAVVG | Water Systems | 0 | 791355.21
Existing | CZ05 | cAVVG | Refrigeration | 0 | 0
Existing | CZ05 | cAVVG | Generators | 0 | 0
Existing | CZ05 | cAVVG | Total End Uses | 2429953.56 | 1386468.19
Existing | CZ06 | cAVVG | Heating | 0 | 106833.85
Existing | CZ06 | cAVVG | Cooling | 417418.94 | 0
Existing | CZ06 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ06 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ06 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ06 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ06 | cAVVG | Fans | 615260.64 | 0
Existing | CZ06 | cAVVG | Pumps | 8168.31 | 0
Existing | CZ06 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ06 | cAVVG | Humidification | 0 | 0
Existing | CZ06 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ06 | cAVVG | Water Systems | 0 | 728922.8
Existing | CZ06 | cAVVG | Refrigeration | 0 | 0
Existing | CZ06 | cAVVG | Generators | 0 | 0
Existing | CZ06 | cAVVG | Total End Uses | 2596461.66 | 1054601.5
Existing | CZ07 | cAVVG | Heating | 0 | 105611.92
Existing | CZ07 | cAVVG | Cooling | 456156.68 | 0
Existing | CZ07 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ07 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ07 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ07 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ07 | cAVVG | Fans | 617620.56 | 0
Existing | CZ07 | cAVVG | Pumps | 8774.12 | 0
Existing | CZ07 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ07 | cAVVG | Humidification | 0 | 0
Existing | CZ07 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ07 | cAVVG | Water Systems | 0 | 719530.06
Existing | CZ07 | cAVVG | Refrigeration | 0 | 0
Existing | CZ07 | cAVVG | Generators | 0 | 0
Existing | CZ07 | cAVVG | Total End Uses | 2638165.13 | 1043986.84
Existing | CZ08 | cAVVG | Heating | 0 | 142970.63
Existing | CZ08 | cAVVG | Cooling | 538510.36 | 0
Existing | CZ08 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ08 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ08 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ08 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ08 | cAVVG | Fans | 634358.83 | 0
Existing | CZ08 | cAVVG | Pumps | 7772.3 | 0
Existing | CZ08 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ08 | cAVVG | Humidification | 0 | 0
Existing | CZ08 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ08 | cAVVG | Water Systems | 0 | 718474.27
Existing | CZ08 | cAVVG | Refrigeration | 0 | 0
Existing | CZ08 | cAVVG | Generators | 0 | 0
Existing | CZ08 | cAVVG | Total End Uses | 2736255.27 | 1080289.76
Existing | CZ09 | cAVVG | Heating | 0 | 119899.1
Existing | CZ09 | cAVVG | Cooling | 614823.2 | 0
Existing | CZ09 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ09 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ09 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ09 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ09 | cAVVG | Fans | 667919 | 0
Existing | CZ09 | cAVVG | Pumps | 8179.6 | 0
Existing | CZ09 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ09 | cAVVG | Humidification | 0 | 0
Existing | CZ09 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ09 | cAVVG | Water Systems | 0 | 708479.43
Existing | CZ09 | cAVVG | Refrigeration | 0 | 0
Existing | CZ09 | cAVVG | Generators | 0 | 0
Existing | CZ09 | cAVVG | Total End Uses | 2846535.57 | 1047223.38
Existing | CZ10 | cAVVG | Heating | 0 | 259402.75
Existing | CZ10 | cAVVG | Cooling | 774477.43 | 0
Existing | CZ10 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ10 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ10 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ10 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ10 | cAVVG | Fans | 700530.99 | 0
Existing | CZ10 | cAVVG | Pumps | 7965.88 | 0
Existing | CZ10 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ10 | cAVVG | Humidification | 0 | 0
Existing | CZ10 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ10 | cAVVG | Water Systems | 0 | 702475.66
Existing | CZ10 | cAVVG | Refrigeration | 0 | 0
Existing | CZ10 | cAVVG | Generators | 0 | 0
Existing | CZ10 | cAVVG | Total End Uses | 3038588.07 | 1180723.26
Existing | CZ11 | cAVVG | Heating | 0 | 563053.27
Existing | CZ11 | cAVVG | Cooling | 788700.58 | 0
Existing | CZ11 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ11 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ11 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ11 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ11 | cAVVG | Fans | 734616.42 | 0
Existing | CZ11 | cAVVG | Pumps | 7100.01 | 0
Existing | CZ11 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ11 | cAVVG | Humidification | 0 | 0
Existing | CZ11 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ11 | cAVVG | Water Systems | 0 | 717982.65
Existing | CZ11 | cAVVG | Refrigeration | 0 | 0
Existing | CZ11 | cAVVG | Generators | 0 | 0
Existing | CZ11 | cAVVG | Total End Uses | 3086030.78 | 1499880.77
Existing | CZ12 | cAVVG | Heating | 0 | 530827.47
Existing | CZ12 | cAVVG | Cooling | 654669.99 | 0
Existing | CZ12 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ12 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ12 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ12 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ12 | cAVVG | Fans | 688430.16 | 0
Existing | CZ12 | cAVVG | Pumps | 6914.84 | 0
Existing | CZ12 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ12 | cAVVG | Humidification | 0 | 0
Existing | CZ12 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ12 | cAVVG | Water Systems | 0 | 738437.39
Existing | CZ12 | cAVVG | Refrigeration | 0 | 0
Existing | CZ12 | cAVVG | Generators | 0 | 0
Existing | CZ12 | cAVVG | Total End Uses | 2905628.76 | 1488109.72
Existing | CZ13 | cAVVG | Heating | 0 | 427453.44
Existing | CZ13 | cAVVG | Cooling | 875601.38 | 0
Existing | CZ13 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ13 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ13 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ13 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ13 | cAVVG | Fans | 711270.97 | 0
Existing | CZ13 | cAVVG | Pumps | 8020.29 | 0
Existing | CZ13 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ13 | cAVVG | Humidification | 0 | 0
Existing | CZ13 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ13 | cAVVG | Water Systems | 0 | 697016.25
Existing | CZ13 | cAVVG | Refrigeration | 0 | 0
Existing | CZ13 | cAVVG | Generators | 0 | 0
Existing | CZ13 | cAVVG | Total End Uses | 3150506.41 | 1343314.54
Existing | CZ14 | cAVVG | Heating | 0 | 265792.25
Existing | CZ14 | cAVVG | Cooling | 1079000.5 | 0
Existing | CZ14 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ14 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ14 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ14 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ14 | cAVVG | Fans | 737586.68 | 0
Existing | CZ14 | cAVVG | Pumps | 7739.81 | 0
Existing | CZ14 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ14 | cAVVG | Humidification | 0 | 0
Existing | CZ14 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ14 | cAVVG | Water Systems | 0 | 661517.48
Existing | CZ14 | cAVVG | Refrigeration | 0 | 0
Existing | CZ14 | cAVVG | Generators | 0 | 0
Existing | CZ14 | cAVVG | Total End Uses | 3379940.76 | 1146154.57
Existing | CZ15 | cAVVG | Heating | 0 | 99638.52
Existing | CZ15 | cAVVG | Cooling | 1536652.66 | 0
Existing | CZ15 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ15 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ15 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ15 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ15 | cAVVG | Fans | 711061.69 | 0
Existing | CZ15 | cAVVG | Pumps | 11355.94 | 0
Existing | CZ15 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ15 | cAVVG | Humidification | 0 | 0
Existing | CZ15 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ15 | cAVVG | Water Systems | 0 | 587120.66
Existing | CZ15 | cAVVG | Refrigeration | 0 | 0
Existing | CZ15 | cAVVG | Generators | 0 | 0
Existing | CZ15 | cAVVG | Total End Uses | 3814684.06 | 905604.03
Existing | CZ16 | cAVVG | Heating | 0 | 720403.09
Existing | CZ16 | cAVVG | Cooling | 679749.43 | 0
Existing | CZ16 | cAVVG | Interior Lighting | 673572.97 | 0
Existing | CZ16 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ16 | cAVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ16 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ16 | cAVVG | Fans | 796671.46 | 0
Existing | CZ16 | cAVVG | Pumps | 7406.32 | 0
Existing | CZ16 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ16 | cAVVG | Humidification | 0 | 0
Existing | CZ16 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ16 | cAVVG | Water Systems | 0 | 780702.03
Existing | CZ16 | cAVVG | Refrigeration | 0 | 0
Existing | CZ16 | cAVVG | Generators | 0 | 0
Existing | CZ16 | cAVVG | Total End Uses | 3039440.99 | 1719949.97
New Construction | CZ01 | cAVVG | Heating | 0 | 956981.74
New Construction | CZ01 | cAVVG | Cooling | 40833.91 | 0
New Construction | CZ01 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ01 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ01 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ01 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ01 | cAVVG | Fans | 475517.06 | 0
New Construction | CZ01 | cAVVG | Pumps | 628.4 | 0
New Construction | CZ01 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ01 | cAVVG | Humidification | 0 | 0
New Construction | CZ01 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ01 | cAVVG | Water Systems | 0 | 864505.76
New Construction | CZ01 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ01 | cAVVG | Generators | 0 | 0
New Construction | CZ01 | cAVVG | Total End Uses | 1721470.83 | 2040332.36
New Construction | CZ02 | cAVVG | Heating | 0 | 753225.8
New Construction | CZ02 | cAVVG | Cooling | 267416.63 | 0
New Construction | CZ02 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ02 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ02 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ02 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ02 | cAVVG | Fans | 624873.21 | 0
New Construction | CZ02 | cAVVG | Pumps | 4013.86 | 0
New Construction | CZ02 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ02 | cAVVG | Humidification | 0 | 0
New Construction | CZ02 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ02 | cAVVG | Water Systems | 0 | 794064.01
New Construction | CZ02 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ02 | cAVVG | Generators | 0 | 0
New Construction | CZ02 | cAVVG | Total End Uses | 2100795.15 | 1766134.66
New Construction | CZ03 | cAVVG | Heating | 0 | 530150.17
New Construction | CZ03 | cAVVG | Cooling | 161545 | 0
New Construction | CZ03 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ03 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ03 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ03 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ03 | cAVVG | Fans | 567911.93 | 0
New Construction | CZ03 | cAVVG | Pumps | 3348.84 | 0
New Construction | CZ03 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ03 | cAVVG | Humidification | 0 | 0
New Construction | CZ03 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ03 | cAVVG | Water Systems | 0 | 791125.99
New Construction | CZ03 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ03 | cAVVG | Generators | 0 | 0
New Construction | CZ03 | cAVVG | Total End Uses | 1937297.23 | 1540121.01
New Construction | CZ04 | cAVVG | Heating | 0 | 457189.07
New Construction | CZ04 | cAVVG | Cooling | 320739.77 | 0
New Construction | CZ04 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ04 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ04 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ04 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ04 | cAVVG | Fans | 601684.41 | 0
New Construction | CZ04 | cAVVG | Pumps | 4528.18 | 0
New Construction | CZ04 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ04 | cAVVG | Humidification | 0 | 0
New Construction | CZ04 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ04 | cAVVG | Water Systems | 0 | 763642.19
New Construction | CZ04 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ04 | cAVVG | Generators | 0 | 0
New Construction | CZ04 | cAVVG | Total End Uses | 2131443.81 | 1439676.12
New Construction | CZ05 | cAVVG | Heating | 0 | 489736.91
New Construction | CZ05 | cAVVG | Cooling | 200974.31 | 0
New Construction | CZ05 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ05 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ05 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ05 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ05 | cAVVG | Fans | 555045.57 | 0
New Construction | CZ05 | cAVVG | Pumps | 3712.8 | 0
New Construction | CZ05 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ05 | cAVVG | Humidification | 0 | 0
New Construction | CZ05 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ05 | cAVVG | Water Systems | 0 | 791117.02
New Construction | CZ05 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ05 | cAVVG | Generators | 0 | 0
New Construction | CZ05 | cAVVG | Total End Uses | 1964224.14 | 1499698.78
New Construction | CZ06 | cAVVG | Heating | 0 | 155839.48
New Construction | CZ06 | cAVVG | Cooling | 337097.5 | 0
New Construction | CZ06 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ06 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ06 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ06 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ06 | cAVVG | Fans | 559343.07 | 0
New Construction | CZ06 | cAVVG | Pumps | 6476.9 | 0
New Construction | CZ06 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ06 | cAVVG | Humidification | 0 | 0
New Construction | CZ06 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ06 | cAVVG | Water Systems | 0 | 728645.06
New Construction | CZ06 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ06 | cAVVG | Generators | 0 | 0
New Construction | CZ06 | cAVVG | Total End Uses | 2107408.92 | 1103329.4
New Construction | CZ07 | cAVVG | Heating | 0 | 146905.52
New Construction | CZ07 | cAVVG | Cooling | 372079.36 | 0
New Construction | CZ07 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ07 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ07 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ07 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ07 | cAVVG | Fans | 552128.9 | 0
New Construction | CZ07 | cAVVG | Pumps | 6082.13 | 0
New Construction | CZ07 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ07 | cAVVG | Humidification | 0 | 0
New Construction | CZ07 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ07 | cAVVG | Water Systems | 0 | 719206.82
New Construction | CZ07 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ07 | cAVVG | Generators | 0 | 0
New Construction | CZ07 | cAVVG | Total End Uses | 2134781.84 | 1084957.19
New Construction | CZ08 | cAVVG | Heating | 0 | 192401.17
New Construction | CZ08 | cAVVG | Cooling | 454148.84 | 0
New Construction | CZ08 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ08 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ08 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ08 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ08 | cAVVG | Fans | 585742.42 | 0
New Construction | CZ08 | cAVVG | Pumps | 6307.22 | 0
New Construction | CZ08 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ08 | cAVVG | Humidification | 0 | 0
New Construction | CZ08 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ08 | cAVVG | Water Systems | 0 | 718186.58
New Construction | CZ08 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ08 | cAVVG | Generators | 0 | 0
New Construction | CZ08 | cAVVG | Total End Uses | 2250689.93 | 1129432.6
New Construction | CZ09 | cAVVG | Heating | 0 | 154236.35
New Construction | CZ09 | cAVVG | Cooling | 513024.08 | 0
New Construction | CZ09 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ09 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ09 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ09 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ09 | cAVVG | Fans | 603547.03 | 0
New Construction | CZ09 | cAVVG | Pumps | 6506.62 | 0
New Construction | CZ09 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ09 | cAVVG | Humidification | 0 | 0
New Construction | CZ09 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ09 | cAVVG | Water Systems | 0 | 708140.1
New Construction | CZ09 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ09 | cAVVG | Generators | 0 | 0
New Construction | CZ09 | cAVVG | Total End Uses | 2327569.19 | 1081221.3
New Construction | CZ10 | cAVVG | Heating | 0 | 297904.1
New Construction | CZ10 | cAVVG | Cooling | 680789.64 | 0
New Construction | CZ10 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ10 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ10 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ10 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ10 | cAVVG | Fans | 628650.85 | 0
New Construction | CZ10 | cAVVG | Pumps | 6633.62 | 0
New Construction | CZ10 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ10 | cAVVG | Humidification | 0 | 0
New Construction | CZ10 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ10 | cAVVG | Water Systems | 0 | 702067.83
New Construction | CZ10 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ10 | cAVVG | Generators | 0 | 0
New Construction | CZ10 | cAVVG | Total End Uses | 2520565.56 | 1218816.77
New Construction | CZ11 | cAVVG | Heating | 0 | 513806.34
New Construction | CZ11 | cAVVG | Cooling | 606691.08 | 0
New Construction | CZ11 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ11 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ11 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ11 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ11 | cAVVG | Fans | 519629.82 | 0
New Construction | CZ11 | cAVVG | Pumps | 5120.28 | 0
New Construction | CZ11 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ11 | cAVVG | Humidification | 0 | 0
New Construction | CZ11 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ11 | cAVVG | Water Systems | 0 | 717344
New Construction | CZ11 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ11 | cAVVG | Generators | 0 | 0
New Construction | CZ11 | cAVVG | Total End Uses | 2335932.64 | 1449995.19
New Construction | CZ12 | cAVVG | Heating | 0 | 506240.6
New Construction | CZ12 | cAVVG | Cooling | 507337.98 | 0
New Construction | CZ12 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ12 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ12 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ12 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ12 | cAVVG | Fans | 512044.37 | 0
New Construction | CZ12 | cAVVG | Pumps | 5209.05 | 0
New Construction | CZ12 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ12 | cAVVG | Humidification | 0 | 0
New Construction | CZ12 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ12 | cAVVG | Water Systems | 0 | 737920.96
New Construction | CZ12 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ12 | cAVVG | Generators | 0 | 0
New Construction | CZ12 | cAVVG | Total End Uses | 2229082.85 | 1463006.41
New Construction | CZ13 | cAVVG | Heating | 0 | 419491.77
New Construction | CZ13 | cAVVG | Cooling | 673658.06 | 0
New Construction | CZ13 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ13 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ13 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ13 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ13 | cAVVG | Fans | 518807.27 | 0
New Construction | CZ13 | cAVVG | Pumps | 5778.19 | 0
New Construction | CZ13 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ13 | cAVVG | Humidification | 0 | 0
New Construction | CZ13 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ13 | cAVVG | Water Systems | 0 | 696548.06
New Construction | CZ13 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ13 | cAVVG | Generators | 0 | 0
New Construction | CZ13 | cAVVG | Total End Uses | 2402734.97 | 1334884.69
New Construction | CZ14 | cAVVG | Heating | 0 | 264740.83
New Construction | CZ14 | cAVVG | Cooling | 854375.83 | 0
New Construction | CZ14 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ14 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ14 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ14 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ14 | cAVVG | Fans | 547536.71 | 0
New Construction | CZ14 | cAVVG | Pumps | 5528.9 | 0
New Construction | CZ14 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ14 | cAVVG | Humidification | 0 | 0
New Construction | CZ14 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ14 | cAVVG | Water Systems | 0 | 660893.49
New Construction | CZ14 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ14 | cAVVG | Generators | 0 | 0
New Construction | CZ14 | cAVVG | Total End Uses | 2611932.89 | 1144479.17
New Construction | CZ15 | cAVVG | Heating | 0 | 101818.15
New Construction | CZ15 | cAVVG | Cooling | 1222946.93 | 0
New Construction | CZ15 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ15 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ15 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ15 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ15 | cAVVG | Fans | 536171.53 | 0
New Construction | CZ15 | cAVVG | Pumps | 8279.39 | 0
New Construction | CZ15 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ15 | cAVVG | Humidification | 0 | 0
New Construction | CZ15 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ15 | cAVVG | Water Systems | 0 | 586612.37
New Construction | CZ15 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ15 | cAVVG | Generators | 0 | 0
New Construction | CZ15 | cAVVG | Total End Uses | 2971889.29 | 907275.37
New Construction | CZ16 | cAVVG | Heating | 0 | 672125.23
New Construction | CZ16 | cAVVG | Cooling | 540384.47 | 0
New Construction | CZ16 | cAVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ16 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ16 | cAVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ16 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ16 | cAVVG | Fans | 585044.75 | 0
New Construction | CZ16 | cAVVG | Pumps | 5259.63 | 0
New Construction | CZ16 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ16 | cAVVG | Humidification | 0 | 0
New Construction | CZ16 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ16 | cAVVG | Water Systems | 0 | 780229.66
New Construction | CZ16 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ16 | cAVVG | Generators | 0 | 0
New Construction | CZ16 | cAVVG | Total End Uses | 2335180.3 | 1671199.75
Existing | CZ01 | cDXGF | Heating | 0 | 813325.03
Existing | CZ01 | cDXGF | Cooling | 47280.63 | 0
Existing | CZ01 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ01 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ01 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXGF | Fans | 731884.77 | 0
Existing | CZ01 | cDXGF | Pumps | 0 | 0
Existing | CZ01 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ01 | cDXGF | Humidification | 0 | 0
Existing | CZ01 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ01 | cDXGF | Water Systems | 0 | 864674.75
Existing | CZ01 | cDXGF | Refrigeration | 0 | 0
Existing | CZ01 | cDXGF | Generators | 0 | 0
Existing | CZ01 | cDXGF | Total End Uses | 2334779.17 | 1896844.63
Existing | CZ02 | cDXGF | Heating | 0 | 536988.41
Existing | CZ02 | cDXGF | Cooling | 294972.88 | 0
Existing | CZ02 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ02 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ02 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXGF | Fans | 829572.51 | 0
Existing | CZ02 | cDXGF | Pumps | 0 | 0
Existing | CZ02 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ02 | cDXGF | Humidification | 0 | 0
Existing | CZ02 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ02 | cDXGF | Water Systems | 0 | 794290.78
Existing | CZ02 | cDXGF | Refrigeration | 0 | 0
Existing | CZ02 | cDXGF | Generators | 0 | 0
Existing | CZ02 | cDXGF | Total End Uses | 2680159.16 | 1550124.05
Existing | CZ03 | cDXGF | Heating | 0 | 353326.92
Existing | CZ03 | cDXGF | Cooling | 187228.14 | 0
Existing | CZ03 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ03 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ03 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXGF | Fans | 794233.61 | 0
Existing | CZ03 | cDXGF | Pumps | 0 | 0
Existing | CZ03 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ03 | cDXGF | Humidification | 0 | 0
Existing | CZ03 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ03 | cDXGF | Water Systems | 0 | 791289.4
Existing | CZ03 | cDXGF | Refrigeration | 0 | 0
Existing | CZ03 | cDXGF | Generators | 0 | 0
Existing | CZ03 | cDXGF | Total End Uses | 2537075.53 | 1363461.17
Existing | CZ04 | cDXGF | Heating | 0 | 316572.12
Existing | CZ04 | cDXGF | Cooling | 355821.14 | 0
Existing | CZ04 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ04 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ04 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXGF | Fans | 827834.44 | 0
Existing | CZ04 | cDXGF | Pumps | 0 | 0
Existing | CZ04 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ04 | cDXGF | Humidification | 0 | 0
Existing | CZ04 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ04 | cDXGF | Water Systems | 0 | 763979.44
Existing | CZ04 | cDXGF | Refrigeration | 0 | 0
Existing | CZ04 | cDXGF | Generators | 0 | 0
Existing | CZ04 | cDXGF | Total End Uses | 2739269.35 | 1299396.42
Existing | CZ05 | cDXGF | Heating | 0 | 333094.88
Existing | CZ05 | cDXGF | Cooling | 237215.82 | 0
Existing | CZ05 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ05 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ05 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXGF | Fans | 776966.85 | 0
Existing | CZ05 | cDXGF | Pumps | 0 | 0
Existing | CZ05 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ05 | cDXGF | Humidification | 0 | 0
Existing | CZ05 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ05 | cDXGF | Water Systems | 0 | 791317.75
Existing | CZ05 | cDXGF | Refrigeration | 0 | 0
Existing | CZ05 | cDXGF | Generators | 0 | 0
Existing | CZ05 | cDXGF | Total End Uses | 2569796.44 | 1343257.49
Existing | CZ06 | cDXGF | Heating | 0 | 91809.33
Existing | CZ06 | cDXGF | Cooling | 375716.59 | 0
Existing | CZ06 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ06 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ06 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXGF | Fans | 759586.33 | 0
Existing | CZ06 | cDXGF | Pumps | 0 | 0
Existing | CZ06 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ06 | cDXGF | Humidification | 0 | 0
Existing | CZ06 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ06 | cDXGF | Water Systems | 0 | 728874.34
Existing | CZ06 | cDXGF | Refrigeration | 0 | 0
Existing | CZ06 | cDXGF | Generators | 0 | 0
Existing | CZ06 | cDXGF | Total End Uses | 2690916.69 | 1039528.52
Existing | CZ07 | cDXGF | Heating | 0 | 88313.79
Existing | CZ07 | cDXGF | Cooling | 407232.31 | 0
Existing | CZ07 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ07 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ07 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXGF | Fans | 750680.99 | 0
Existing | CZ07 | cDXGF | Pumps | 0 | 0
Existing | CZ07 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ07 | cDXGF | Humidification | 0 | 0
Existing | CZ07 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ07 | cDXGF | Water Systems | 0 | 719459.61
Existing | CZ07 | cDXGF | Refrigeration | 0 | 0
Existing | CZ07 | cDXGF | Generators | 0 | 0
Existing | CZ07 | cDXGF | Total End Uses | 2713527.07 | 1026618.25
Existing | CZ08 | cDXGF | Heating | 0 | 119811.29
Existing | CZ08 | cDXGF | Cooling | 488061.88 | 0
Existing | CZ08 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ08 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ08 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXGF | Fans | 787786.57 | 0
Existing | CZ08 | cDXGF | Pumps | 0 | 0
Existing | CZ08 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ08 | cDXGF | Humidification | 0 | 0
Existing | CZ08 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ08 | cDXGF | Water Systems | 0 | 718448.52
Existing | CZ08 | cDXGF | Refrigeration | 0 | 0
Existing | CZ08 | cDXGF | Generators | 0 | 0
Existing | CZ08 | cDXGF | Total End Uses | 2831462.22 | 1057104.67
Existing | CZ09 | cDXGF | Heating | 0 | 96608.36
Existing | CZ09 | cDXGF | Cooling | 563038.46 | 0
Existing | CZ09 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ09 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ09 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXGF | Fans | 828348.28 | 0
Existing | CZ09 | cDXGF | Pumps | 0 | 0
Existing | CZ09 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ09 | cDXGF | Humidification | 0 | 0
Existing | CZ09 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ09 | cDXGF | Water Systems | 0 | 708431.79
Existing | CZ09 | cDXGF | Refrigeration | 0 | 0
Existing | CZ09 | cDXGF | Generators | 0 | 0
Existing | CZ09 | cDXGF | Total End Uses | 2947000.51 | 1023885
Existing | CZ10 | cDXGF | Heating | 0 | 220938
Existing | CZ10 | cDXGF | Cooling | 718476.67 | 0
Existing | CZ10 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ10 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ10 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXGF | Fans | 855929.12 | 0
Existing | CZ10 | cDXGF | Pumps | 0 | 0
Existing | CZ10 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ10 | cDXGF | Humidification | 0 | 0
Existing | CZ10 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ10 | cDXGF | Water Systems | 0 | 702454.95
Existing | CZ10 | cDXGF | Refrigeration | 0 | 0
Existing | CZ10 | cDXGF | Generators | 0 | 0
Existing | CZ10 | cDXGF | Total End Uses | 3130019.56 | 1142237.8
Existing | CZ11 | cDXGF | Heating | 0 | 491859.03
Existing | CZ11 | cDXGF | Cooling | 739478.17 | 0
Existing | CZ11 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ11 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ11 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXGF | Fans | 901992.96 | 0
Existing | CZ11 | cDXGF | Pumps | 0 | 0
Existing | CZ11 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ11 | cDXGF | Humidification | 0 | 0
Existing | CZ11 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ11 | cDXGF | Water Systems | 0 | 717930.47
Existing | CZ11 | cDXGF | Refrigeration | 0 | 0
Existing | CZ11 | cDXGF | Generators | 0 | 0
Existing | CZ11 | cDXGF | Total End Uses | 3197084.9 | 1428634.35
Existing | CZ12 | cDXGF | Heating | 0 | 470012.55
Existing | CZ12 | cDXGF | Cooling | 607207.62 | 0
Existing | CZ12 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ12 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ12 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXGF | Fans | 833997.04 | 0
Existing | CZ12 | cDXGF | Pumps | 0 | 0
Existing | CZ12 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ12 | cDXGF | Humidification | 0 | 0
Existing | CZ12 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ12 | cDXGF | Water Systems | 0 | 738425.53
Existing | CZ12 | cDXGF | Refrigeration | 0 | 0
Existing | CZ12 | cDXGF | Generators | 0 | 0
Existing | CZ12 | cDXGF | Total End Uses | 2996818.42 | 1427282.93
Existing | CZ13 | cDXGF | Heating | 0 | 376041.86
Existing | CZ13 | cDXGF | Cooling | 820268.38 | 0
Existing | CZ13 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ13 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ13 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXGF | Fans | 868387.85 | 0
Existing | CZ13 | cDXGF | Pumps | 0 | 0
Existing | CZ13 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ13 | cDXGF | Humidification | 0 | 0
Existing | CZ13 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ13 | cDXGF | Water Systems | 0 | 697038.18
Existing | CZ13 | cDXGF | Refrigeration | 0 | 0
Existing | CZ13 | cDXGF | Generators | 0 | 0
Existing | CZ13 | cDXGF | Total End Uses | 3244269.99 | 1291924.89
Existing | CZ14 | cDXGF | Heating | 0 | 228915.34
Existing | CZ14 | cDXGF | Cooling | 1023978.29 | 0
Existing | CZ14 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ14 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ14 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXGF | Fans | 906124.87 | 0
Existing | CZ14 | cDXGF | Pumps | 0 | 0
Existing | CZ14 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ14 | cDXGF | Humidification | 0 | 0
Existing | CZ14 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ14 | cDXGF | Water Systems | 0 | 661472.01
Existing | CZ14 | cDXGF | Refrigeration | 0 | 0
Existing | CZ14 | cDXGF | Generators | 0 | 0
Existing | CZ14 | cDXGF | Total End Uses | 3485716.94 | 1109232.21
Existing | CZ15 | cDXGF | Heating | 0 | 80070.45
Existing | CZ15 | cDXGF | Cooling | 1434435.64 | 0
Existing | CZ15 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ15 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ15 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXGF | Fans | 860469.11 | 0
Existing | CZ15 | cDXGF | Pumps | 0 | 0
Existing | CZ15 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ15 | cDXGF | Humidification | 0 | 0
Existing | CZ15 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ15 | cDXGF | Water Systems | 0 | 587124.26
Existing | CZ15 | cDXGF | Refrigeration | 0 | 0
Existing | CZ15 | cDXGF | Generators | 0 | 0
Existing | CZ15 | cDXGF | Total End Uses | 3850518.52 | 886039.56
Existing | CZ16 | cDXGF | Heating | 0 | 640152.32
Existing | CZ16 | cDXGF | Cooling | 645607.73 | 0
Existing | CZ16 | cDXGF | Interior Lighting | 673572.97 | 0
Existing | CZ16 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXGF | Interior Equipment | 882040.8 | 218844.85
Existing | CZ16 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXGF | Fans | 950525.38 | 0
Existing | CZ16 | cDXGF | Pumps | 0 | 0
Existing | CZ16 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ16 | cDXGF | Humidification | 0 | 0
Existing | CZ16 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ16 | cDXGF | Water Systems | 0 | 780680.55
Existing | CZ16 | cDXGF | Refrigeration | 0 | 0
Existing | CZ16 | cDXGF | Generators | 0 | 0
Existing | CZ16 | cDXGF | Total End Uses | 3151746.88 | 1639677.73
New Construction | CZ01 | cDXGF | Heating | 0 | 890275.21
New Construction | CZ01 | cDXGF | Cooling | 37923.27 | 0
New Construction | CZ01 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ01 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ01 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXGF | Fans | 548553.3 | 0
New Construction | CZ01 | cDXGF | Pumps | 0 | 0
New Construction | CZ01 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXGF | Humidification | 0 | 0
New Construction | CZ01 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXGF | Water Systems | 0 | 864445.23
New Construction | CZ01 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ01 | cDXGF | Generators | 0 | 0
New Construction | CZ01 | cDXGF | Total End Uses | 1790968.03 | 1973565.3
New Construction | CZ02 | cDXGF | Heating | 0 | 677812.95
New Construction | CZ02 | cDXGF | Cooling | 240400.18 | 0
New Construction | CZ02 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ02 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ02 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXGF | Fans | 734494.48 | 0
New Construction | CZ02 | cDXGF | Pumps | 0 | 0
New Construction | CZ02 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXGF | Humidification | 0 | 0
New Construction | CZ02 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXGF | Water Systems | 0 | 793977.97
New Construction | CZ02 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ02 | cDXGF | Generators | 0 | 0
New Construction | CZ02 | cDXGF | Total End Uses | 2179386.1 | 1690635.77
New Construction | CZ03 | cDXGF | Heating | 0 | 479098.99
New Construction | CZ03 | cDXGF | Cooling | 142483.25 | 0
New Construction | CZ03 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ03 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ03 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXGF | Fans | 690414.3 | 0
New Construction | CZ03 | cDXGF | Pumps | 0 | 0
New Construction | CZ03 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXGF | Humidification | 0 | 0
New Construction | CZ03 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXGF | Water Systems | 0 | 791040.65
New Construction | CZ03 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ03 | cDXGF | Generators | 0 | 0
New Construction | CZ03 | cDXGF | Total End Uses | 2037389 | 1488984.49
New Construction | CZ04 | cDXGF | Heating | 0 | 407279.57
New Construction | CZ04 | cDXGF | Cooling | 292048.48 | 0
New Construction | CZ04 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ04 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ04 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXGF | Fans | 721856.2 | 0
New Construction | CZ04 | cDXGF | Pumps | 0 | 0
New Construction | CZ04 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXGF | Humidification | 0 | 0
New Construction | CZ04 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXGF | Water Systems | 0 | 763646.56
New Construction | CZ04 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ04 | cDXGF | Generators | 0 | 0
New Construction | CZ04 | cDXGF | Total End Uses | 2218396.14 | 1389770.98
New Construction | CZ05 | cDXGF | Heating | 0 | 439309.95
New Construction | CZ05 | cDXGF | Cooling | 181877.48 | 0
New Construction | CZ05 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ05 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ05 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXGF | Fans | 671860.83 | 0
New Construction | CZ05 | cDXGF | Pumps | 0 | 0
New Construction | CZ05 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXGF | Humidification | 0 | 0
New Construction | CZ05 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXGF | Water Systems | 0 | 791096.32
New Construction | CZ05 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ05 | cDXGF | Generators | 0 | 0
New Construction | CZ05 | cDXGF | Total End Uses | 2058229.76 | 1449251.12
New Construction | CZ06 | cDXGF | Heating | 0 | 131205.18
New Construction | CZ06 | cDXGF | Cooling | 298577.14 | 0
New Construction | CZ06 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ06 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ06 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXGF | Fans | 663917.97 | 0
New Construction | CZ06 | cDXGF | Pumps | 0 | 0
New Construction | CZ06 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXGF | Humidification | 0 | 0
New Construction | CZ06 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXGF | Water Systems | 0 | 728518.35
New Construction | CZ06 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ06 | cDXGF | Generators | 0 | 0
New Construction | CZ06 | cDXGF | Total End Uses | 2166986.56 | 1078568.38
New Construction | CZ07 | cDXGF | Heating | 0 | 118757.2
New Construction | CZ07 | cDXGF | Cooling | 328007.5 | 0
New Construction | CZ07 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ07 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ07 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXGF | Fans | 646350.87 | 0
New Construction | CZ07 | cDXGF | Pumps | 0 | 0
New Construction | CZ07 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXGF | Humidification | 0 | 0
New Construction | CZ07 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXGF | Water Systems | 0 | 719024.68
New Construction | CZ07 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ07 | cDXGF | Generators | 0 | 0
New Construction | CZ07 | cDXGF | Total End Uses | 2178849.82 | 1056626.74
New Construction | CZ08 | cDXGF | Heating | 0 | 160398.91
New Construction | CZ08 | cDXGF | Cooling | 406678.53 | 0
New Construction | CZ08 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ08 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ08 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXGF | Fans | 692177.64 | 0
New Construction | CZ08 | cDXGF | Pumps | 0 | 0
New Construction | CZ08 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXGF | Humidification | 0 | 0
New Construction | CZ08 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXGF | Water Systems | 0 | 718007.17
New Construction | CZ08 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ08 | cDXGF | Generators | 0 | 0
New Construction | CZ08 | cDXGF | Total End Uses | 2303347.63 | 1097250.94
New Construction | CZ09 | cDXGF | Heating | 0 | 122947.2
New Construction | CZ09 | cDXGF | Cooling | 465129.21 | 0
New Construction | CZ09 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ09 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ09 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXGF | Fans | 710896.82 | 0
New Construction | CZ09 | cDXGF | Pumps | 0 | 0
New Construction | CZ09 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXGF | Humidification | 0 | 0
New Construction | CZ09 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXGF | Water Systems | 0 | 708013.76
New Construction | CZ09 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ09 | cDXGF | Generators | 0 | 0
New Construction | CZ09 | cDXGF | Total End Uses | 2380517.48 | 1049805.81
New Construction | CZ10 | cDXGF | Heating | 0 | 257552.94
New Construction | CZ10 | cDXGF | Cooling | 629430.66 | 0
New Construction | CZ10 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ10 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ10 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXGF | Fans | 737132 | 0
New Construction | CZ10 | cDXGF | Pumps | 0 | 0
New Construction | CZ10 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXGF | Humidification | 0 | 0
New Construction | CZ10 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXGF | Water Systems | 0 | 702102.75
New Construction | CZ10 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ10 | cDXGF | Generators | 0 | 0
New Construction | CZ10 | cDXGF | Total End Uses | 2571054.11 | 1178500.55
New Construction | CZ11 | cDXGF | Heating | 0 | 467898.63
New Construction | CZ11 | cDXGF | Cooling | 563300.09 | 0
New Construction | CZ11 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ11 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ11 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXGF | Fans | 594912.76 | 0
New Construction | CZ11 | cDXGF | Pumps | 0 | 0
New Construction | CZ11 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXGF | Humidification | 0 | 0
New Construction | CZ11 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXGF | Water Systems | 0 | 717383.99
New Construction | CZ11 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ11 | cDXGF | Generators | 0 | 0
New Construction | CZ11 | cDXGF | Total End Uses | 2362704.31 | 1404127.46
New Construction | CZ12 | cDXGF | Heating | 0 | 470375.4
New Construction | CZ12 | cDXGF | Cooling | 466195.03 | 0
New Construction | CZ12 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ12 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ12 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXGF | Fans | 577308.39 | 0
New Construction | CZ12 | cDXGF | Pumps | 0 | 0
New Construction | CZ12 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXGF | Humidification | 0 | 0
New Construction | CZ12 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXGF | Water Systems | 0 | 737962.87
New Construction | CZ12 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ12 | cDXGF | Generators | 0 | 0
New Construction | CZ12 | cDXGF | Total End Uses | 2247994.87 | 1427183.12
New Construction | CZ13 | cDXGF | Heating | 0 | 383675.47
New Construction | CZ13 | cDXGF | Cooling | 625779.49 | 0
New Construction | CZ13 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ13 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ13 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXGF | Fans | 587785.68 | 0
New Construction | CZ13 | cDXGF | Pumps | 0 | 0
New Construction | CZ13 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXGF | Humidification | 0 | 0
New Construction | CZ13 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXGF | Water Systems | 0 | 696420.02
New Construction | CZ13 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ13 | cDXGF | Generators | 0 | 0
New Construction | CZ13 | cDXGF | Total End Uses | 2418056.62 | 1298940.34
New Construction | CZ14 | cDXGF | Heating | 0 | 234337.11
New Construction | CZ14 | cDXGF | Cooling | 803182.26 | 0
New Construction | CZ14 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ14 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ14 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXGF | Fans | 623641.71 | 0
New Construction | CZ14 | cDXGF | Pumps | 0 | 0
New Construction | CZ14 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXGF | Humidification | 0 | 0
New Construction | CZ14 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXGF | Water Systems | 0 | 660821.42
New Construction | CZ14 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ14 | cDXGF | Generators | 0 | 0
New Construction | CZ14 | cDXGF | Total End Uses | 2631315.42 | 1114003.38
New Construction | CZ15 | cDXGF | Heating | 0 | 79747.67
New Construction | CZ15 | cDXGF | Cooling | 1125929.99 | 0
New Construction | CZ15 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ15 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ15 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXGF | Fans | 593130.13 | 0
New Construction | CZ15 | cDXGF | Pumps | 0 | 0
New Construction | CZ15 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXGF | Humidification | 0 | 0
New Construction | CZ15 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXGF | Water Systems | 0 | 586584.38
New Construction | CZ15 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ15 | cDXGF | Generators | 0 | 0
New Construction | CZ15 | cDXGF | Total End Uses | 2923551.56 | 885176.9
New Construction | CZ16 | cDXGF | Heating | 0 | 628668.78
New Construction | CZ16 | cDXGF | Cooling | 508921.27 | 0
New Construction | CZ16 | cDXGF | Interior Lighting | 322450.66 | 0
New Construction | CZ16 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXGF | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ16 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXGF | Fans | 649915.94 | 0
New Construction | CZ16 | cDXGF | Pumps | 0 | 0
New Construction | CZ16 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXGF | Humidification | 0 | 0
New Construction | CZ16 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXGF | Water Systems | 0 | 780244.79
New Construction | CZ16 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ16 | cDXGF | Generators | 0 | 0
New Construction | CZ16 | cDXGF | Total End Uses | 2363328.66 | 1627758.42
Existing | CZ01 | cDXHP | Heating | 24498.76 | 715325.26
Existing | CZ01 | cDXHP | Cooling | 46831.51 | 0
Existing | CZ01 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ01 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ01 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXHP | Fans | 731890.18 | 0
Existing | CZ01 | cDXHP | Pumps | 0 | 0
Existing | CZ01 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ01 | cDXHP | Humidification | 0 | 0
Existing | CZ01 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ01 | cDXHP | Water Systems | 0 | 864677.13
Existing | CZ01 | cDXHP | Refrigeration | 0 | 0
Existing | CZ01 | cDXHP | Generators | 0 | 0
Existing | CZ01 | cDXHP | Total End Uses | 2358834.22 | 1798847.24
Existing | CZ02 | cDXHP | Heating | 18950.65 | 470281.31
Existing | CZ02 | cDXHP | Cooling | 293592.44 | 0
Existing | CZ02 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ02 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ02 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXHP | Fans | 829571.27 | 0
Existing | CZ02 | cDXHP | Pumps | 0 | 0
Existing | CZ02 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ02 | cDXHP | Humidification | 0 | 0
Existing | CZ02 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ02 | cDXHP | Water Systems | 0 | 794290.77
Existing | CZ02 | cDXHP | Refrigeration | 0 | 0
Existing | CZ02 | cDXHP | Generators | 0 | 0
Existing | CZ02 | cDXHP | Total End Uses | 2697728.13 | 1483416.93
Existing | CZ03 | cDXHP | Heating | 8722.32 | 318969.98
Existing | CZ03 | cDXHP | Cooling | 186410.86 | 0
Existing | CZ03 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ03 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ03 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXHP | Fans | 794233.51 | 0
Existing | CZ03 | cDXHP | Pumps | 0 | 0
Existing | CZ03 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ03 | cDXHP | Humidification | 0 | 0
Existing | CZ03 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ03 | cDXHP | Water Systems | 0 | 791289.31
Existing | CZ03 | cDXHP | Refrigeration | 0 | 0
Existing | CZ03 | cDXHP | Generators | 0 | 0
Existing | CZ03 | cDXHP | Total End Uses | 2544980.45 | 1329104.14
Existing | CZ04 | cDXHP | Heating | 8157.06 | 284659.77
Existing | CZ04 | cDXHP | Cooling | 355031.19 | 0
Existing | CZ04 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ04 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ04 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXHP | Fans | 827834.82 | 0
Existing | CZ04 | cDXHP | Pumps | 0 | 0
Existing | CZ04 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ04 | cDXHP | Humidification | 0 | 0
Existing | CZ04 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ04 | cDXHP | Water Systems | 0 | 763979.42
Existing | CZ04 | cDXHP | Refrigeration | 0 | 0
Existing | CZ04 | cDXHP | Generators | 0 | 0
Existing | CZ04 | cDXHP | Total End Uses | 2746636.84 | 1267484.04
Existing | CZ05 | cDXHP | Heating | 8599.03 | 301217.2
Existing | CZ05 | cDXHP | Cooling | 236465.25 | 0
Existing | CZ05 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ05 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ05 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXHP | Fans | 776965 | 0
Existing | CZ05 | cDXHP | Pumps | 0 | 0
Existing | CZ05 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ05 | cDXHP | Humidification | 0 | 0
Existing | CZ05 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ05 | cDXHP | Water Systems | 0 | 791317.67
Existing | CZ05 | cDXHP | Refrigeration | 0 | 0
Existing | CZ05 | cDXHP | Generators | 0 | 0
Existing | CZ05 | cDXHP | Total End Uses | 2577643.05 | 1311379.72
Existing | CZ06 | cDXHP | Heating | 1405.26 | 85954.62
Existing | CZ06 | cDXHP | Cooling | 371641.79 | 0
Existing | CZ06 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ06 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ06 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXHP | Fans | 759577.43 | 0
Existing | CZ06 | cDXHP | Pumps | 0 | 0
Existing | CZ06 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ06 | cDXHP | Humidification | 0 | 0
Existing | CZ06 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ06 | cDXHP | Water Systems | 0 | 728874.25
Existing | CZ06 | cDXHP | Refrigeration | 0 | 0
Existing | CZ06 | cDXHP | Generators | 0 | 0
Existing | CZ06 | cDXHP | Total End Uses | 2688238.24 | 1033673.72
Existing | CZ07 | cDXHP | Heating | 1504.18 | 82066.07
Existing | CZ07 | cDXHP | Cooling | 404240.99 | 0
Existing | CZ07 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ07 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ07 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXHP | Fans | 750679.94 | 0
Existing | CZ07 | cDXHP | Pumps | 0 | 0
Existing | CZ07 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ07 | cDXHP | Humidification | 0 | 0
Existing | CZ07 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ07 | cDXHP | Water Systems | 0 | 719459.55
Existing | CZ07 | cDXHP | Refrigeration | 0 | 0
Existing | CZ07 | cDXHP | Generators | 0 | 0
Existing | CZ07 | cDXHP | Total End Uses | 2712038.88 | 1020370.47
Existing | CZ08 | cDXHP | Heating | 2208.45 | 110796.92
Existing | CZ08 | cDXHP | Cooling | 486508.22 | 0
Existing | CZ08 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ08 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ08 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXHP | Fans | 787785.37 | 0
Existing | CZ08 | cDXHP | Pumps | 0 | 0
Existing | CZ08 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ08 | cDXHP | Humidification | 0 | 0
Existing | CZ08 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ08 | cDXHP | Water Systems | 0 | 718448.55
Existing | CZ08 | cDXHP | Refrigeration | 0 | 0
Existing | CZ08 | cDXHP | Generators | 0 | 0
Existing | CZ08 | cDXHP | Total End Uses | 2832115.81 | 1048090.32
Existing | CZ09 | cDXHP | Heating | 1547.89 | 90247.91
Existing | CZ09 | cDXHP | Cooling | 561212.3 | 0
Existing | CZ09 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ09 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ09 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXHP | Fans | 828348.35 | 0
Existing | CZ09 | cDXHP | Pumps | 0 | 0
Existing | CZ09 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ09 | cDXHP | Humidification | 0 | 0
Existing | CZ09 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ09 | cDXHP | Water Systems | 0 | 708431.8
Existing | CZ09 | cDXHP | Refrigeration | 0 | 0
Existing | CZ09 | cDXHP | Generators | 0 | 0
Existing | CZ09 | cDXHP | Total End Uses | 2946722.32 | 1017524.56
Existing | CZ10 | cDXHP | Heating | 7666.46 | 194273.33
Existing | CZ10 | cDXHP | Cooling | 718161.77 | 0
Existing | CZ10 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ10 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ10 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXHP | Fans | 855929.04 | 0
Existing | CZ10 | cDXHP | Pumps | 0 | 0
Existing | CZ10 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ10 | cDXHP | Humidification | 0 | 0
Existing | CZ10 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ10 | cDXHP | Water Systems | 0 | 702454.95
Existing | CZ10 | cDXHP | Refrigeration | 0 | 0
Existing | CZ10 | cDXHP | Generators | 0 | 0
Existing | CZ10 | cDXHP | Total End Uses | 3137371.04 | 1115573.13
Existing | CZ11 | cDXHP | Heating | 18105.69 | 426368.93
Existing | CZ11 | cDXHP | Cooling | 740169.85 | 0
Existing | CZ11 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ11 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ11 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXHP | Fans | 901973.06 | 0
Existing | CZ11 | cDXHP | Pumps | 0 | 0
Existing | CZ11 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ11 | cDXHP | Humidification | 0 | 0
Existing | CZ11 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ11 | cDXHP | Water Systems | 0 | 717931.34
Existing | CZ11 | cDXHP | Refrigeration | 0 | 0
Existing | CZ11 | cDXHP | Generators | 0 | 0
Existing | CZ11 | cDXHP | Total End Uses | 3215862.37 | 1363145.13
Existing | CZ12 | cDXHP | Heating | 16720.04 | 410647.11
Existing | CZ12 | cDXHP | Cooling | 606983.38 | 0
Existing | CZ12 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ12 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ12 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXHP | Fans | 833996.89 | 0
Existing | CZ12 | cDXHP | Pumps | 0 | 0
Existing | CZ12 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ12 | cDXHP | Humidification | 0 | 0
Existing | CZ12 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ12 | cDXHP | Water Systems | 0 | 738425.6
Existing | CZ12 | cDXHP | Refrigeration | 0 | 0
Existing | CZ12 | cDXHP | Generators | 0 | 0
Existing | CZ12 | cDXHP | Total End Uses | 3013314.08 | 1367917.57
Existing | CZ13 | cDXHP | Heating | 11986.89 | 332837.35
Existing | CZ13 | cDXHP | Cooling | 820388.12 | 0
Existing | CZ13 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ13 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ13 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXHP | Fans | 868383.63 | 0
Existing | CZ13 | cDXHP | Pumps | 0 | 0
Existing | CZ13 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ13 | cDXHP | Humidification | 0 | 0
Existing | CZ13 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ13 | cDXHP | Water Systems | 0 | 697038.18
Existing | CZ13 | cDXHP | Refrigeration | 0 | 0
Existing | CZ13 | cDXHP | Generators | 0 | 0
Existing | CZ13 | cDXHP | Total End Uses | 3256372.41 | 1248720.39
Existing | CZ14 | cDXHP | Heating | 6726.05 | 206256.27
Existing | CZ14 | cDXHP | Cooling | 1024733.88 | 0
Existing | CZ14 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ14 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ14 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXHP | Fans | 906120.08 | 0
Existing | CZ14 | cDXHP | Pumps | 0 | 0
Existing | CZ14 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ14 | cDXHP | Humidification | 0 | 0
Existing | CZ14 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ14 | cDXHP | Water Systems | 0 | 661472.32
Existing | CZ14 | cDXHP | Refrigeration | 0 | 0
Existing | CZ14 | cDXHP | Generators | 0 | 0
Existing | CZ14 | cDXHP | Total End Uses | 3493193.78 | 1086573.44
Existing | CZ15 | cDXHP | Heating | 1887.11 | 73238.93
Existing | CZ15 | cDXHP | Cooling | 1434503.51 | 0
Existing | CZ15 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ15 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ15 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXHP | Fans | 860477.41 | 0
Existing | CZ15 | cDXHP | Pumps | 0 | 0
Existing | CZ15 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ15 | cDXHP | Humidification | 0 | 0
Existing | CZ15 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ15 | cDXHP | Water Systems | 0 | 587121.45
Existing | CZ15 | cDXHP | Refrigeration | 0 | 0
Existing | CZ15 | cDXHP | Generators | 0 | 0
Existing | CZ15 | cDXHP | Total End Uses | 3852481.8 | 879205.24
Existing | CZ16 | cDXHP | Heating | 31595.03 | 551691.66
Existing | CZ16 | cDXHP | Cooling | 646985.28 | 0
Existing | CZ16 | cDXHP | Interior Lighting | 673572.97 | 0
Existing | CZ16 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXHP | Interior Equipment | 882040.8 | 218844.85
Existing | CZ16 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXHP | Fans | 950512.43 | 0
Existing | CZ16 | cDXHP | Pumps | 0 | 0
Existing | CZ16 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ16 | cDXHP | Humidification | 0 | 0
Existing | CZ16 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ16 | cDXHP | Water Systems | 0 | 780678.96
Existing | CZ16 | cDXHP | Refrigeration | 0 | 0
Existing | CZ16 | cDXHP | Generators | 0 | 0
Existing | CZ16 | cDXHP | Total End Uses | 3184706.5 | 1551215.47
New Construction | CZ01 | cDXHP | Heating | 30288.92 | 767513.17
New Construction | CZ01 | cDXHP | Cooling | 37493.71 | 0
New Construction | CZ01 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ01 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ01 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXHP | Fans | 548553.31 | 0
New Construction | CZ01 | cDXHP | Pumps | 0 | 0
New Construction | CZ01 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXHP | Humidification | 0 | 0
New Construction | CZ01 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXHP | Water Systems | 0 | 864445.23
New Construction | CZ01 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ01 | cDXHP | Generators | 0 | 0
New Construction | CZ01 | cDXHP | Total End Uses | 1820827.39 | 1850803.26
New Construction | CZ02 | cDXHP | Heating | 27695.33 | 573107.64
New Construction | CZ02 | cDXHP | Cooling | 239272.9 | 0
New Construction | CZ02 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ02 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ02 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXHP | Fans | 734509.73 | 0
New Construction | CZ02 | cDXHP | Pumps | 0 | 0
New Construction | CZ02 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXHP | Humidification | 0 | 0
New Construction | CZ02 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXHP | Water Systems | 0 | 793983.87
New Construction | CZ02 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ02 | cDXHP | Generators | 0 | 0
New Construction | CZ02 | cDXHP | Total End Uses | 2205969.42 | 1585936.36
New Construction | CZ03 | cDXHP | Heating | 15653.61 | 415091.94
New Construction | CZ03 | cDXHP | Cooling | 141930.94 | 0
New Construction | CZ03 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ03 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ03 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXHP | Fans | 690414.38 | 0
New Construction | CZ03 | cDXHP | Pumps | 0 | 0
New Construction | CZ03 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXHP | Humidification | 0 | 0
New Construction | CZ03 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXHP | Water Systems | 0 | 791040.65
New Construction | CZ03 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ03 | cDXHP | Generators | 0 | 0
New Construction | CZ03 | cDXHP | Total End Uses | 2052490.38 | 1424977.44
New Construction | CZ04 | cDXHP | Heating | 13739.54 | 351537.77
New Construction | CZ04 | cDXHP | Cooling | 291459.74 | 0
New Construction | CZ04 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ04 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ04 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXHP | Fans | 721856.03 | 0
New Construction | CZ04 | cDXHP | Pumps | 0 | 0
New Construction | CZ04 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXHP | Humidification | 0 | 0
New Construction | CZ04 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXHP | Water Systems | 0 | 763646.42
New Construction | CZ04 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ04 | cDXHP | Generators | 0 | 0
New Construction | CZ04 | cDXHP | Total End Uses | 2231546.76 | 1334029.03
New Construction | CZ05 | cDXHP | Heating | 14854.18 | 380474.25
New Construction | CZ05 | cDXHP | Cooling | 181348.36 | 0
New Construction | CZ05 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ05 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ05 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXHP | Fans | 671862.24 | 0
New Construction | CZ05 | cDXHP | Pumps | 0 | 0
New Construction | CZ05 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXHP | Humidification | 0 | 0
New Construction | CZ05 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXHP | Water Systems | 0 | 791097.24
New Construction | CZ05 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ05 | cDXHP | Generators | 0 | 0
New Construction | CZ05 | cDXHP | Total End Uses | 2072556.24 | 1390416.34
New Construction | CZ06 | cDXHP | Heating | 3100.93 | 118057.87
New Construction | CZ06 | cDXHP | Cooling | 294863.17 | 0
New Construction | CZ06 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ06 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ06 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXHP | Fans | 663917.25 | 0
New Construction | CZ06 | cDXHP | Pumps | 0 | 0
New Construction | CZ06 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXHP | Humidification | 0 | 0
New Construction | CZ06 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXHP | Water Systems | 0 | 728518.5
New Construction | CZ06 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ06 | cDXHP | Generators | 0 | 0
New Construction | CZ06 | cDXHP | Total End Uses | 2166372.8 | 1065421.23
New Construction | CZ07 | cDXHP | Heating | 2928.55 | 106369.72
New Construction | CZ07 | cDXHP | Cooling | 325288.5 | 0
New Construction | CZ07 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ07 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ07 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXHP | Fans | 646350.42 | 0
New Construction | CZ07 | cDXHP | Pumps | 0 | 0
New Construction | CZ07 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXHP | Humidification | 0 | 0
New Construction | CZ07 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXHP | Water Systems | 0 | 719024.87
New Construction | CZ07 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ07 | cDXHP | Generators | 0 | 0
New Construction | CZ07 | cDXHP | Total End Uses | 2179058.92 | 1044239.44
New Construction | CZ08 | cDXHP | Heating | 4300.26 | 142494.74
New Construction | CZ08 | cDXHP | Cooling | 405442.86 | 0
New Construction | CZ08 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ08 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ08 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXHP | Fans | 692177.55 | 0
New Construction | CZ08 | cDXHP | Pumps | 0 | 0
New Construction | CZ08 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXHP | Humidification | 0 | 0
New Construction | CZ08 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXHP | Water Systems | 0 | 718007.25
New Construction | CZ08 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ08 | cDXHP | Generators | 0 | 0
New Construction | CZ08 | cDXHP | Total End Uses | 2306412.12 | 1079346.84
New Construction | CZ09 | cDXHP | Heating | 3150.22 | 109769.56
New Construction | CZ09 | cDXHP | Cooling | 463407.09 | 0
New Construction | CZ09 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ09 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ09 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXHP | Fans | 710896.52 | 0
New Construction | CZ09 | cDXHP | Pumps | 0 | 0
New Construction | CZ09 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXHP | Humidification | 0 | 0
New Construction | CZ09 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXHP | Water Systems | 0 | 708013.76
New Construction | CZ09 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ09 | cDXHP | Generators | 0 | 0
New Construction | CZ09 | cDXHP | Total End Uses | 2381945.28 | 1036628.16
New Construction | CZ10 | cDXHP | Heating | 10597.83 | 218322.78
New Construction | CZ10 | cDXHP | Cooling | 629232.07 | 0
New Construction | CZ10 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ10 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ10 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXHP | Fans | 737129.86 | 0
New Construction | CZ10 | cDXHP | Pumps | 0 | 0
New Construction | CZ10 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXHP | Humidification | 0 | 0
New Construction | CZ10 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXHP | Water Systems | 0 | 702102.54
New Construction | CZ10 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ10 | cDXHP | Generators | 0 | 0
New Construction | CZ10 | cDXHP | Total End Uses | 2581451.22 | 1139270.18
New Construction | CZ11 | cDXHP | Heating | 18619.06 | 398860.06
New Construction | CZ11 | cDXHP | Cooling | 563976.42 | 0
New Construction | CZ11 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ11 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ11 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXHP | Fans | 594871.53 | 0
New Construction | CZ11 | cDXHP | Pumps | 0 | 0
New Construction | CZ11 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXHP | Humidification | 0 | 0
New Construction | CZ11 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXHP | Water Systems | 0 | 717381.94
New Construction | CZ11 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ11 | cDXHP | Generators | 0 | 0
New Construction | CZ11 | cDXHP | Total End Uses | 2381958.46 | 1335086.85
New Construction | CZ12 | cDXHP | Heating | 18412.26 | 402352.63
New Construction | CZ12 | cDXHP | Cooling | 466228.18 | 0
New Construction | CZ12 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ12 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ12 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXHP | Fans | 577300.42 | 0
New Construction | CZ12 | cDXHP | Pumps | 0 | 0
New Construction | CZ12 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXHP | Humidification | 0 | 0
New Construction | CZ12 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXHP | Water Systems | 0 | 737899.43
New Construction | CZ12 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ12 | cDXHP | Generators | 0 | 0
New Construction | CZ12 | cDXHP | Total End Uses | 2266432.32 | 1359096.91
New Construction | CZ13 | cDXHP | Heating | 13849.93 | 331823.4
New Construction | CZ13 | cDXHP | Cooling | 625879.88 | 0
New Construction | CZ13 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ13 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ13 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXHP | Fans | 587780.55 | 0
New Construction | CZ13 | cDXHP | Pumps | 0 | 0
New Construction | CZ13 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXHP | Humidification | 0 | 0
New Construction | CZ13 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXHP | Water Systems | 0 | 696420.61
New Construction | CZ13 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ13 | cDXHP | Generators | 0 | 0
New Construction | CZ13 | cDXHP | Total End Uses | 2432001.82 | 1247088.86
New Construction | CZ14 | cDXHP | Heating | 7999.98 | 206099.41
New Construction | CZ14 | cDXHP | Cooling | 803772.88 | 0
New Construction | CZ14 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ14 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ14 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXHP | Fans | 623606.1 | 0
New Construction | CZ14 | cDXHP | Pumps | 0 | 0
New Construction | CZ14 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXHP | Humidification | 0 | 0
New Construction | CZ14 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXHP | Water Systems | 0 | 660821.12
New Construction | CZ14 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ14 | cDXHP | Generators | 0 | 0
New Construction | CZ14 | cDXHP | Total End Uses | 2639870.42 | 1085765.39
New Construction | CZ15 | cDXHP | Heating | 2626.34 | 69868.15
New Construction | CZ15 | cDXHP | Cooling | 1126194.06 | 0
New Construction | CZ15 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ15 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ15 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXHP | Fans | 593111.5 | 0
New Construction | CZ15 | cDXHP | Pumps | 0 | 0
New Construction | CZ15 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXHP | Humidification | 0 | 0
New Construction | CZ15 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXHP | Water Systems | 0 | 586508.51
New Construction | CZ15 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ15 | cDXHP | Generators | 0 | 0
New Construction | CZ15 | cDXHP | Total End Uses | 2926423.36 | 875221.52
New Construction | CZ16 | cDXHP | Heating | 33118.92 | 530575.32
New Construction | CZ16 | cDXHP | Cooling | 510394.41 | 0
New Construction | CZ16 | cDXHP | Interior Lighting | 322450.66 | 0
New Construction | CZ16 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXHP | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ16 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXHP | Fans | 649908.4 | 0
New Construction | CZ16 | cDXHP | Pumps | 0 | 0
New Construction | CZ16 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXHP | Humidification | 0 | 0
New Construction | CZ16 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXHP | Water Systems | 0 | 780212.93
New Construction | CZ16 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ16 | cDXHP | Generators | 0 | 0
New Construction | CZ16 | cDXHP | Total End Uses | 2397913.18 | 1529633.11
Existing | CZ01 | cDXOH | Heating | 0 | 719534.6
Existing | CZ01 | cDXOH | Cooling | 46500.35 | 0
Existing | CZ01 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ01 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ01 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXOH | Fans | 732189.91 | 0
Existing | CZ01 | cDXOH | Pumps | 0 | 0
Existing | CZ01 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ01 | cDXOH | Humidification | 0 | 0
Existing | CZ01 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ01 | cDXOH | Water Systems | 0 | 864653.99
Existing | CZ01 | cDXOH | Refrigeration | 0 | 0
Existing | CZ01 | cDXOH | Generators | 0 | 0
Existing | CZ01 | cDXOH | Total End Uses | 2334304.03 | 1803033.44
Existing | CZ02 | cDXOH | Heating | 0 | 472603.69
Existing | CZ02 | cDXOH | Cooling | 294155.86 | 0
Existing | CZ02 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ02 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ02 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXOH | Fans | 829872.52 | 0
Existing | CZ02 | cDXOH | Pumps | 0 | 0
Existing | CZ02 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ02 | cDXOH | Humidification | 0 | 0
Existing | CZ02 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ02 | cDXOH | Water Systems | 0 | 794289.89
Existing | CZ02 | cDXOH | Refrigeration | 0 | 0
Existing | CZ02 | cDXOH | Generators | 0 | 0
Existing | CZ02 | cDXOH | Total End Uses | 2679642.15 | 1485738.43
Existing | CZ03 | cDXOH | Heating | 0 | 319873.18
Existing | CZ03 | cDXOH | Cooling | 186874.45 | 0
Existing | CZ03 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ03 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ03 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXOH | Fans | 794366.82 | 0
Existing | CZ03 | cDXOH | Pumps | 0 | 0
Existing | CZ03 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ03 | cDXOH | Humidification | 0 | 0
Existing | CZ03 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ03 | cDXOH | Water Systems | 0 | 791294.67
Existing | CZ03 | cDXOH | Refrigeration | 0 | 0
Existing | CZ03 | cDXOH | Generators | 0 | 0
Existing | CZ03 | cDXOH | Total End Uses | 2536855.05 | 1330012.7
Existing | CZ04 | cDXOH | Heating | 0 | 285506.15
Existing | CZ04 | cDXOH | Cooling | 355409.49 | 0
Existing | CZ04 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ04 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ04 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXOH | Fans | 827998.78 | 0
Existing | CZ04 | cDXOH | Pumps | 0 | 0
Existing | CZ04 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ04 | cDXOH | Humidification | 0 | 0
Existing | CZ04 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ04 | cDXOH | Water Systems | 0 | 763951.38
Existing | CZ04 | cDXOH | Refrigeration | 0 | 0
Existing | CZ04 | cDXOH | Generators | 0 | 0
Existing | CZ04 | cDXOH | Total End Uses | 2739022.05 | 1268302.38
Existing | CZ05 | cDXOH | Heating | 0 | 301857.61
Existing | CZ05 | cDXOH | Cooling | 236642.81 | 0
Existing | CZ05 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ05 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ05 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXOH | Fans | 777003.45 | 0
Existing | CZ05 | cDXOH | Pumps | 0 | 0
Existing | CZ05 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ05 | cDXOH | Humidification | 0 | 0
Existing | CZ05 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ05 | cDXOH | Water Systems | 0 | 791310.89
Existing | CZ05 | cDXOH | Refrigeration | 0 | 0
Existing | CZ05 | cDXOH | Generators | 0 | 0
Existing | CZ05 | cDXOH | Total End Uses | 2569260.03 | 1312013.35
Existing | CZ06 | cDXOH | Heating | 0 | 86021.45
Existing | CZ06 | cDXOH | Cooling | 375619.19 | 0
Existing | CZ06 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ06 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ06 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXOH | Fans | 759616.82 | 0
Existing | CZ06 | cDXOH | Pumps | 0 | 0
Existing | CZ06 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ06 | cDXOH | Humidification | 0 | 0
Existing | CZ06 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ06 | cDXOH | Water Systems | 0 | 728867.74
Existing | CZ06 | cDXOH | Refrigeration | 0 | 0
Existing | CZ06 | cDXOH | Generators | 0 | 0
Existing | CZ06 | cDXOH | Total End Uses | 2690849.78 | 1033734.05
Existing | CZ07 | cDXOH | Heating | 0 | 82137.52
Existing | CZ07 | cDXOH | Cooling | 407130.91 | 0
Existing | CZ07 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ07 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ07 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXOH | Fans | 750685.94 | 0
Existing | CZ07 | cDXOH | Pumps | 0 | 0
Existing | CZ07 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ07 | cDXOH | Humidification | 0 | 0
Existing | CZ07 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ07 | cDXOH | Water Systems | 0 | 719492.53
Existing | CZ07 | cDXOH | Refrigeration | 0 | 0
Existing | CZ07 | cDXOH | Generators | 0 | 0
Existing | CZ07 | cDXOH | Total End Uses | 2713430.62 | 1020474.9
Existing | CZ08 | cDXOH | Heating | 0 | 110880.81
Existing | CZ08 | cDXOH | Cooling | 487895.15 | 0
Existing | CZ08 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ08 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ08 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXOH | Fans | 787784.55 | 0
Existing | CZ08 | cDXOH | Pumps | 0 | 0
Existing | CZ08 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ08 | cDXOH | Humidification | 0 | 0
Existing | CZ08 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ08 | cDXOH | Water Systems | 0 | 718448.6
Existing | CZ08 | cDXOH | Refrigeration | 0 | 0
Existing | CZ08 | cDXOH | Generators | 0 | 0
Existing | CZ08 | cDXOH | Total End Uses | 2831293.47 | 1048174.26
Existing | CZ09 | cDXOH | Heating | 0 | 90337.69
Existing | CZ09 | cDXOH | Cooling | 562916.09 | 0
Existing | CZ09 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ09 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ09 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXOH | Fans | 828344.07 | 0
Existing | CZ09 | cDXOH | Pumps | 0 | 0
Existing | CZ09 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ09 | cDXOH | Humidification | 0 | 0
Existing | CZ09 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ09 | cDXOH | Water Systems | 0 | 708431.84
Existing | CZ09 | cDXOH | Refrigeration | 0 | 0
Existing | CZ09 | cDXOH | Generators | 0 | 0
Existing | CZ09 | cDXOH | Total End Uses | 2946873.93 | 1017614.38
Existing | CZ10 | cDXOH | Heating | 0 | 194877.82
Existing | CZ10 | cDXOH | Cooling | 717941.31 | 0
Existing | CZ10 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ10 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ10 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXOH | Fans | 855984.11 | 0
Existing | CZ10 | cDXOH | Pumps | 0 | 0
Existing | CZ10 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ10 | cDXOH | Humidification | 0 | 0
Existing | CZ10 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ10 | cDXOH | Water Systems | 0 | 702459.89
Existing | CZ10 | cDXOH | Refrigeration | 0 | 0
Existing | CZ10 | cDXOH | Generators | 0 | 0
Existing | CZ10 | cDXOH | Total End Uses | 3129539.19 | 1116182.57
Existing | CZ11 | cDXOH | Heating | 0 | 429109.17
Existing | CZ11 | cDXOH | Cooling | 738792.92 | 0
Existing | CZ11 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ11 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ11 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXOH | Fans | 902711.75 | 0
Existing | CZ11 | cDXOH | Pumps | 0 | 0
Existing | CZ11 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ11 | cDXOH | Humidification | 0 | 0
Existing | CZ11 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ11 | cDXOH | Water Systems | 0 | 717955.57
Existing | CZ11 | cDXOH | Refrigeration | 0 | 0
Existing | CZ11 | cDXOH | Generators | 0 | 0
Existing | CZ11 | cDXOH | Total End Uses | 3197118.44 | 1365909.59
Existing | CZ12 | cDXOH | Heating | 0 | 413132.97
Existing | CZ12 | cDXOH | Cooling | 606547.5 | 0
Existing | CZ12 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ12 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ12 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXOH | Fans | 834535.96 | 0
Existing | CZ12 | cDXOH | Pumps | 0 | 0
Existing | CZ12 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ12 | cDXOH | Humidification | 0 | 0
Existing | CZ12 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ12 | cDXOH | Water Systems | 0 | 738430.28
Existing | CZ12 | cDXOH | Refrigeration | 0 | 0
Existing | CZ12 | cDXOH | Generators | 0 | 0
Existing | CZ12 | cDXOH | Total End Uses | 2996697.22 | 1370408.1
Existing | CZ13 | cDXOH | Heating | 0 | 334719.17
Existing | CZ13 | cDXOH | Cooling | 819849.39 | 0
Existing | CZ13 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ13 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ13 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXOH | Fans | 868651.87 | 0
Existing | CZ13 | cDXOH | Pumps | 0 | 0
Existing | CZ13 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ13 | cDXOH | Humidification | 0 | 0
Existing | CZ13 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ13 | cDXOH | Water Systems | 0 | 697041.84
Existing | CZ13 | cDXOH | Refrigeration | 0 | 0
Existing | CZ13 | cDXOH | Generators | 0 | 0
Existing | CZ13 | cDXOH | Total End Uses | 3244115.04 | 1250605.86
Existing | CZ14 | cDXOH | Heating | 0 | 206883.1
Existing | CZ14 | cDXOH | Cooling | 1023584 | 0
Existing | CZ14 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ14 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ14 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXOH | Fans | 906245.49 | 0
Existing | CZ14 | cDXOH | Pumps | 0 | 0
Existing | CZ14 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ14 | cDXOH | Humidification | 0 | 0
Existing | CZ14 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ14 | cDXOH | Water Systems | 0 | 661475.89
Existing | CZ14 | cDXOH | Refrigeration | 0 | 0
Existing | CZ14 | cDXOH | Generators | 0 | 0
Existing | CZ14 | cDXOH | Total End Uses | 3485443.26 | 1087203.84
Existing | CZ15 | cDXOH | Heating | 0 | 73352.72
Existing | CZ15 | cDXOH | Cooling | 1434208.16 | 0
Existing | CZ15 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ15 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ15 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXOH | Fans | 860490.72 | 0
Existing | CZ15 | cDXOH | Pumps | 0 | 0
Existing | CZ15 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ15 | cDXOH | Humidification | 0 | 0
Existing | CZ15 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ15 | cDXOH | Water Systems | 0 | 587126
Existing | CZ15 | cDXOH | Refrigeration | 0 | 0
Existing | CZ15 | cDXOH | Generators | 0 | 0
Existing | CZ15 | cDXOH | Total End Uses | 3850312.65 | 879323.57
Existing | CZ16 | cDXOH | Heating | 0 | 555364.61
Existing | CZ16 | cDXOH | Cooling | 644204.53 | 0
Existing | CZ16 | cDXOH | Interior Lighting | 673572.97 | 0
Existing | CZ16 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXOH | Interior Equipment | 882040.8 | 218844.85
Existing | CZ16 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXOH | Fans | 952956.76 | 0
Existing | CZ16 | cDXOH | Pumps | 0 | 0
Existing | CZ16 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ16 | cDXOH | Humidification | 0 | 0
Existing | CZ16 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ16 | cDXOH | Water Systems | 0 | 780687.63
Existing | CZ16 | cDXOH | Refrigeration | 0 | 0
Existing | CZ16 | cDXOH | Generators | 0 | 0
Existing | CZ16 | cDXOH | Total End Uses | 3152775.06 | 1554897.09
New Construction | CZ01 | cDXOH | Heating | 0 | 776906.54
New Construction | CZ01 | cDXOH | Cooling | 36322.47 | 0
New Construction | CZ01 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ01 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ01 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXOH | Fans | 548781.6 | 0
New Construction | CZ01 | cDXOH | Pumps | 0 | 0
New Construction | CZ01 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXOH | Humidification | 0 | 0
New Construction | CZ01 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXOH | Water Systems | 0 | 864514.48
New Construction | CZ01 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ01 | cDXOH | Generators | 0 | 0
New Construction | CZ01 | cDXOH | Total End Uses | 1789595.52 | 1860265.88
New Construction | CZ02 | cDXOH | Heating | 0 | 577997.83
New Construction | CZ02 | cDXOH | Cooling | 238748.32 | 0
New Construction | CZ02 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ02 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ02 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXOH | Fans | 735203.19 | 0
New Construction | CZ02 | cDXOH | Pumps | 0 | 0
New Construction | CZ02 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXOH | Humidification | 0 | 0
New Construction | CZ02 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXOH | Water Systems | 0 | 794018.72
New Construction | CZ02 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ02 | cDXOH | Generators | 0 | 0
New Construction | CZ02 | cDXOH | Total End Uses | 2178442.97 | 1590861.39
New Construction | CZ03 | cDXOH | Heating | 0 | 417879
New Construction | CZ03 | cDXOH | Cooling | 141616.88 | 0
New Construction | CZ03 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ03 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ03 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXOH | Fans | 690493.53 | 0
New Construction | CZ03 | cDXOH | Pumps | 0 | 0
New Construction | CZ03 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXOH | Humidification | 0 | 0
New Construction | CZ03 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXOH | Water Systems | 0 | 791020.37
New Construction | CZ03 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ03 | cDXOH | Generators | 0 | 0
New Construction | CZ03 | cDXOH | Total End Uses | 2036601.86 | 1427744.23
New Construction | CZ04 | cDXOH | Heating | 0 | 353611.77
New Construction | CZ04 | cDXOH | Cooling | 291096.24 | 0
New Construction | CZ04 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ04 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ04 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXOH | Fans | 722080.6 | 0
New Construction | CZ04 | cDXOH | Pumps | 0 | 0
New Construction | CZ04 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXOH | Humidification | 0 | 0
New Construction | CZ04 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXOH | Water Systems | 0 | 763625.94
New Construction | CZ04 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ04 | cDXOH | Generators | 0 | 0
New Construction | CZ04 | cDXOH | Total End Uses | 2217668.29 | 1336082.56
New Construction | CZ05 | cDXOH | Heating | 0 | 382591.08
New Construction | CZ05 | cDXOH | Cooling | 180452 | 0
New Construction | CZ05 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ05 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ05 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXOH | Fans | 671996.64 | 0
New Construction | CZ05 | cDXOH | Pumps | 0 | 0
New Construction | CZ05 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXOH | Humidification | 0 | 0
New Construction | CZ05 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXOH | Water Systems | 0 | 791092.71
New Construction | CZ05 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ05 | cDXOH | Generators | 0 | 0
New Construction | CZ05 | cDXOH | Total End Uses | 2056940.09 | 1392528.64
New Construction | CZ06 | cDXOH | Heating | 0 | 118502.94
New Construction | CZ06 | cDXOH | Cooling | 298268.47 | 0
New Construction | CZ06 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ06 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ06 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXOH | Fans | 663957.93 | 0
New Construction | CZ06 | cDXOH | Pumps | 0 | 0
New Construction | CZ06 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXOH | Humidification | 0 | 0
New Construction | CZ06 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXOH | Water Systems | 0 | 728562.14
New Construction | CZ06 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ06 | cDXOH | Generators | 0 | 0
New Construction | CZ06 | cDXOH | Total End Uses | 2166717.85 | 1065909.94
New Construction | CZ07 | cDXOH | Heating | 0 | 106816.25
New Construction | CZ07 | cDXOH | Cooling | 327704.69 | 0
New Construction | CZ07 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ07 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ07 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXOH | Fans | 646420.21 | 0
New Construction | CZ07 | cDXOH | Pumps | 0 | 0
New Construction | CZ07 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXOH | Humidification | 0 | 0
New Construction | CZ07 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXOH | Water Systems | 0 | 718980.24
New Construction | CZ07 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ07 | cDXOH | Generators | 0 | 0
New Construction | CZ07 | cDXOH | Total End Uses | 2178616.35 | 1044641.34
New Construction | CZ08 | cDXOH | Heating | 0 | 143032.74
New Construction | CZ08 | cDXOH | Cooling | 406184.48 | 0
New Construction | CZ08 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ08 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ08 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXOH | Fans | 692254.53 | 0
New Construction | CZ08 | cDXOH | Pumps | 0 | 0
New Construction | CZ08 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXOH | Humidification | 0 | 0
New Construction | CZ08 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXOH | Water Systems | 0 | 718097.22
New Construction | CZ08 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ08 | cDXOH | Generators | 0 | 0
New Construction | CZ08 | cDXOH | Total End Uses | 2302930.47 | 1079974.81
New Construction | CZ09 | cDXOH | Heating | 0 | 110091.5
New Construction | CZ09 | cDXOH | Cooling | 464721.97 | 0
New Construction | CZ09 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ09 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ09 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXOH | Fans | 710967.81 | 0
New Construction | CZ09 | cDXOH | Pumps | 0 | 0
New Construction | CZ09 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXOH | Humidification | 0 | 0
New Construction | CZ09 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXOH | Water Systems | 0 | 708051.69
New Construction | CZ09 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ09 | cDXOH | Generators | 0 | 0
New Construction | CZ09 | cDXOH | Total End Uses | 2380181.23 | 1036988.05
New Construction | CZ10 | cDXOH | Heating | 0 | 219418.96
New Construction | CZ10 | cDXOH | Cooling | 628362.78 | 0
New Construction | CZ10 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ10 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ10 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXOH | Fans | 737303.77 | 0
New Construction | CZ10 | cDXOH | Pumps | 0 | 0
New Construction | CZ10 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXOH | Humidification | 0 | 0
New Construction | CZ10 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXOH | Water Systems | 0 | 702003.87
New Construction | CZ10 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ10 | cDXOH | Generators | 0 | 0
New Construction | CZ10 | cDXOH | Total End Uses | 2570158 | 1140267.68
New Construction | CZ11 | cDXOH | Heating | 0 | 403805.57
New Construction | CZ11 | cDXOH | Cooling | 561840.87 | 0
New Construction | CZ11 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ11 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ11 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXOH | Fans | 595009.29 | 0
New Construction | CZ11 | cDXOH | Pumps | 0 | 0
New Construction | CZ11 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXOH | Humidification | 0 | 0
New Construction | CZ11 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXOH | Water Systems | 0 | 717449.49
New Construction | CZ11 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ11 | cDXOH | Generators | 0 | 0
New Construction | CZ11 | cDXOH | Total End Uses | 2361341.61 | 1340099.91
New Construction | CZ12 | cDXOH | Heating | 0 | 406916.35
New Construction | CZ12 | cDXOH | Cooling | 464686.75 | 0
New Construction | CZ12 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ12 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ12 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXOH | Fans | 577413.4 | 0
New Construction | CZ12 | cDXOH | Pumps | 0 | 0
New Construction | CZ12 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXOH | Humidification | 0 | 0
New Construction | CZ12 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXOH | Water Systems | 0 | 738083.93
New Construction | CZ12 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ12 | cDXOH | Generators | 0 | 0
New Construction | CZ12 | cDXOH | Total End Uses | 2246591.59 | 1363845.14
New Construction | CZ13 | cDXOH | Heating | 0 | 335705.73
New Construction | CZ13 | cDXOH | Cooling | 624674.37 | 0
New Construction | CZ13 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ13 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ13 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXOH | Fans | 587756.19 | 0
New Construction | CZ13 | cDXOH | Pumps | 0 | 0
New Construction | CZ13 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXOH | Humidification | 0 | 0
New Construction | CZ13 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXOH | Water Systems | 0 | 696527.32
New Construction | CZ13 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ13 | cDXOH | Generators | 0 | 0
New Construction | CZ13 | cDXOH | Total End Uses | 2416922.01 | 1251077.91
New Construction | CZ14 | cDXOH | Heating | 0 | 207614.55
New Construction | CZ14 | cDXOH | Cooling | 802135.63 | 0
New Construction | CZ14 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ14 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ14 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXOH | Fans | 623807.45 | 0
New Construction | CZ14 | cDXOH | Pumps | 0 | 0
New Construction | CZ14 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXOH | Humidification | 0 | 0
New Construction | CZ14 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXOH | Water Systems | 0 | 660871.8
New Construction | CZ14 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ14 | cDXOH | Generators | 0 | 0
New Construction | CZ14 | cDXOH | Total End Uses | 2630434.53 | 1087331.2
New Construction | CZ15 | cDXOH | Heating | 0 | 70123.05
New Construction | CZ15 | cDXOH | Cooling | 1125090.15 | 0
New Construction | CZ15 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ15 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ15 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXOH | Fans | 593160.08 | 0
New Construction | CZ15 | cDXOH | Pumps | 0 | 0
New Construction | CZ15 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXOH | Humidification | 0 | 0
New Construction | CZ15 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXOH | Water Systems | 0 | 586553.17
New Construction | CZ15 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ15 | cDXOH | Generators | 0 | 0
New Construction | CZ15 | cDXOH | Total End Uses | 2922741.68 | 875521.07
New Construction | CZ16 | cDXOH | Heating | 0 | 537230.01
New Construction | CZ16 | cDXOH | Cooling | 506150.34 | 0
New Construction | CZ16 | cDXOH | Interior Lighting | 322450.66 | 0
New Construction | CZ16 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXOH | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ16 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXOH | Fans | 651233.9 | 0
New Construction | CZ16 | cDXOH | Pumps | 0 | 0
New Construction | CZ16 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXOH | Humidification | 0 | 0
New Construction | CZ16 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXOH | Water Systems | 0 | 780244.29
New Construction | CZ16 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ16 | cDXOH | Generators | 0 | 0
New Construction | CZ16 | cDXOH | Total End Uses | 2361875.68 | 1536319.16
Existing | CZ01 | cPVVG | Heating | 0 | 875550.55
Existing | CZ01 | cPVVG | Cooling | 48744.82 | 0
Existing | CZ01 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ01 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ01 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ01 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ01 | cPVVG | Fans | 584059.61 | 0
Existing | CZ01 | cPVVG | Pumps | 0 | 0
Existing | CZ01 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ01 | cPVVG | Humidification | 0 | 0
Existing | CZ01 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ01 | cPVVG | Water Systems | 0 | 864663.07
Existing | CZ01 | cPVVG | Refrigeration | 0 | 0
Existing | CZ01 | cPVVG | Generators | 0 | 0
Existing | CZ01 | cPVVG | Total End Uses | 2188418.2 | 1959058.47
Existing | CZ02 | cPVVG | Heating | 0 | 577520.7
Existing | CZ02 | cPVVG | Cooling | 291475.74 | 0
Existing | CZ02 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ02 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ02 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ02 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ02 | cPVVG | Fans | 670208.63 | 0
Existing | CZ02 | cPVVG | Pumps | 0 | 0
Existing | CZ02 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ02 | cPVVG | Humidification | 0 | 0
Existing | CZ02 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ02 | cPVVG | Water Systems | 0 | 794287.47
Existing | CZ02 | cPVVG | Refrigeration | 0 | 0
Existing | CZ02 | cPVVG | Generators | 0 | 0
Existing | CZ02 | cPVVG | Total End Uses | 2517298.14 | 1590653.02
Existing | CZ03 | cPVVG | Heating | 0 | 380739.66
Existing | CZ03 | cPVVG | Cooling | 190186.32 | 0
Existing | CZ03 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ03 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ03 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ03 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ03 | cPVVG | Fans | 636686 | 0
Existing | CZ03 | cPVVG | Pumps | 0 | 0
Existing | CZ03 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ03 | cPVVG | Humidification | 0 | 0
Existing | CZ03 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ03 | cPVVG | Water Systems | 0 | 791295.43
Existing | CZ03 | cPVVG | Refrigeration | 0 | 0
Existing | CZ03 | cPVVG | Generators | 0 | 0
Existing | CZ03 | cPVVG | Total End Uses | 2382486.09 | 1390879.94
Existing | CZ04 | cPVVG | Heating | 0 | 342343.26
Existing | CZ04 | cPVVG | Cooling | 351900.24 | 0
Existing | CZ04 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ04 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ04 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ04 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ04 | cPVVG | Fans | 667738.13 | 0
Existing | CZ04 | cPVVG | Pumps | 0 | 0
Existing | CZ04 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ04 | cPVVG | Humidification | 0 | 0
Existing | CZ04 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ04 | cPVVG | Water Systems | 0 | 763968.52
Existing | CZ04 | cPVVG | Refrigeration | 0 | 0
Existing | CZ04 | cPVVG | Generators | 0 | 0
Existing | CZ04 | cPVVG | Total End Uses | 2575252.14 | 1325156.63
Existing | CZ05 | cPVVG | Heating | 0 | 356318.72
Existing | CZ05 | cPVVG | Cooling | 238398.69 | 0
Existing | CZ05 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ05 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ05 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ05 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ05 | cPVVG | Fans | 626087.3 | 0
Existing | CZ05 | cPVVG | Pumps | 0 | 0
Existing | CZ05 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ05 | cPVVG | Humidification | 0 | 0
Existing | CZ05 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ05 | cPVVG | Water Systems | 0 | 791326.98
Existing | CZ05 | cPVVG | Refrigeration | 0 | 0
Existing | CZ05 | cPVVG | Generators | 0 | 0
Existing | CZ05 | cPVVG | Total End Uses | 2420099.76 | 1366490.56
Existing | CZ06 | cPVVG | Heating | 0 | 98980.8
Existing | CZ06 | cPVVG | Cooling | 376690.45 | 0
Existing | CZ06 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ06 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ06 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ06 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ06 | cPVVG | Fans | 613346.57 | 0
Existing | CZ06 | cPVVG | Pumps | 0 | 0
Existing | CZ06 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ06 | cPVVG | Humidification | 0 | 0
Existing | CZ06 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ06 | cPVVG | Water Systems | 0 | 728886.42
Existing | CZ06 | cPVVG | Refrigeration | 0 | 0
Existing | CZ06 | cPVVG | Generators | 0 | 0
Existing | CZ06 | cPVVG | Total End Uses | 2545650.79 | 1046712.07
Existing | CZ07 | cPVVG | Heating | 0 | 95204.27
Existing | CZ07 | cPVVG | Cooling | 402786.55 | 0
Existing | CZ07 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ07 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ07 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ07 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ07 | cPVVG | Fans | 606411.36 | 0
Existing | CZ07 | cPVVG | Pumps | 0 | 0
Existing | CZ07 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ07 | cPVVG | Humidification | 0 | 0
Existing | CZ07 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ07 | cPVVG | Water Systems | 0 | 719497.26
Existing | CZ07 | cPVVG | Refrigeration | 0 | 0
Existing | CZ07 | cPVVG | Generators | 0 | 0
Existing | CZ07 | cPVVG | Total End Uses | 2564811.69 | 1033546.39
Existing | CZ08 | cPVVG | Heating | 0 | 129001.05
Existing | CZ08 | cPVVG | Cooling | 482401.99 | 0
Existing | CZ08 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ08 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ08 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ08 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ08 | cPVVG | Fans | 634501.63 | 0
Existing | CZ08 | cPVVG | Pumps | 0 | 0
Existing | CZ08 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ08 | cPVVG | Humidification | 0 | 0
Existing | CZ08 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ08 | cPVVG | Water Systems | 0 | 718446.68
Existing | CZ08 | cPVVG | Refrigeration | 0 | 0
Existing | CZ08 | cPVVG | Generators | 0 | 0
Existing | CZ08 | cPVVG | Total End Uses | 2672517.39 | 1066292.58
Existing | CZ09 | cPVVG | Heating | 0 | 104353.58
Existing | CZ09 | cPVVG | Cooling | 553619.19 | 0
Existing | CZ09 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ09 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ09 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ09 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ09 | cPVVG | Fans | 668162.55 | 0
Existing | CZ09 | cPVVG | Pumps | 0 | 0
Existing | CZ09 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ09 | cPVVG | Humidification | 0 | 0
Existing | CZ09 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ09 | cPVVG | Water Systems | 0 | 708442.39
Existing | CZ09 | cPVVG | Refrigeration | 0 | 0
Existing | CZ09 | cPVVG | Generators | 0 | 0
Existing | CZ09 | cPVVG | Total End Uses | 2777395.52 | 1031640.83
Existing | CZ10 | cPVVG | Heating | 0 | 239480.7
Existing | CZ10 | cPVVG | Cooling | 705916.33 | 0
Existing | CZ10 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ10 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ10 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ10 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ10 | cPVVG | Fans | 697307.09 | 0
Existing | CZ10 | cPVVG | Pumps | 0 | 0
Existing | CZ10 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ10 | cPVVG | Humidification | 0 | 0
Existing | CZ10 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ10 | cPVVG | Water Systems | 0 | 702467.74
Existing | CZ10 | cPVVG | Refrigeration | 0 | 0
Existing | CZ10 | cPVVG | Generators | 0 | 0
Existing | CZ10 | cPVVG | Total End Uses | 2958837.18 | 1160793.28
Existing | CZ11 | cPVVG | Heating | 0 | 533728.22
Existing | CZ11 | cPVVG | Cooling | 725756.4 | 0
Existing | CZ11 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ11 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ11 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ11 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ11 | cPVVG | Fans | 734045.43 | 0
Existing | CZ11 | cPVVG | Pumps | 0 | 0
Existing | CZ11 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ11 | cPVVG | Humidification | 0 | 0
Existing | CZ11 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ11 | cPVVG | Water Systems | 0 | 717948.62
Existing | CZ11 | cPVVG | Refrigeration | 0 | 0
Existing | CZ11 | cPVVG | Generators | 0 | 0
Existing | CZ11 | cPVVG | Total End Uses | 3015415.6 | 1470521.69
Existing | CZ12 | cPVVG | Heating | 0 | 505568.32
Existing | CZ12 | cPVVG | Cooling | 597667.68 | 0
Existing | CZ12 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ12 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ12 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ12 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ12 | cPVVG | Fans | 679697.56 | 0
Existing | CZ12 | cPVVG | Pumps | 0 | 0
Existing | CZ12 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ12 | cPVVG | Humidification | 0 | 0
Existing | CZ12 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ12 | cPVVG | Water Systems | 0 | 738419.83
Existing | CZ12 | cPVVG | Refrigeration | 0 | 0
Existing | CZ12 | cPVVG | Generators | 0 | 0
Existing | CZ12 | cPVVG | Total End Uses | 2832979.01 | 1462833
Existing | CZ13 | cPVVG | Heating | 0 | 405823.29
Existing | CZ13 | cPVVG | Cooling | 805964.78 | 0
Existing | CZ13 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ13 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ13 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ13 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ13 | cPVVG | Fans | 706043.52 | 0
Existing | CZ13 | cPVVG | Pumps | 0 | 0
Existing | CZ13 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ13 | cPVVG | Humidification | 0 | 0
Existing | CZ13 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ13 | cPVVG | Water Systems | 0 | 696999.02
Existing | CZ13 | cPVVG | Refrigeration | 0 | 0
Existing | CZ13 | cPVVG | Generators | 0 | 0
Existing | CZ13 | cPVVG | Total End Uses | 3067622.07 | 1321667.15
Existing | CZ14 | cPVVG | Heating | 0 | 247248.51
Existing | CZ14 | cPVVG | Cooling | 1003264.77 | 0
Existing | CZ14 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ14 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ14 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ14 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ14 | cPVVG | Fans | 735981.83 | 0
Existing | CZ14 | cPVVG | Pumps | 0 | 0
Existing | CZ14 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ14 | cPVVG | Humidification | 0 | 0
Existing | CZ14 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ14 | cPVVG | Water Systems | 0 | 661470
Existing | CZ14 | cPVVG | Refrigeration | 0 | 0
Existing | CZ14 | cPVVG | Generators | 0 | 0
Existing | CZ14 | cPVVG | Total End Uses | 3294860.38 | 1127563.36
Existing | CZ15 | cPVVG | Heating | 0 | 86420.88
Existing | CZ15 | cPVVG | Cooling | 1409318.42 | 0
Existing | CZ15 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ15 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ15 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ15 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ15 | cPVVG | Fans | 705650.1 | 0
Existing | CZ15 | cPVVG | Pumps | 0 | 0
Existing | CZ15 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ15 | cPVVG | Humidification | 0 | 0
Existing | CZ15 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ15 | cPVVG | Water Systems | 0 | 587125.27
Existing | CZ15 | cPVVG | Refrigeration | 0 | 0
Existing | CZ15 | cPVVG | Generators | 0 | 0
Existing | CZ15 | cPVVG | Total End Uses | 3670582.3 | 892391.01
Existing | CZ16 | cPVVG | Heating | 0 | 688499.43
Existing | CZ16 | cPVVG | Cooling | 633307 | 0
Existing | CZ16 | cPVVG | Interior Lighting | 673572.97 | 0
Existing | CZ16 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ16 | cPVVG | Interior Equipment | 882040.8 | 218844.85
Existing | CZ16 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ16 | cPVVG | Fans | 777063.27 | 0
Existing | CZ16 | cPVVG | Pumps | 0 | 0
Existing | CZ16 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ16 | cPVVG | Humidification | 0 | 0
Existing | CZ16 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ16 | cPVVG | Water Systems | 0 | 780675.6
Existing | CZ16 | cPVVG | Refrigeration | 0 | 0
Existing | CZ16 | cPVVG | Generators | 0 | 0
Existing | CZ16 | cPVVG | Total End Uses | 2965984.04 | 1688019.88
New Construction | CZ01 | cPVVG | Heating | 0 | 948227.48
New Construction | CZ01 | cPVVG | Cooling | 38492.08 | 0
New Construction | CZ01 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ01 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ01 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ01 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ01 | cPVVG | Fans | 446403.22 | 0
New Construction | CZ01 | cPVVG | Pumps | 0 | 0
New Construction | CZ01 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ01 | cPVVG | Humidification | 0 | 0
New Construction | CZ01 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ01 | cPVVG | Water Systems | 0 | 864529.21
New Construction | CZ01 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ01 | cPVVG | Generators | 0 | 0
New Construction | CZ01 | cPVVG | Total End Uses | 1689386.76 | 2031601.55
New Construction | CZ02 | cPVVG | Heating | 0 | 722479.31
New Construction | CZ02 | cPVVG | Cooling | 237044.37 | 0
New Construction | CZ02 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ02 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ02 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ02 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ02 | cPVVG | Fans | 614642.3 | 0
New Construction | CZ02 | cPVVG | Pumps | 0 | 0
New Construction | CZ02 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ02 | cPVVG | Humidification | 0 | 0
New Construction | CZ02 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ02 | cPVVG | Water Systems | 0 | 793981.57
New Construction | CZ02 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ02 | cPVVG | Generators | 0 | 0
New Construction | CZ02 | cPVVG | Total End Uses | 2056178.12 | 1735305.73
New Construction | CZ03 | cPVVG | Heating | 0 | 514495.55
New Construction | CZ03 | cPVVG | Cooling | 143319.24 | 0
New Construction | CZ03 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ03 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ03 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ03 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ03 | cPVVG | Fans | 573411.7 | 0
New Construction | CZ03 | cPVVG | Pumps | 0 | 0
New Construction | CZ03 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ03 | cPVVG | Humidification | 0 | 0
New Construction | CZ03 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ03 | cPVVG | Water Systems | 0 | 791063.76
New Construction | CZ03 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ03 | cPVVG | Generators | 0 | 0
New Construction | CZ03 | cPVVG | Total End Uses | 1921222.4 | 1524404.17
New Construction | CZ04 | cPVVG | Heating | 0 | 438836.7
New Construction | CZ04 | cPVVG | Cooling | 288240.72 | 0
New Construction | CZ04 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ04 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ04 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ04 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ04 | cPVVG | Fans | 602853.01 | 0
New Construction | CZ04 | cPVVG | Pumps | 0 | 0
New Construction | CZ04 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ04 | cPVVG | Humidification | 0 | 0
New Construction | CZ04 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ04 | cPVVG | Water Systems | 0 | 763577.24
New Construction | CZ04 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ04 | cPVVG | Generators | 0 | 0
New Construction | CZ04 | cPVVG | Total End Uses | 2095585.18 | 1421258.79
New Construction | CZ05 | cPVVG | Heating | 0 | 470673.93
New Construction | CZ05 | cPVVG | Cooling | 181321.07 | 0
New Construction | CZ05 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ05 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ05 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ05 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ05 | cPVVG | Fans | 560015.07 | 0
New Construction | CZ05 | cPVVG | Pumps | 0 | 0
New Construction | CZ05 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ05 | cPVVG | Humidification | 0 | 0
New Construction | CZ05 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ05 | cPVVG | Water Systems | 0 | 791113.39
New Construction | CZ05 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ05 | cPVVG | Generators | 0 | 0
New Construction | CZ05 | cPVVG | Total End Uses | 1945827.59 | 1480632.18
New Construction | CZ06 | cPVVG | Heating | 0 | 142741.15
New Construction | CZ06 | cPVVG | Cooling | 297308.73 | 0
New Construction | CZ06 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ06 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ06 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ06 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ06 | cPVVG | Fans | 553580 | 0
New Construction | CZ06 | cPVVG | Pumps | 0 | 0
New Construction | CZ06 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ06 | cPVVG | Humidification | 0 | 0
New Construction | CZ06 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ06 | cPVVG | Water Systems | 0 | 728482.02
New Construction | CZ06 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ06 | cPVVG | Generators | 0 | 0
New Construction | CZ06 | cPVVG | Total End Uses | 2055380.18 | 1090068.01
New Construction | CZ07 | cPVVG | Heating | 0 | 129312.4
New Construction | CZ07 | cPVVG | Cooling | 323353.4 | 0
New Construction | CZ07 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ07 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ07 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ07 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ07 | cPVVG | Fans | 538667.36 | 0
New Construction | CZ07 | cPVVG | Pumps | 0 | 0
New Construction | CZ07 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ07 | cPVVG | Humidification | 0 | 0
New Construction | CZ07 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ07 | cPVVG | Water Systems | 0 | 719066.75
New Construction | CZ07 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ07 | cPVVG | Generators | 0 | 0
New Construction | CZ07 | cPVVG | Total End Uses | 2066512.21 | 1067224.01
New Construction | CZ08 | cPVVG | Heating | 0 | 174201.89
New Construction | CZ08 | cPVVG | Cooling | 401788.01 | 0
New Construction | CZ08 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ08 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ08 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ08 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ08 | cPVVG | Fans | 577692.22 | 0
New Construction | CZ08 | cPVVG | Pumps | 0 | 0
New Construction | CZ08 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ08 | cPVVG | Humidification | 0 | 0
New Construction | CZ08 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ08 | cPVVG | Water Systems | 0 | 718073.63
New Construction | CZ08 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ08 | cPVVG | Generators | 0 | 0
New Construction | CZ08 | cPVVG | Total End Uses | 2183971.69 | 1111120.38
New Construction | CZ09 | cPVVG | Heating | 0 | 134539.91
New Construction | CZ09 | cPVVG | Cooling | 457656.1 | 0
New Construction | CZ09 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ09 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ09 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ09 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ09 | cPVVG | Fans | 594872.04 | 0
New Construction | CZ09 | cPVVG | Pumps | 0 | 0
New Construction | CZ09 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ09 | cPVVG | Humidification | 0 | 0
New Construction | CZ09 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ09 | cPVVG | Water Systems | 0 | 708037.59
New Construction | CZ09 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ09 | cPVVG | Generators | 0 | 0
New Construction | CZ09 | cPVVG | Total End Uses | 2257019.59 | 1061422.36
New Construction | CZ10 | cPVVG | Heating | 0 | 278255.53
New Construction | CZ10 | cPVVG | Cooling | 620052.3 | 0
New Construction | CZ10 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ10 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ10 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ10 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ10 | cPVVG | Fans | 618196.18 | 0
New Construction | CZ10 | cPVVG | Pumps | 0 | 0
New Construction | CZ10 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ10 | cPVVG | Humidification | 0 | 0
New Construction | CZ10 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ10 | cPVVG | Water Systems | 0 | 702032.98
New Construction | CZ10 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ10 | cPVVG | Generators | 0 | 0
New Construction | CZ10 | cPVVG | Total End Uses | 2442739.93 | 1199133.36
New Construction | CZ11 | cPVVG | Heating | 0 | 499258.91
New Construction | CZ11 | cPVVG | Cooling | 556525.39 | 0
New Construction | CZ11 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ11 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ11 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ11 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ11 | cPVVG | Fans | 497332.87 | 0
New Construction | CZ11 | cPVVG | Pumps | 0 | 0
New Construction | CZ11 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ11 | cPVVG | Humidification | 0 | 0
New Construction | CZ11 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ11 | cPVVG | Water Systems | 0 | 717410.31
New Construction | CZ11 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ11 | cPVVG | Generators | 0 | 0
New Construction | CZ11 | cPVVG | Total End Uses | 2258349.71 | 1435514.07
New Construction | CZ12 | cPVVG | Heating | 0 | 498800.01
New Construction | CZ12 | cPVVG | Cooling | 460589.98 | 0
New Construction | CZ12 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ12 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ12 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ12 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ12 | cPVVG | Fans | 481474.3 | 0
New Construction | CZ12 | cPVVG | Pumps | 0 | 0
New Construction | CZ12 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ12 | cPVVG | Humidification | 0 | 0
New Construction | CZ12 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ12 | cPVVG | Water Systems | 0 | 737818.5
New Construction | CZ12 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ12 | cPVVG | Generators | 0 | 0
New Construction | CZ12 | cPVVG | Total End Uses | 2146555.73 | 1455463.36
New Construction | CZ13 | cPVVG | Heating | 0 | 408375.53
New Construction | CZ13 | cPVVG | Cooling | 618662.15 | 0
New Construction | CZ13 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ13 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ13 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ13 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ13 | cPVVG | Fans | 492291.78 | 0
New Construction | CZ13 | cPVVG | Pumps | 0 | 0
New Construction | CZ13 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ13 | cPVVG | Humidification | 0 | 0
New Construction | CZ13 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ13 | cPVVG | Water Systems | 0 | 696497.11
New Construction | CZ13 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ13 | cPVVG | Generators | 0 | 0
New Construction | CZ13 | cPVVG | Total End Uses | 2315445.39 | 1323717.48
New Construction | CZ14 | cPVVG | Heating | 0 | 250976.62
New Construction | CZ14 | cPVVG | Cooling | 792726.26 | 0
New Construction | CZ14 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ14 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ14 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ14 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ14 | cPVVG | Fans | 525045.47 | 0
New Construction | CZ14 | cPVVG | Pumps | 0 | 0
New Construction | CZ14 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ14 | cPVVG | Humidification | 0 | 0
New Construction | CZ14 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ14 | cPVVG | Water Systems | 0 | 660938.07
New Construction | CZ14 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ14 | cPVVG | Generators | 0 | 0
New Construction | CZ14 | cPVVG | Total End Uses | 2522263.19 | 1130759.54
New Construction | CZ15 | cPVVG | Heating | 0 | 86144.81
New Construction | CZ15 | cPVVG | Cooling | 1114029.67 | 0
New Construction | CZ15 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ15 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ15 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ15 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ15 | cPVVG | Fans | 509836.4 | 0
New Construction | CZ15 | cPVVG | Pumps | 0 | 0
New Construction | CZ15 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ15 | cPVVG | Humidification | 0 | 0
New Construction | CZ15 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ15 | cPVVG | Water Systems | 0 | 586575.43
New Construction | CZ15 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ15 | cPVVG | Generators | 0 | 0
New Construction | CZ15 | cPVVG | Total End Uses | 2828357.52 | 891565.1
New Construction | CZ16 | cPVVG | Heating | 0 | 665992.14
New Construction | CZ16 | cPVVG | Cooling | 502058.96 | 0
New Construction | CZ16 | cPVVG | Interior Lighting | 322450.66 | 0
New Construction | CZ16 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ16 | cPVVG | Interior Equipment | 882040.8 | 218844.85
New Construction | CZ16 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ16 | cPVVG | Fans | 543425.67 | 0
New Construction | CZ16 | cPVVG | Pumps | 0 | 0
New Construction | CZ16 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ16 | cPVVG | Humidification | 0 | 0
New Construction | CZ16 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ16 | cPVVG | Water Systems | 0 | 780107.81
New Construction | CZ16 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ16 | cPVVG | Generators | 0 | 0
New Construction | CZ16 | cPVVG | Total End Uses | 2249976.08 | 1664944.8

## PV
PV - Education - Secondary School (NA)

## EV Charger
EV Charger - Education - Secondary School (NA)

## Raw_building (hidden)
Building Type | Building Category | Roof Type | Window Wall Ratio (%)
Education - Secondary School | Nonresidential | Flat Roof | 15.14

## Raw_windowdimensionsillheight (hidden)
Window Name | Width [ft] | Height [ft] | Sill Height [ft]
E1 NORTH WIN (G.W1.E2.W1) | 7.35 | 5.74 | 3
E1 SOUTH WIN (G.W1.E1.W1) | 7.35 | 5.74 | 3
E1 WEST WIN (G.W1.E3.W1) | 13.88 | 5.74 | 3
E2 NORTH WIN (G.N3.E2.W1) | 45.54 | 5.74 | 3
E2 SOUTH WIN (G.S2.E1.W1) | 45.54 | 5.74 | 3
E4 EAST WIN (G.E2.E2.W1) | 54.99 | 5.74 | 3
E4 NORTH WIN (G.N3.E3.W1) | 109.94 | 5.74 | 3
E4 SOUTH WIN (G.S1.E1.W1) | 109.94 | 5.74 | 3
E4 WEST WIN (G.W4.E4.W1) | 54.99 | 5.74 | 3
E3 EAST WIN (G.SW1.E2.W1) | 16.11 | 5.74 | 3
E3 NORTH WIN (G.SW1.E3.W1) | 23.2 | 5.74 | 3
E3 SOUTH WIN (G.SW1.E1.W1) | 48.43 | 5.74 | 3
E17 EAST WIN (G.W1.E2.W1) | 49.51 | 5.74 | 3
E17 NORTH WIN (G.W1.E3.W1) | 49.51 | 5.74 | 3
E17 SOUTH WIN (G.W1.E1.W1) | 49.51 | 5.74 | 3
E17 WEST WIN (G.W1.E4.W1) | 49.51 | 5.74 | 3
E3 EAST WIN (G.NE2.E5.W1) | 25.3 | 5.74 | 3
E3 NORTH WIN (G.NE2.E4.W1) | 25.23 | 5.74 | 3

## Raw_shadinggeometry (hidden)
Shading Name | Width [ft] | Length [ft]
No Shading

## Raw_zonesummary (hidden)
Vintage | Space | Zone Name | Conditioned | Area (Excluding Plenums and CrawlSpace) (ft2) | Area (Including Plenums and CrawlSpace) (ft2) | Width (ft) | Length (ft) | Volume (ft3) | Multipliers | People (Persons/1000 ft2) | Lighting (Btu/h-ft2) | Plug Loads (Btu/h-ft2) | Outdoor Air Flow per Person (cfm/person) | Outdoor Air Flow per Zone Floor Area (cfm/ft2) | Zone Type | HVAC System Identifier | Schedule Identifier | Height (ft)
Existing | CLASSROOM E1 WEST PERIM (G.W1) | CLASSROOM E1 WEST PERIM (G.W1) | Yes | 3751.24 | 3751.24 | 44.59 | 84.09 | 48768.49 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Alternative | Retail | 13.0006
Existing | CLASSROOM E2 NORTH PERIM (G.N3) | CLASSROOM E2 NORTH PERIM (G.N3) | Yes | 2092.38 | 2092.38 | 69.46 | 30.12 | 18832.36 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | Retail | 9.0004
Existing | CLASSROOM E2 SOUTH PERIM (G.S2) | CLASSROOM E2 SOUTH PERIM (G.S2) | Yes | 2092.38 | 2092.38 | 69.46 | 30.12 | 18832.36 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | Retail | 9.0004
Existing | CLASSROOM E2 WEST PERIM (G.W1) | CLASSROOM E2 WEST PERIM (G.W1) | Yes | 1656.55 | 1656.55 | 69.46 | 23.85 | 14909.67 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | Retail | 9.0004
Existing | CLASSROOM E4 CORE (G.C6) | CLASSROOM E4 CORE (G.C6) | Yes | 1798.23 | 1798.23 | 75.39 | 34.32 | 16184.9 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0005
Existing | CLASSROOM E4 EAST PERIM (G.E2) | CLASSROOM E4 EAST PERIM (G.E2) | Yes | 1619.41 | 1619.41 | 42.52 | 84.09 | 14575.41 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
Existing | CLASSROOM E4 NORTH PERIM (G.N3) | CLASSROOM E4 NORTH PERIM (G.N3) | Yes | 4148.61 | 4148.61 | 167.68 | 42.52 | 37339.35 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
Existing | CLASSROOM E4 SOUTH PERIM (G.S1) | CLASSROOM E4 SOUTH PERIM (G.S1) | Yes | 4148.61 | 4148.61 | 107.71 | 42.52 | 37339.35 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
Existing | CLASSROOM E4 WEST PERIM (G.W4) | CLASSROOM E4 WEST PERIM (G.W4) | Yes | 1619.41 | 1619.41 | 30.12 | 42.52 | 14575.41 | 1 | 25 | 4.48 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
Existing | COMPUTER CLASSROOM E4 CORE SPC (G.C5) | COMPUTER CLASSROOM E4 CORE SPC (G.C5) | Yes | 770.67 | 770.67 | 32.32 | 23.85 | 6936.36 | 1 | 1.5 | 3.7719 | 68.2333 | 0.0 | 0.15 | Computer | Customized | Computer room | 9.0004
Existing | DINING E3 SW PERIM (G.SW1) | DINING E3 SW PERIM (G.SW1) | Yes | 5634 | 5634 | 75.07 | 75.07 | 73245.58 | 1 | 33.33 | 4.1409 | 2.5588 | 0.0 | 0.5 | Dining_fast | Alternative | Retail | 13.0006
Existing | E2 NORTH PERIM PLNM (G.N6) | E2 NORTH PERIM PLNM (G.N6) | No | 0 | 2092.38 | 69.46 | 42.52 | 8369.94 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | E2 SOUTH PERIM PLNM (G.S5) | E2 SOUTH PERIM PLNM (G.S5) | No | 0 | 2092.38 | 69.46 | 42.52 | 8369.94 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | E2 WEST PERIM PLNM (G.W4) | E2 WEST PERIM PLNM (G.W4) | No | 0 | 1656.55 | 69.46 | 23.85 | 6626.52 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | E4 CORE PLNM (G.C11) | E4 CORE PLNM (G.C11) | No | 0 | 770.67 | 32.32 | 23.85 | 3082.83 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | E4 CORE PLNM (G.C12) | E4 CORE PLNM (G.C12) | No | 0 | 1798.23 | 75.39 | 23.85 | 7193.29 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | E4 EAST PERIM PLNM (G.E8) | E4 EAST PERIM PLNM (G.E8) | No | 0 | 1619.41 | 42.52 | 84.09 | 6477.96 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | E4 NORTH PERIM PLNM (G.N9) | E4 NORTH PERIM PLNM (G.N9) | No | 0 | 4148.61 | 167.68 | 42.52 | 16595.27 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | E4 SOUTH PERIM PLNM (G.S7) | E4 SOUTH PERIM PLNM (G.S7) | No | 0 | 4148.61 | 167.68 | 42.52 | 16595.27 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | E4 WEST PERIM PLNM (G.W10) | E4 WEST PERIM PLNM (G.W10) | No | 0 | 1619.41 | 23.85 | 42.52 | 6477.96 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
Existing | GYMNASIUM E17 WEST PERIM (G.W1) | GYMNASIUM E17 WEST PERIM (G.W1) | Yes | 22502.2 | 22502.2 | 150 | 150 | 585085.65 | 1 | 33.33 | 3.3597 | 1.7058 | 0.0 | 0.5 | Gym | Alternative | Retail | 26.0013
Existing | KITCHEN E3 NE PERIM (G.NE2) | KITCHEN E3 NE PERIM (G.NE2) | Yes | 2629.64 | 2629.64 | 51.18 | 51.38 | 34187 | 1 | 2.5 | 5.6273 | 26.4716 | 0.0 | 0.15 | Kitchen | Customized | Kitchen | 13.0006
New Construction | CLASSROOM E1 WEST PERIM (G.W1) | CLASSROOM E1 WEST PERIM (G.W1) | Yes | 3751.24 | 3751.24 | 44.59 | 84.09 | 48768.49 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Alternative | Retail | 13.0006
New Construction | CLASSROOM E2 NORTH PERIM (G.N3) | CLASSROOM E2 NORTH PERIM (G.N3) | Yes | 2092.38 | 2092.38 | 69.46 | 30.12 | 18832.36 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | Retail | 9.0004
New Construction | CLASSROOM E2 SOUTH PERIM (G.S2) | CLASSROOM E2 SOUTH PERIM (G.S2) | Yes | 2092.38 | 2092.38 | 69.46 | 30.12 | 18832.36 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | Retail | 9.0004
New Construction | CLASSROOM E2 WEST PERIM (G.W1) | CLASSROOM E2 WEST PERIM (G.W1) | Yes | 1656.55 | 1656.55 | 69.46 | 23.85 | 14909.67 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | Retail | 9.0004
New Construction | CLASSROOM E4 CORE (G.C6) | CLASSROOM E4 CORE (G.C6) | Yes | 1798.23 | 1798.23 | 75.39 | 34.32 | 16184.9 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0005
New Construction | CLASSROOM E4 EAST PERIM (G.E2) | CLASSROOM E4 EAST PERIM (G.E2) | Yes | 1619.41 | 1619.41 | 42.52 | 84.09 | 14575.41 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
New Construction | CLASSROOM E4 NORTH PERIM (G.N3) | CLASSROOM E4 NORTH PERIM (G.N3) | Yes | 4148.61 | 4148.61 | 167.68 | 42.52 | 37339.35 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
New Construction | CLASSROOM E4 SOUTH PERIM (G.S1) | CLASSROOM E4 SOUTH PERIM (G.S1) | Yes | 4148.61 | 4148.61 | 107.71 | 42.52 | 37339.35 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
New Construction | CLASSROOM E4 WEST PERIM (G.W4) | CLASSROOM E4 WEST PERIM (G.W4) | Yes | 1619.41 | 1619.41 | 30.12 | 42.52 | 14575.41 | 1 | 25 | 2.047 | 3.4117 | 0.0 | 0.38 | Classroom_class | Main | School | 9.0004
New Construction | COMPUTER CLASSROOM E4 CORE SPC (G.C5) | COMPUTER CLASSROOM E4 CORE SPC (G.C5) | Yes | 770.67 | 770.67 | 32.32 | 23.85 | 6936.36 | 1 | 1.5 | 1.7058 | 68.2333 | 0.0 | 0.15 | Computer | Customized | Computer room | 9.0004
New Construction | DINING E3 SW PERIM (G.SW1) | DINING E3 SW PERIM (G.SW1) | Yes | 5634 | 5634 | 75.07 | 75.07 | 73245.58 | 1 | 33.33 | 1.5353 | 2.5588 | 0.0 | 0.5 | Dining_fast | Alternative | Retail | 13.0006
New Construction | E2 NORTH PERIM PLNM (G.N6) | E2 NORTH PERIM PLNM (G.N6) | No | 0 | 2092.38 | 69.46 | 42.52 | 8369.94 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | E2 SOUTH PERIM PLNM (G.S5) | E2 SOUTH PERIM PLNM (G.S5) | No | 0 | 2092.38 | 69.46 | 42.52 | 8369.94 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | E2 WEST PERIM PLNM (G.W4) | E2 WEST PERIM PLNM (G.W4) | No | 0 | 1656.55 | 69.46 | 23.85 | 6626.52 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | E4 CORE PLNM (G.C11) | E4 CORE PLNM (G.C11) | No | 0 | 770.67 | 32.32 | 23.85 | 3082.83 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | E4 CORE PLNM (G.C12) | E4 CORE PLNM (G.C12) | No | 0 | 1798.23 | 75.39 | 23.85 | 7193.29 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | E4 EAST PERIM PLNM (G.E8) | E4 EAST PERIM PLNM (G.E8) | No | 0 | 1619.41 | 42.52 | 84.09 | 6477.96 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | E4 NORTH PERIM PLNM (G.N9) | E4 NORTH PERIM PLNM (G.N9) | No | 0 | 4148.61 | 167.68 | 42.52 | 16595.27 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | E4 SOUTH PERIM PLNM (G.S7) | E4 SOUTH PERIM PLNM (G.S7) | No | 0 | 4148.61 | 167.68 | 42.52 | 16595.27 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | E4 WEST PERIM PLNM (G.W10) | E4 WEST PERIM PLNM (G.W10) | No | 0 | 1619.41 | 23.85 | 42.52 | 6477.96 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 4.0002
New Construction | GYMNASIUM E17 WEST PERIM (G.W1) | GYMNASIUM E17 WEST PERIM (G.W1) | Yes | 22502.2 | 22502.2 | 150 | 150 | 585085.65 | 1 | 33.33 | 1.7058 | 1.7058 | 0.0 | 0.5 | Gym | Alternative | Retail | 26.0013
New Construction | KITCHEN E3 NE PERIM (G.NE2) | KITCHEN E3 NE PERIM (G.NE2) | Yes | 2629.64 | 2629.64 | 51.18 | 51.38 | 34187 | 1 | 2.5 | 3.2411 | 26.4716 | 0.0 | 0.15 | Kitchen | Customized | Kitchen | 13.0006