## Geometry Summary (hidden)
Abbreviation | Building Type | Shape | Number of Floors | Aspect Ratio | Zone Height_1 | Zone Height_2 | Zone Height_3 | Plenum Height | Floor to Floor Height (feet) | Floor to Ceiling Height (feet)
Asm | Assembly | #VALUE! | 1 | 1 | 12.0006 | na | na | 3.0001 | 12.0006 | 15.0007
ECC | Education - Community College | #VALUE! | 3 | 5.7 | 9.0004 | 13.0006 | na | 4.0002 | 9 / 13 | 13 / 17
EPr | Education - Primary School | #VALUE! | 1 | 2 | 9.0004 | 12.0006 | na | 3.0001 | 9 / 12 | 12 / 15
ERC | Education - Relocatable Classroom | #VALUE! | 1 | 1.7 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
ESe | Education - Secondary School | #VALUE! | 2 | 2.5/1.0 | 9.0004 | 13.0006 | na | 4.0002 | 9 / 13 | 13 / 17
EUn | Education - University | #VALUE! | 4 | 2.0/15.0 | 10.0005 | 9.0004 | 14.0007 | 4.0002 | 9 / 10 / 14 | 13 / 14 / 18
Fin | Financial buildings, incl. banks | #VALUE! | 1 | 1 | 11.0005 | na | na | na | 11.0005 | 11.0005
Gro | Grocery | #VALUE! | 1 | 1 | 25.0012 | na | na | na | 25.0012 | 25.0012
Hsp | Health/Medical - Hospital | #VALUE! | 3 | 1 | 10.007 | 12.9927 | na | 2.9857 | 10 / 13 | 13 / 16
Htl | Lodging - Hotel | #VALUE! | 4 | 6.6 | 8.0004 | 10.5005 | na | 1.5001 | 8 / 11 | 10 / 12
Lib | Libraries | #VALUE! | 1 | 1 | 13.0006 | na | na | na | 13.0006 | 13.0006
MBT | Manufacturing Biotech | #VALUE! | 1 | 6 | 9.0004 | na | na | 6.0003 | 9.0004 | 15.0008
MLI | Manufacturing Light Industrial | #VALUE! | 1 | 1 | 35.0017 | na | na | na | 35.0017 | 35.0017
Mtl | Lodging - Motel | #VALUE! | 2 | 5.1 | 9.0004 | na | na | na | 9.0004 | 9.0004
Nrs | Health/Medical - Nursing Home | #VALUE! | 2 | 10.3 | 12.9986 | 9.0005 | na | 4.0055 | 9 / 13 | 13 / 17
OfL | Office - Large | #VALUE! | 3 | 1.5 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
OfS | Office - Small | #VALUE! | 2 | 1.5 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
Rel | Religious assembly buildings | #VALUE! | 1 | 2.5 | 37.5018 | 15.0007 | na | na | 38 / 15 | 38 / 15
RFF | Restaurant - Fast-Food | #VALUE! | 1 | 1 | 10.0005 | na | na | 3.0002 | 10.0005 | 13.0007
RSD | Restaurant - Sit-Down | #VALUE! | 1 | 1 | 10.0005 | na | na | 3.0001 | 10.0005 | 13.0006
Rt3 | Retail - Multistory Large | #VALUE! | 3 | 1 | 15.0007 | na | na | 5.8002 | 15.0007 | 20.8009
RtL | Retail - Single-Story Large | #VALUE! | 1 | 1 | 20.501 | na | na | na | 20.501 | 20.501
RtS | Retail - Small | #VALUE! | 1 | 1 | 10.0005 | na | na | 2.0001 | 10.0005 | 12.0006
SCn | Storage - Conditioned | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023
SUn | Storage - Unconditioned | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023
WRf | Warehouse - Refrigerated | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023

## Prototype
TRC, Updated Febuary 2026
Health/Medical - Hospital
Characteristic | Value
Building Type | Health/Medical - Hospital
Building Category | Nonresidential
Vintages | Two vintages: Existing and New Construction
Shape | #VALUE!
Total Floor Area (ft²) | 250010.12
Aspect Ratio | 1
Number of Floors | 3
Roof Type | Flat Roof
Gross Window to Wall Ratio (%) | 10.02
Shading Geometry | No Shading
Floor to Floor Height (feet) | 10 / 13
Floor to Ceiling Height (feet) | 13 / 16
Glazing Sill Height (feet) | 2.99

## Notes
Prototype Overview
Name | Description
Asm | Assembly
ECC | Education - Community College
EPr | Education - Primary School
ERC | Education - Relocatable Classroom
ESe | Education - Secondary School
EUn | Education - University
Fin | Financial buildings, incl. banks
Gro | Grocery
Hsp | Health/Medical - Hospital
Htl | Lodging - Hotel
Lib | Libraries
MBT | Manufacturing Biotech
MLI | Manufacturing Light Industrial
Mtl | Lodging - Motel
Nrs | Health/Medical - Nursing Home
OfL | Office - Large
OfS | Office - Small
Rel | Religious assembly buildings
RFF | Restaurant - Fast-Food
RSD | Restaurant - Sit-Down
Rt3 | Retail - Multistory Large
RtL | Retail - Single-Story Large
RtS | Retail - Small
SCn | Storage - Conditioned
SUn | Storage - Unconditioned
WRf | Warehouse - Refrigerated
Vintages
Existing | Weighted average of Title 24 requirements based on vintages from 1975 to 2022
New Construction | Title 24 2025
Run Begin Day
Begin Month | Begin Day of Month | Day of Week for Start Day
1 | 1 | Sunday
Special Days
Name | Start Date | Duration (days) | Special Day Type
New Years Day | January 1 | 1 | Holiday
Veterans Day | November 11 | 1 | Holiday
Christmas | December 25 | 1 | Holiday
Independence Day | July 4 | 1 | Holiday
MLK Day | 3rd Monday in January | 1 | Holiday
Presidents Day | 3rd Monday in February | 1 | Holiday
Memorial Day | Last Monday in May | 1 | Holiday
Labor Day | 1st Monday in September | 1 | Holiday
Columbus Day | 2nd Monday in October | 1 | Holiday
Thanksgiving | 4th Thursday in November | 1 | Holiday

## Raw_runbeginday (hidden)
Begin Month | Begin Day of Month | Day of Week for Start Day
1 | 1 | Sunday

## Raw_specialdays (hidden)
Name | Start Day | Duration | Special Day Type
New Years Day | January 1 | 1 | Holiday
Veterans Day | November 11 | 1 | Holiday
Christmas | December 25 | 1 | Holiday
Independence Day | July 4 | 1 | Holiday
MLK Day | 3rd Monday in January | 1 | Holiday
Presidents Day | 3rd Monday in February | 1 | Holiday
Memorial Day | Last Monday in May | 1 | Holiday
Labor Day | 1st Monday in September | 1 | Holiday
Columbus Day | 2nd Monday in October | 1 | Holiday
Thanksgiving | 4th Thursday in November | 1 | Holiday

## Climate Zone
Climate Zones - All Prototypes
Climate Zone | Representative City | Weather File Name
CZ01 | Eureka | CA_EUREKA_725940S_CZ2022.epw
CZ02 | Napa | CA_NAPA-CO_724955S_CZ2022.epw
CZ03 | Oakland | CA_OAKLAND-METRO-AP_724930S_CZ2022.epw
CZ04 | San Jose | CA_SAN-JOSE-IAP_724945S_CZ2022.epw
CZ05 | Santa Maria | CA_SANTA-MARIA-PUBLIC-AP_723940S_CZ2022.epw
CZ06 | Los Angeles | CA_LOS-ANGELES-IAP_722950S_CZ2022.epw
CZ07 | San Diego-Lindbergh | CA_SAN-DIEGO-LINDBERGH-FLD_722900S_CZ2022.epw
CZ08 | Long Beach-Daugherty | CA_LONG-BEACH-DAUGHERTY-FLD_722970S_CZ2022.epw
CZ09 | Los Angeles | CA_LOS-ANGELES-DOWNTOWN-USC_722874S_CZ2022.epw
CZ10 | Riverside | CA_RIVERSIDE-MUNI_722869S_CZ2022.epw
CZ11 | Red Bluff | CA_RED-BLUFF-MUNI-AP_725910S_CZ2022.epw
CZ12 | Stockton | CA_STOCKTON-METRO-AP_724920S_CZ2022.epw
CZ13 | Fresno Yosemite | CA_FRESNO-YOSEMITE-IAP_723890S_CZ2022.epw
CZ14 | Daggett Barstow | CA_DAGGETT-BARSTOW-AP_723815S_CZ2022.epw
CZ15 | El Centro | CA_EL-CENTRO-NAF_722810S_CZ2022.epw
CZ16 | Bishop | CA_BISHOP-AP_724800S_CZ2022.epw
Source: California Energy Commission, https://cecgis-caenergy.opendata.arcgis.com/datasets/CAEnergy::california-building-climate-zones/about

## Zones
Zone Summary - Health/Medical - Hospital
Space | Zone Name | Conditioned [Y/N] | Zone Type | HVAC System Identifier (Main/Alternative/Customized) | Schedule Identifier | Area Fraction | Area (Excluding Plenums and Crawl Space) (ft²) | Volume (ft³) | Multipliers | People (Persons/1,000 ft²) | Note
DINING EL1 NORTH PERIM (G.N1) | DINING EL1 NORTH PERIM (G.N1) | Yes | Dining_fast | Main | Office | 0.945% | 2362.68 | 30697.7 | 1 | 33.33
DINING EL1 SOUTH PERIM (G.S2) | DINING EL1 SOUTH PERIM (G.S2) | Yes | Dining_fast | Main | Office | 0.7036% | 1759.04 | 22854.75 | 1 | 33.33
EL2 CORE PLNM ZN (G.C14) | EL2 CORE PLNM ZN (G.C14) | No | Plenum | - | Plenum | 0% | 0 | 133338.68 | 1 | 0
EL2 EAST PERIM PLNM ZN (G.E8) | EL2 EAST PERIM PLNM ZN (G.E8) | No | Plenum | - | Plenum | 0% | 0 | 17663.95 | 1 | 0
EL2 NNW PERIM PLNM ZN (G.NNW10) | EL2 NNW PERIM PLNM ZN (G.NNW10) | No | Plenum | - | Plenum | 0% | 0 | 4693.75 | 1 | 0
EL2 NORTH PERIM PLNM ZN (G.N13) | EL2 NORTH PERIM PLNM ZN (G.N13) | No | Plenum | - | Plenum | 0% | 0 | 17921.36 | 1 | 0
EL2 SSW PERIM PLNM ZN (G.SSW9) | EL2 SSW PERIM PLNM ZN (G.SSW9) | No | Plenum | - | Plenum | 0% | 0 | 4693.75 | 1 | 0
EL2 SOUTH PERIM PLNM ZN (G.S12) | EL2 SOUTH PERIM PLNM ZN (G.S12) | No | Plenum | - | Plenum | 0% | 0 | 17921.36 | 1 | 0
EL2 WEST PERIM PLNM ZN (G.W11) | EL2 WEST PERIM PLNM ZN (G.W11) | No | Plenum | - | Plenum | 0% | 0 | 34922.47 | 1 | 0
EL3 CORE PLNM ZN (G.C16) | EL3 CORE PLNM ZN (G.C16) | No | Plenum | - | Plenum | 0% | 0 | 52756.77 | 1 | 0
EL3 CORE PLNM ZN (G.C16) ZN | EL3 CORE PLNM ZN (G.C16) ZN | No | Plenum | - | Plenum | 0% | 0 | 115504.38 | 1 | 0
EL3 EAST PERIM PLNM ZN (G.E9) | EL3 EAST PERIM PLNM ZN (G.E9) | No | Plenum | - | Plenum | 0% | 0 | 17663.95 | 1 | 0
EL3 NORTH PERIM PLNM ZN (G.N11) | EL3 NORTH PERIM PLNM ZN (G.N11) | No | Plenum | - | Plenum | 0% | 0 | 7090.76 | 1 | 0
EL3 NORTH PERIM PLNM ZN (G.N14) | EL3 NORTH PERIM PLNM ZN (G.N14) | No | Plenum | - | Plenum | 0% | 0 | 15524.34 | 1 | 0
EL3 SOUTH PERIM PLNM ZN (G.S12) | EL3 SOUTH PERIM PLNM ZN (G.S12) | No | Plenum | - | Plenum | 0% | 0 | 7090.76 | 1 | 0
EL3 SOUTH PERIM PLNM ZN (G.S15) | EL3 SOUTH PERIM PLNM ZN (G.S15) | No | Plenum | - | Plenum | 0% | 0 | 15524.34 | 1 | 0
EL3 WEST PERIM PLNM ZN (G.W10) | EL3 WEST PERIM PLNM ZN (G.W10) | No | Plenum | - | Plenum | 0% | 0 | 17663.95 | 1 | 0
EL4 CORE PLNM ZN (G.C13) | EL4 CORE PLNM ZN (G.C13) | No | Plenum | - | Plenum | 0% | 0 | 80199.75 | 1 | 0
EL4 CORE PLNM ZN (G.C16) | EL4 CORE PLNM ZN (G.C16) | No | Plenum | - | Plenum | 0% | 0 | 88061.4 | 1 | 0
EL4 EAST PERIM PLNM ZN (G.E9) | EL4 EAST PERIM PLNM ZN (G.E9) | No | Plenum | - | Plenum | 0% | 0 | 17663.95 | 1 | 0
EL4 NORTH PERIM PLNM ZN (G.N11) | EL4 NORTH PERIM PLNM ZN (G.N11) | No | Plenum | - | Plenum | 0% | 0 | 10779.23 | 1 | 0
EL4 NORTH PERIM PLNM ZN (G.N14) | EL4 NORTH PERIM PLNM ZN (G.N14) | No | Plenum | - | Plenum | 0% | 0 | 11835.87 | 1 | 0
EL4 SOUTH PERIM PLNM ZN (G.S12) | EL4 SOUTH PERIM PLNM ZN (G.S12) | No | Plenum | - | Plenum | 0% | 0 | 10779.23 | 1 | 0
EL4 SOUTH PERIM PLNM ZN (G.S15) | EL4 SOUTH PERIM PLNM ZN (G.S15) | No | Plenum | - | Plenum | 0% | 0 | 11835.87 | 1 | 0
EL4 WEST PERIM PLNM ZN (G.W10) | EL4 WEST PERIM PLNM ZN (G.W10) | No | Plenum | - | Plenum | 0% | 0 | 17663.95 | 1 | 0
KITCHEN EL1 WEST PERIM (G.W3) | KITCHEN EL1 WEST PERIM (G.W3) | Yes | Kitchen | Customized | Kitchen | 0.7178% | 1794.45 | 23314.85 | 1 | 2.5
OFFICE EL2 CORE (G.C7) | OFFICE EL2 CORE (G.C7) | Yes | Office | Main | Office | 17.86% | 44658.95 | 446904.36 | 1 | 5
OFFICE EL2 EAST PERIM (G.E1) | OFFICE EL2 EAST PERIM (G.E1) | Yes | Office | Main | Office | 2.366% | 5916.16 | 59203.35 | 1 | 5
OFFICE EL2 NORTH PERIM (G.N6) | OFFICE EL2 NORTH PERIM (G.N6) | Yes | Office | Main | Office | 2.401% | 6002.38 | 60066.09 | 1 | 5
OFFICE EL2 SOUTH PERIM (G.S5) | OFFICE EL2 SOUTH PERIM (G.S5) | Yes | Office | Main | Office | 2.401% | 6002.38 | 60066.09 | 1 | 5
OFFICE EL3 CORE (G.C5) | OFFICE EL3 CORE (G.C5) | Yes | Office | Alternative | Health | 7.068% | 17669.76 | 176822.13 | 1 | 5
OFFICE EL3 NORTH PERIM (G.N3) | OFFICE EL3 NORTH PERIM (G.N3) | Yes | Office | Alternative | Health | 0.9499% | 2374.9 | 23765.74 | 1 | 5
OFFICE EL3 SOUTH PERIM (G.S4) | OFFICE EL3 SOUTH PERIM (G.S4) | Yes | Office | Alternative | Health | 0.9499% | 2374.9 | 23765.74 | 1 | 5
OFFICE EL3 WEST PERIM (G.W2) | OFFICE EL3 WEST PERIM (G.W2) | Yes | Office | Alternative | Health | 2.366% | 5916.16 | 59203.35 | 1 | 5
PATIENTROOM EL3 CORE (G.C8) | PATIENTROOM EL3 CORE (G.C8) | Yes | Health_patient | Alternative | Health | 15.47% | 38685.73 | 387130.06 | 1 | 5
PATIENTROOM EL3 EAST PERIM (G.E1) | PATIENTROOM EL3 EAST PERIM (G.E1) | Yes | Health_patient | Alternative | Health | 2.366% | 5916.16 | 59203.35 | 1 | 5
PATIENTROOM EL3 NORTH PERIM (G.N6) | PATIENTROOM EL3 NORTH PERIM (G.N6) | Yes | Health_patient | Alternative | Health | 2.08% | 5199.55 | 52032.14 | 1 | 5
PATIENTROOM EL3 SOUTH PERIM (G.S7) | PATIENTROOM EL3 SOUTH PERIM (G.S7) | Yes | Health_patient | Alternative | Health | 2.08% | 5199.55 | 52032.14 | 1 | 5
PATIENTROOM EL4 CORE (G.C5) | PATIENTROOM EL4 CORE (G.C5) | Yes | Health_patient | Alternative | Health | 10.74% | 26861.2 | 268801.35 | 1 | 5
PATIENTROOM EL4 NORTH PERIM (G.N3) | PATIENTROOM EL4 NORTH PERIM (G.N3) | Yes | Health_patient | Alternative | Health | 1.444% | 3610.27 | 36128.19 | 1 | 5
PATIENTROOM EL4 SOUTH PERIM (G.S4) | PATIENTROOM EL4 SOUTH PERIM (G.S4) | Yes | Health_patient | Alternative | Health | 1.444% | 3610.27 | 36128.19 | 1 | 5
PATIENTROOM EL4 WEST PERIM (G.W2) | PATIENTROOM EL4 WEST PERIM (G.W2) | Yes | Health_patient | Alternative | Health | 2.366% | 5916.16 | 59203.35 | 1 | 5
SURGERY EL2 NNW PERIM (G.NNW3) | SURGERY EL2 NNW PERIM (G.NNW3) | Yes | Health_operating | Main | Office | 0.6288% | 1572.07 | 15731.79 | 1 | 5
SURGERY EL2 SSW PERIM (G.SSW2) | SURGERY EL2 SSW PERIM (G.SSW2) | Yes | Health_operating | Main | Office | 0.6288% | 1572.07 | 15731.79 | 1 | 5
SURGERY EL2 WEST PERIM (G.W4) | SURGERY EL2 WEST PERIM (G.W4) | Yes | Health_operating | Main | Office | 4.678% | 11696.54 | 117047.83 | 1 | 5
SURGERY EL4 CORE (G.C8) | SURGERY EL4 CORE (G.C8) | Yes | Health_operating | Alternative | Health | 11.8% | 29494.29 | 295150.84 | 1 | 5
SURGERY EL4 EAST PERIM (G.E1) | SURGERY EL4 EAST PERIM (G.E1) | Yes | Health_operating | Alternative | Health | 2.366% | 5916.16 | 59203.35 | 1 | 5
SURGERY EL4 NORTH PERIM (G.N6) | SURGERY EL4 NORTH PERIM (G.N6) | Yes | Health_operating | Alternative | Health | 1.586% | 3964.17 | 39669.69 | 1 | 5
SURGERY EL4 SOUTH PERIM (G.S7) | SURGERY EL4 SOUTH PERIM (G.S7) | Yes | Health_operating | Alternative | Health | 1.586% | 3964.17 | 39669.69 | 1 | 5
Total (49 Space) | Total (49 Space) | Total (26 Conditioned zones, 23 Unconditioned Zones) |  |  |  |  | 250010.12

## Envelope
Envelope - Health/Medical - Hospital
Element | Prototype | Assembly Type | Construction | Unit | Vintage | Selected T24 | Note | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Health/Medical - Hospital | - | Stucco+Wall Continuous Insulation+Gypsum 5/8in | U-value IP | Existing | Weighted average |  | 0.393 | 0.609 | 0.577 | 0.629 | 0.615 | 0.623 | 0.73 | 0.626 | 0.621 | 0.884 | 0.497 | 0.533 | 0.509 | 0.384 | 0.378 | 0.357
External Wall | Health/Medical - Hospital | - | Stucco+Wall Continuous Insulation+Gypsum 5/8in | U-value IP | New Construction | 2025 |  | 0.257 | 1.452 | 1.452 | 1.452 | 1.452 | 1.515 | 1.515 | 1.515 | 1.515 | 1.452 | 0.185 | 0.257 | 0.218 | 0.185 | 0.185 | 0.176
Roof | Health/Medical - Hospital | - | Roof Membrane+Roof Continuous Insulation+Metal Decking | U-value IP | Existing | Weighted average |  | 0.062 | 0.061 | 0.062 | 0.061 | 0.061 | 0.065 | 0.065 | 0.065 | 0.065 | 0.062 | 0.061 | 0.061 | 0.06 | 0.06 | 0.059 | 0.06
Roof | Health/Medical - Hospital | - | Roof Membrane+Roof Continuous Insulation+Metal Decking | U-value IP | New Construction | 2025 |  | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
Windows | Health/Medical - Hospital | - | Theoretical Glazing | U-value IP | Existing | Weighted average |  | 1.024 | 1.078 | 1.131 | 1.108 | 1.109 | 1.115 | 1.075 | 1.114 | 1.112 | 0.875 | 0.942 | 0.94 | 0.929 | 0.886 | 0.831 | 0.885
Windows | Health/Medical - Hospital | - | Theoretical Glazing | U-value IP | New Construction | 2025 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
Windows | Health/Medical - Hospital | - | Theoretical Glazing | SHGC | Existing | Weighted average |  | 0.70708 | 0.70715 | 0.73753 | 0.71836 | 0.75308 | 0.7254 | 0.72673 | 0.7241 | 0.72365 | 0.5734 | 0.64366 | 0.64394 | 0.6358 | 0.60724 | 0.57129 | 0.62767
Windows | Health/Medical - Hospital | - | Theoretical Glazing | SHGC | New Construction | 2025 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Windows | Health/Medical - Hospital | - | Theoretical Glazing | Visible Transmittance | Existing | Weighted average |  | 0.26089 | 0.26141 | 0.26004 | 0.26231 | 0.26223 | 0.26197 | 0.26576 | 0.26213 | 0.26228 | 0.27816 | 0.26665 | 0.26607 | 0.26793 | 0.27125 | 0.27583 | 0.27139
Windows | Health/Medical - Hospital | - | Theoretical Glazing | Visible Transmittance | New Construction | 2025 |  | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
Infiltration - Health/Medical - Hospital
|  |  |  | Element | Unit | Vintage | Note | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
|  |  |  | Infiltration Rate | CFM/ft2 | Existing | Infiltration rate is flow rate per exterior surface area at 10 mph wind speed, modeled proportionally to wind speed. | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801
[6 empty] | New Construction |  | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801

## Raw_envelope (hidden)
Climate Zone | Vintage | Exterior Roof Layers | Roof U-Value [Btu/h-ft2-F] | Exterior Wall Layers | Wall U-Value [Btu/h-ft2-F] | Exterior Window Layers | Window U-Value [Btu/h-ft2-F] | Window SHGC | Window VT
CZ01 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.062 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.393 | Theoretical Glazing | 1.024 | 0.70708 | 0.26089
CZ02 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.609 | Theoretical Glazing | 1.078 | 0.70715 | 0.26141
CZ03 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.062 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.577 | Theoretical Glazing | 1.131 | 0.73753 | 0.26004
CZ04 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.629 | Theoretical Glazing | 1.108 | 0.71836 | 0.26231
CZ05 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.615 | Theoretical Glazing | 1.109 | 0.75308 | 0.26223
CZ06 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.623 | Theoretical Glazing | 1.115 | 0.7254 | 0.26197
CZ07 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.73 | Theoretical Glazing | 1.075 | 0.72673 | 0.26576
CZ08 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.626 | Theoretical Glazing | 1.114 | 0.7241 | 0.26213
CZ09 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.621 | Theoretical Glazing | 1.112 | 0.72365 | 0.26228
CZ10 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.062 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.884 | Theoretical Glazing | 0.875 | 0.5734 | 0.27816
CZ11 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.497 | Theoretical Glazing | 0.942 | 0.64366 | 0.26665
CZ12 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.533 | Theoretical Glazing | 0.94 | 0.64394 | 0.26607
CZ13 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.06 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.509 | Theoretical Glazing | 0.929 | 0.6358 | 0.26793
CZ14 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.06 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.384 | Theoretical Glazing | 0.886 | 0.60724 | 0.27125
CZ15 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.059 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.378 | Theoretical Glazing | 0.831 | 0.57129 | 0.27583
CZ16 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.06 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.357 | Theoretical Glazing | 0.885 | 0.62767 | 0.27139
CZ01 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.257 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ02 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.452 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ03 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.452 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ04 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.452 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ05 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.452 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ06 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.515 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ07 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.515 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ08 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.515 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ09 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.515 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ10 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 1.452 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ11 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.185 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ12 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.257 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ13 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.218 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ14 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.185 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ15 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.185 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ16 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.176 | Theoretical Glazing | 0.36 | 0.25 | 0.42

## Raw_infiltrationcfmft (hidden)
Vintage | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Existing | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801
New Construction | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801

## Thermostat
Thermostat Setpoints - Health/Medical - Hospital | [18 empty] | Zone Type
Schedule Identifier | Setpoint | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Notes | Health
Health | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Kitchen
Health | Heating Setback (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | Office
Health | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Health | Cooling Setback (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Kitchen | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Office | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Office | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Office | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Office | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Raw_thermostatsetpoints (hidden)
Climate Zone | Schedule Identifier | Heating Setpoint (F) | Heating Setback (F) | Cooling Setpoint (F) | Cooling Setback (F)
CZ01 | Health | 70 | 70 | 75 | 75
CZ01 | Kitchen | 70 | 60 | 75 | 85
CZ01 | Office | 70 | 60 | 75 | 85
CZ02 | Health | 70 | 70 | 75 | 75
CZ02 | Kitchen | 70 | 60 | 75 | 85
CZ02 | Office | 70 | 60 | 75 | 85
CZ03 | Health | 70 | 70 | 75 | 75
CZ03 | Kitchen | 70 | 60 | 75 | 85
CZ03 | Office | 70 | 60 | 75 | 85
CZ04 | Health | 70 | 70 | 75 | 75
CZ04 | Kitchen | 70 | 60 | 75 | 85
CZ04 | Office | 70 | 60 | 75 | 85
CZ05 | Health | 70 | 70 | 75 | 75
CZ05 | Kitchen | 70 | 60 | 75 | 85
CZ05 | Office | 70 | 60 | 75 | 85
CZ06 | Health | 70 | 70 | 75 | 75
CZ06 | Kitchen | 70 | 60 | 75 | 85
CZ06 | Office | 70 | 60 | 75 | 85
CZ07 | Health | 70 | 70 | 75 | 75
CZ07 | Kitchen | 70 | 60 | 75 | 85
CZ07 | Office | 70 | 60 | 75 | 85
CZ08 | Health | 70 | 70 | 75 | 75
CZ08 | Kitchen | 70 | 60 | 75 | 85
CZ08 | Office | 70 | 60 | 75 | 85
CZ09 | Health | 70 | 70 | 75 | 75
CZ09 | Kitchen | 70 | 60 | 75 | 85
CZ09 | Office | 70 | 60 | 75 | 85
CZ10 | Health | 70 | 70 | 75 | 75
CZ10 | Kitchen | 70 | 60 | 75 | 85
CZ10 | Office | 70 | 60 | 75 | 85
CZ11 | Health | 70 | 70 | 75 | 75
CZ11 | Kitchen | 70 | 60 | 75 | 85
CZ11 | Office | 70 | 60 | 75 | 85
CZ12 | Health | 70 | 70 | 75 | 75
CZ12 | Kitchen | 70 | 60 | 75 | 85
CZ12 | Office | 70 | 60 | 75 | 85
CZ13 | Health | 70 | 70 | 75 | 75
CZ13 | Kitchen | 70 | 60 | 75 | 85
CZ13 | Office | 70 | 60 | 75 | 85
CZ14 | Health | 70 | 70 | 75 | 75
CZ14 | Kitchen | 70 | 60 | 75 | 85
CZ14 | Office | 70 | 60 | 75 | 85
CZ15 | Health | 70 | 70 | 75 | 75
CZ15 | Kitchen | 70 | 60 | 75 | 85
CZ15 | Office | 70 | 60 | 75 | 85
CZ16 | Health | 70 | 70 | 75 | 75
CZ16 | Kitchen | 70 | 60 | 75 | 85
CZ16 | Office | 70 | 60 | 75 | 85

## HVAC System
HVAC system - Health/Medical - Hospital
Vintage | System Name | Category | Heating Type* | Cooling Type* | Air Distribution | Heating Efficiency | Cooling Efficiency | Note
Existing | cDXGF | Main | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.65
Existing | cDXGF | Alternative | Boiler (gas) | Chiller system | MZ-VAV | 0.8 | 2.87
Existing | cDXGF | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
New Construction | cDXGF | Main | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.65
New Construction | cDXGF | Alternative | Boiler (gas) | Chiller system | MZ-VAV | 0.8 | 2.87
New Construction | cDXGF | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
Existing | cDXHP | Main | DX-AIR | DX-AIR | SZ-CAV | 3.738 | 3.65
Existing | cDXHP | Alternative | Boiler (gas) | Chiller system | MZ-VAV | 0.8 | 2.87
Existing | cDXHP | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
New Construction | cDXHP | Main | DX-AIR | DX-AIR | SZ-CAV | 3.738 | 3.65
New Construction | cDXHP | Alternative | Boiler (gas) | Chiller system | MZ-VAV | 0.8 | 2.87
New Construction | cDXHP | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
Existing | cAVVG | Main | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Alternative | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.805 | 3.05
New Construction | cAVVG | Main | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Alternative | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.805 | 3.05
Existing | cDXOH | Main | None | DX-AIR | SZ-CAV | - | 3.65
Existing | cDXOH | Alternative | Boiler (gas) | Chiller system | MZ-VAV | 0.8 | 2.87
Existing | cDXOH | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
New Construction | cDXOH | Main | None | DX-AIR | SZ-CAV | - | 3.65
New Construction | cDXOH | Alternative | Boiler (gas) | Chiller system | MZ-VAV | 0.8 | 2.87
New Construction | cDXOH | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
Existing | cPVVG | Main | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.65
Existing | cPVVG | Alternative | Boiler (gas) | Chiller system | MZ-VAV | 0.8 | 2.87
Existing | cPVVG | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
New Construction | cPVVG | Main | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.65
New Construction | cPVVG | Alternative | Boiler (gas) | Chiller system | MZ-VAV | 0.8 | 2.87
New Construction | cPVVG | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
*DX Heating and cooling COPs are calculated based on coil-only input power and exclude fan power
Fan Power - Health/Medical - Hospital
Vintage | System Name | HVAC System Identifier | Fan System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm | Note
Existing | cAVVG | Main | MZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cAVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cAVVG | Main | MZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cAVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXGF | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXGF | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXGF | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXGF | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXGF | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXGF | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXHP | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXHP | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXHP | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXHP | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXHP | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXHP | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXOH | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXOH | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXOH | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXOH | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXOH | Main | SZ-CAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXOH | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cPVVG | Main | SZ-VAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cPVVG | Main | SZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cPVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cPVVG | Main | SZ-VAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cPVVG | Main | SZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cPVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7

## Raw_fanoverview (hidden)
Vintage | HVAC name | System type | HVAC System Identifier | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm
Existing | cAVVG | MZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cAVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cAVVG | MZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cAVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXGF | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXGF | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXGF | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXGF | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXGF | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXGF | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXHP | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXHP | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXHP | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXHP | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXHP | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXHP | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXOH | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXOH | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cDXOH | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXOH | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXOH | SZ-CAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cDXOH | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cPVVG | SZ-VAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cPVVG | SZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cPVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cPVVG | SZ-VAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cPVVG | SZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cPVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7

## Raw_hvac (hidden)
Vintage | System Name | HVAC System Identifier | Air Distribution | Heating Efficiency | Cooling Efficiency | Cooling Coil Type | Heating Coil Type
Existing | cAVVG | Main | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Alternative | MZ-VAV | 0.805 | 3.05 | WATER | WATER
Existing | cAVVG | Customized | SZ-CAV | 0.805 | 3.05 | WATER | WATER
New Construction | cAVVG | Main | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Alternative | MZ-VAV | 0.805 | 3.05 | WATER | WATER
New Construction | cAVVG | Customized | SZ-CAV | 0.805 | 3.05 | WATER | WATER
Existing | cDXGF | Main | SZ-CAV | 0.8 | 3.65
Existing | cDXGF | Alternative | MZ-VAV | 0.8 | 2.87 | WATER | WATER
Existing | cDXGF | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
New Construction | cDXGF | Main | SZ-CAV | 0.8 | 3.65
New Construction | cDXGF | Alternative | MZ-VAV | 0.8 | 2.87 | WATER | WATER
New Construction | cDXGF | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
Existing | cDXHP | Main | SZ-CAV | 3.738 | 3.65
Existing | cDXHP | Alternative | MZ-VAV | 0.8 | 2.87 | WATER | WATER
Existing | cDXHP | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
New Construction | cDXHP | Main | SZ-CAV | 3.738 | 3.65
New Construction | cDXHP | Alternative | MZ-VAV | 0.8 | 2.87 | WATER | WATER
New Construction | cDXHP | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
Existing | cDXOH | Main | SZ-CAV | - | 3.65
Existing | cDXOH | Alternative | MZ-VAV | 0.8 | 2.87 | WATER | WATER
Existing | cDXOH | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
New Construction | cDXOH | Main | SZ-CAV | - | 3.65
New Construction | cDXOH | Alternative | MZ-VAV | 0.8 | 2.87 | WATER | WATER
New Construction | cDXOH | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
Existing | cPVVG | Main | SZ-VAV | 0.8 | 3.65
Existing | cPVVG | Alternative | MZ-VAV | 0.8 | 2.87 | WATER | WATER
Existing | cPVVG | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
New Construction | cPVVG | Main | SZ-VAV | 0.8 | 3.65
New Construction | cPVVG | Alternative | MZ-VAV | 0.8 | 2.87 | WATER | WATER
New Construction | cPVVG | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER

## Ventilation
Outdoor Airflow Rate - Health/Medical - Hospital | [19 empty] | Zone Type
Zone Type | Floor area (ft²) | cfm/person | cfm/ft² | cfm | Notes | [14 empty] | Dining_fast
Dining_fast | 4121.72 | 0 | 0.5 | 2060.86 | [15 empty] | Health_operating
Health_operating | 58179.47 | 0 | 0.15 | 8726.9205 | [15 empty] | Health_patient
Health_patient | 94998.89 | 0 | 0.15 | 14249.8335 | [15 empty] | Kitchen
Kitchen | 1794.45 | 0 | 0.15 | 269.1675 | [15 empty] | Office
Office | 90915.59 | 0 | 0.15 | 13637.3385
OA Controller - Health/Medical - Hospital
Element | Vintage | Unit | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Notes
Economizer Maximum Limit Dry-Bulb Temperature | Existing | °F | 75 | 73 | 75 | 73 | 75 | 71 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 75 | 75 | 75
| New Construction | °F | 75 | 73 | 75 | 73 | 75 | 71 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 75 | 75 | 75
Exhaust hood - Health/Medical - Hospital
Type of Hood | Max Exhaust Flow Rate (cfm/ft) | Hood Length (ft) | Hood Exhaust Rate (cfm) | Note
- | - | - | -

## Raw_outdoorairflowrate (hidden)
Zone Type | Floor Area (ft2) | cfm/person | cfm/ft2
Dining_fast | 4121.72 | 0 | 0.5
Health_operating | 58179.47 | 0 | 0.15
Health_patient | 94998.89 | 0 | 0.15
Kitchen | 1794.45 | 0 | 0.15
Office | 90915.59 | 0 | 0.15

## Raw_oacontroller (hidden)
Climate Zone | Vintage | Economizer Maximum Limit Dry-Bulb Temperature (F)
CZ01 | Existing | 75
CZ02 | Existing | 73
CZ03 | Existing | 75
CZ04 | Existing | 73
CZ05 | Existing | 75
CZ06 | Existing | 71
CZ07 | Existing | 69
CZ08 | Existing | 71
CZ09 | Existing | 71
CZ10 | Existing | 73
CZ11 | Existing | 75
CZ12 | Existing | 75
CZ13 | Existing | 75
CZ14 | Existing | 75
CZ15 | Existing | 75
CZ16 | Existing | 75
CZ01 | New Construction | 75
CZ02 | New Construction | 73
CZ03 | New Construction | 75
CZ04 | New Construction | 73
CZ05 | New Construction | 75
CZ06 | New Construction | 71
CZ07 | New Construction | 69
CZ08 | New Construction | 71
CZ09 | New Construction | 71
CZ10 | New Construction | 73
CZ11 | New Construction | 75
CZ12 | New Construction | 75
CZ13 | New Construction | 75
CZ14 | New Construction | 75
CZ15 | New Construction | 75
CZ16 | New Construction | 75

## Water Heater
Water Heater - Health/Medical - Hospital
Vintage | Fuel type | Burner Efficiency | Maximum Heater Capacity (Btu/hr) | Tank Volume (gallon) | Tank Loss |  | Notes
[5 empty] | Off Cycle (W/K) | On Cycle (W/K)
Existing | Gas | 0.8 | 886513.84 | 185.92 | 1.6282 | 1.6282
New Construction | Gas | 0.8 | 886513.84 | 185.92 | 1.6282 | 1.6282
Peak Hot Water Consumption - Health/Medical - Hospital
Space | Floor Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Notes
DINING EL1 NORTH PERIM (G.N1) | 2362.68 | 33.33 | 2.7315 | 91.0419 | 1.5174
DINING EL1 SOUTH PERIM (G.S2) | 1759.04 | 33.33 | 2.0337 | 67.7817 | 1.1297
EL2 CORE PLNM ZN (G.C14) | 0 | 0 | 0 | 0 | 0
EL2 EAST PERIM PLNM ZN (G.E8) | 0 | 0 | 0 | 0 | 0
EL2 NNW PERIM PLNM ZN (G.NNW10) | 0 | 0 | 0 | 0 | 0
EL2 NORTH PERIM PLNM ZN (G.N13) | 0 | 0 | 0 | 0 | 0
EL2 SSW PERIM PLNM ZN (G.SSW9) | 0 | 0 | 0 | 0 | 0
EL2 SOUTH PERIM PLNM ZN (G.S12) | 0 | 0 | 0 | 0 | 0
EL2 WEST PERIM PLNM ZN (G.W11) | 0 | 0 | 0 | 0 | 0
EL3 CORE PLNM ZN (G.C16) | 0 | 0 | 0 | 0 | 0
EL3 CORE PLNM ZN (G.C16) ZN | 0 | 0 | 0 | 0 | 0
EL3 EAST PERIM PLNM ZN (G.E9) | 0 | 0 | 0 | 0 | 0
EL3 NORTH PERIM PLNM ZN (G.N11) | 0 | 0 | 0 | 0 | 0
EL3 NORTH PERIM PLNM ZN (G.N14) | 0 | 0 | 0 | 0 | 0
EL3 SOUTH PERIM PLNM ZN (G.S12) | 0 | 0 | 0 | 0 | 0
EL3 SOUTH PERIM PLNM ZN (G.S15) | 0 | 0 | 0 | 0 | 0
EL3 WEST PERIM PLNM ZN (G.W10) | 0 | 0 | 0 | 0 | 0
EL4 CORE PLNM ZN (G.C13) | 0 | 0 | 0 | 0 | 0
EL4 CORE PLNM ZN (G.C16) | 0 | 0 | 0 | 0 | 0
EL4 EAST PERIM PLNM ZN (G.E9) | 0 | 0 | 0 | 0 | 0
EL4 NORTH PERIM PLNM ZN (G.N11) | 0 | 0 | 0 | 0 | 0
EL4 NORTH PERIM PLNM ZN (G.N14) | 0 | 0 | 0 | 0 | 0
EL4 SOUTH PERIM PLNM ZN (G.S12) | 0 | 0 | 0 | 0 | 0
EL4 SOUTH PERIM PLNM ZN (G.S15) | 0 | 0 | 0 | 0 | 0
EL4 WEST PERIM PLNM ZN (G.W10) | 0 | 0 | 0 | 0 | 0
KITCHEN EL1 WEST PERIM (G.W3) | 1794.45 | 2.5 | 2.0741 | 5.1853 | 0.086422
OFFICE EL2 CORE (G.C7) | 44658.95 | 5 | 16.0772 | 80.3861 | 1.3398
OFFICE EL2 EAST PERIM (G.E1) | 5916.16 | 5 | 2.1298 | 10.6491 | 0.17748
OFFICE EL2 NORTH PERIM (G.N6) | 6002.38 | 5 | 2.1609 | 10.8043 | 0.18007
OFFICE EL2 SOUTH PERIM (G.S5) | 6002.38 | 5 | 2.1609 | 10.8043 | 0.18007
OFFICE EL3 CORE (G.C5) | 17669.76 | 5 | 6.3611 | 31.8056 | 0.53009
OFFICE EL3 NORTH PERIM (G.N3) | 2374.9 | 5 | 0.85496 | 4.2748 | 0.071247
OFFICE EL3 SOUTH PERIM (G.S4) | 2374.9 | 5 | 0.85496 | 4.2748 | 0.071247
OFFICE EL3 WEST PERIM (G.W2) | 5916.16 | 5 | 2.1298 | 10.6491 | 0.17748
PATIENTROOM EL3 CORE (G.C8) | 38685.73 | 5 | 18.5692 | 92.8458 | 1.5474
PATIENTROOM EL3 EAST PERIM (G.E1) | 5916.16 | 5 | 0 | 0 | 0
PATIENTROOM EL3 NORTH PERIM (G.N6) | 5199.55 | 5 | 0 | 0 | 0
PATIENTROOM EL3 SOUTH PERIM (G.S7) | 5199.55 | 5 | 2.4958 | 12.4789 | 0.20798
PATIENTROOM EL4 CORE (G.C5) | 26861.2 | 5 | 0 | 0 | 0
PATIENTROOM EL4 NORTH PERIM (G.N3) | 3610.27 | 5 | 0 | 0 | 0
PATIENTROOM EL4 SOUTH PERIM (G.S4) | 3610.27 | 5 | 0 | 0 | 0
PATIENTROOM EL4 WEST PERIM (G.W2) | 5916.16 | 5 | 0 | 0 | 0
SURGERY EL2 NNW PERIM (G.NNW3) | 1572.07 | 5 | 0.75459 | 3.773 | 0.062883
SURGERY EL2 SSW PERIM (G.SSW2) | 1572.07 | 5 | 0.75459 | 3.773 | 0.062883
SURGERY EL2 WEST PERIM (G.W4) | 11696.54 | 5 | 5.6143 | 28.0717 | 0.46786
SURGERY EL4 CORE (G.C8) | 29494.29 | 5 | 0 | 0 | 0
SURGERY EL4 EAST PERIM (G.E1) | 5916.16 | 5 | 0 | 0 | 0
SURGERY EL4 NORTH PERIM (G.N6) | 3964.17 | 5 | 0 | 0 | 0
SURGERY EL4 SOUTH PERIM (G.S7) | 3964.17 | 5 | 0 | 0 | 0
Total (49 Space)

## Raw_waterheater (hidden)
Vintage | Burner Efficiency | Maximum Heater Capacity (Btu/h) | Tank Volume (ft3) | Tank Loss_Off Cycle (W/K) | Tank Loss_On Cycle (W/K)
Existing | 0.8 | 886513.84 | 185.92 | 1.6282 | 1.6282
New Construction | 0.8 | 886513.84 | 185.92 | 1.6282 | 1.6282

## Raw_dhwpeakflowbyzone (hidden)
Space | Peak hot water usage (gal/hr) | Zone Name
Dining EL1 North Perim (G.N1) | 91.0419 | DINING EL1 NORTH PERIM (G.N1)
Dining EL1 South Perim (G.S2) | 67.7817 | DINING EL1 SOUTH PERIM (G.S2)
Kitchen EL1 West Perim (G.W3) | 5.1853 | KITCHEN EL1 WEST PERIM (G.W3)
Office EL2 Core (G.C7) | 80.3861 | OFFICE EL2 CORE (G.C7)
Office EL2 East Perim (G.E1) | 10.6491 | OFFICE EL2 EAST PERIM (G.E1)
Office EL2 North Perim (G.N6) | 10.8043 | OFFICE EL2 NORTH PERIM (G.N6)
Office EL2 South Perim (G.S5) | 10.8043 | OFFICE EL2 SOUTH PERIM (G.S5)
Office EL3 Core (G.C5) | 31.8056 | OFFICE EL3 CORE (G.C5)
Office EL3 North Perim (G.N3) | 4.2748 | OFFICE EL3 NORTH PERIM (G.N3)
Office EL3 South Perim (G.S4) | 4.2748 | OFFICE EL3 SOUTH PERIM (G.S4)
Office EL3 West Perim (G.W2) | 10.6491 | OFFICE EL3 WEST PERIM (G.W2)
PatientRoom EL3 Core (G.C8) | 92.8458 | PATIENTROOM EL3 CORE (G.C8)
PatientRoom EL3 East Perim (G.E1) | 14.1988 | OFFICE EL2 EAST PERIM (G.E1)
PatientRoom EL3 North Perim (G.N6) | 12.4789 | OFFICE EL2 NORTH PERIM (G.N6)
PatientRoom EL3 South Perim (G.S7) | 12.4789 | PATIENTROOM EL3 SOUTH PERIM (G.S7)
PatientRoom EL4 Core (G.C5) | 64.4669 | OFFICE EL3 CORE (G.C5)
PatientRoom EL4 North Perim (G.N3) | 8.6646 | OFFICE EL3 NORTH PERIM (G.N3)
PatientRoom EL4 South Perim (G.S4) | 8.6646 | OFFICE EL3 SOUTH PERIM (G.S4)
PatientRoom EL4 West Perim (G.W2) | 14.1988 | OFFICE EL3 WEST PERIM (G.W2)
Surgery EL2 NNW Perim (G.NNW3) | 3.773 | SURGERY EL2 NNW PERIM (G.NNW3)
Surgery EL2 SSW Perim (G.SSW2) | 3.773 | SURGERY EL2 SSW PERIM (G.SSW2)
Surgery EL2 West Perim (G.W4) | 28.0717 | SURGERY EL2 WEST PERIM (G.W4)
Surgery EL4 Core (G.C8) | 70.7863 | PATIENTROOM EL3 CORE (G.C8)
Surgery EL4 East Perim (G.E1) | 14.1988 | OFFICE EL2 EAST PERIM (G.E1)
Surgery EL4 North Perim (G.N6) | 9.514 | OFFICE EL2 NORTH PERIM (G.N6)
Surgery EL4 South Perim (G.S7) | 9.514 | PATIENTROOM EL3 SOUTH PERIM (G.S7)

## Interior Lights
Interior Lighting - Health/Medical - Hospital
Vintage | Method | Zone type | Floor area (ft²) | Lighting Power Density (Watts/ft²) | Additional Lighting Power for Portable Lighting (Watts/ft²) | Technology | Notes
Existing | Space by space | Dining_fast | 4121.72 | 1.2136 | NA | NA
Existing | Space by space | Health_operating | 58179.47 | 1.3416 | NA | NA
Existing | Space by space | Health_patient | 94998.89 | 1.302 | NA | NA
Existing | Space by space | Kitchen | 1794.45 | 1.6492 | NA | NA
Existing | Space by space | Office | 90915.59 | 1.2504 | NA | NA
New Construction | Space by space | Dining_fast | 4121.72 | 0.44995 | NA | NA
New Construction | Space by space | Health_operating | 58179.47 | 1.8997 | NA | NA
New Construction | Space by space | Health_patient | 94998.89 | 0.69991 | NA | NA
New Construction | Space by space | Kitchen | 1794.45 | 0.94987 | NA | NA
New Construction | Space by space | Office | 90915.59 | 0.59992 | NA | NA

## Ext Lighting
Exterior Lighting - Health/Medical - Hospital
Vintage | Non-Motion Controlled Luminaires (W) | Motion-Controlled Luminaires (W) | Total (W) | Notes
Existing | NA | NA | NA
New Consturction | NA | NA | NA

## Raw_interiorlights (hidden)
Vintage | Zone Type | Floor Area (ft2) | Lighting Power Density(W/ft2)
Existing | Dining_fast | 4121.72 | 1.2136
Existing | Health_operating | 58179.47 | 1.3416
Existing | Health_patient | 94998.89 | 1.302
Existing | Kitchen | 1794.45 | 1.6492
Existing | Office | 90915.59 | 1.2504
New Construction | Dining_fast | 4121.72 | 0.44995
New Construction | Health_operating | 58179.47 | 1.8997
New Construction | Health_patient | 94998.89 | 0.69991
New Construction | Kitchen | 1794.45 | 0.94987
New Construction | Office | 90915.59 | 0.59992

## Equipment
Equipment - Health/Medical - Hospital
Zone Type | Floor Area (ft²) | Plug Load Intensity (W/ft²) | Gas Power Density (Btu/hr-ft²)
Dining_fast | 4121.72 | 0.74991 | 0
Health_operating | 58179.47 | 1.4998 | 0
Health_patient | 94998.89 | 1.4998 | 0
Kitchen | 1794.45 | 7.7581 | 17.5354
Office | 90915.59 | 1.4998 | 0
Refrigeration - Health/Medical - Hospital
Refrigeration System Name | Condenser Fan Power | Refrigeration System Working Fluid | Condenser Type
Elevator - Health/Medical - Hospital
Vintage | No. of Elevators | Cab Lighting Power Limit | Lighting Shutoff | Cab Fan Control | Fan Power Limit | Regenerative Drive Threshold | Design load (W) | Note
Existing | - | - | - | - | - | - | -
New Construction | - | - | - | - | - | - | -

## Raw_equipment (hidden)
Vintage | Zone Type | Floor Area (ft2) | Plug Load Intensity (W/ft2)
Existing | Dining_fast | 4121.72 | 0.74991
Existing | Health_operating | 58179.47 | 1.4998
Existing | Health_patient | 94998.89 | 1.4998
Existing | Kitchen | 1794.45 | 7.7581
Existing | Office | 90915.59 | 1.4998
New Construction | Dining_fast | 4121.72 | 0.74991
New Construction | Health_operating | 58179.47 | 1.4998
New Construction | Health_patient | 94998.89 | 1.4998
New Construction | Kitchen | 1794.45 | 7.7581
New Construction | Office | 90915.59 | 1.4998

## Raw_gasequipment (hidden)
Vintage | Zone Name | Gas Loads (Btu/h-ft2) | Zone Type
Existing | Kitchen EL1 West Perim (G.W3) | 17.5354 | Kitchen
New Construction | Kitchen EL1 West Perim (G.W3) | 17.5354 | Kitchen

## Raw_refrigerationsystem (hidden)
Vintage | Refrigeration System Name | Condenser Fan Power | Working fluid | Condenser Type
No refrigeration system was found

## Schedules
Schedule by Hour - Health/Medical - Hospital
Schedule Identifier | Space type | Type | Notes | Hour
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Cooling Setpoint Schedule | Health | AllDays | Cooling/Heating setpoints are in °F; others are intensity (0–100%) | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | Health | AllOtherDays |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
DHW Sch | Health | Saturdays |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
DHW Sch | Health | Weekdays |  | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.01 | 0.01 | 0.01
Elec Equip Sch | Health | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | Health | Saturdays |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Elec Equip Sch | Health | Weekdays |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Heating Setpoint Schedule | Health | AllDays |  | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | Health | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Health | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Health | Saturdays |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Lighting Schedule | Health | Weekdays |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.45 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
OA Schedule | Health | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | Health | Saturdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OA Schedule | Health | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Occupant Sch | Health | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Health | Saturdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Health | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
Cooling Setpoint Schedule | Kitchen | AllOtherDays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Cooling Setpoint Schedule | Kitchen | Saturdays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Cooling Setpoint Schedule | Kitchen | Weekdays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | Kitchen | AllOtherDays |  | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
DHW Sch | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
DHW Sch | Kitchen | Weekdays |  | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
Elec Equip Sch | Kitchen | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | Kitchen | AllOtherDays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Elec Equip Sch | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Elec Equip Sch | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Heating Setpoint Schedule | Kitchen | AllOtherDays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Heating Setpoint Schedule | Kitchen | Saturdays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Heating Setpoint Schedule | Kitchen | Weekdays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | Kitchen | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Kitchen | AllOtherDays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
Lighting Schedule | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Lighting Schedule | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
OA Schedule | Kitchen | AllOtherDays |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OA Schedule | Kitchen | Saturdays |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OA Schedule | Kitchen | Weekdays |  | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Occupant Sch | Kitchen | AllOtherDays |  | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Occupant Sch | Kitchen | Saturdays |  | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
Occupant Sch | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Cooling Setpoint Schedule | Office | AllOtherDays |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | Office | Saturday |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | Office | Weekdays |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | Office | AllOtherDays |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
DHW Sch | Office | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
DHW Sch | Office | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
Elec Equip Sch | Office | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | Office | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | Office | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | Office | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Heating Setpoint Schedule | Office | AllOtherDays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | Office | Saturday |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | Office | Weekdays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | Office | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Office | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Office | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Office | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OA Schedule | Office | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | Office | Saturday |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OA Schedule | Office | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Occupant Sch | Office | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Office | Saturday |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Office | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
Infiltration Schedule | Plenum | AllDays | bar: Hour 1 to Hour 24

## Schedule_Figures
Schedule Figures (linked to Schedules tab)

## Raw_schedule (hidden)
Schedule Identifier | Schedule Name | Type | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Health | Cooling Setpoint Schedule | AllDays | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Health | DHW Sch | AllOtherDays | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Health | DHW Sch | Saturdays | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
Health | DHW Sch | Weekdays | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.01 | 0.01 | 0.01
Health | Elec Equip Sch | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Health | Elec Equip Sch | Saturdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Health | Elec Equip Sch | Weekdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Health | Heating Setpoint Schedule | AllDays | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Health | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Health | Lighting Schedule | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Health | Lighting Schedule | Saturdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Health | Lighting Schedule | Weekdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.45 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Health | OA Schedule | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health | OA Schedule | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Health | OA Schedule | Weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Health | Occupant Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health | Occupant Sch | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Health | Occupant Sch | Weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
Kitchen | Cooling Setpoint Schedule | AllOtherDays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | Cooling Setpoint Schedule | Saturdays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | Cooling Setpoint Schedule | Weekdays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | DHW Sch | AllOtherDays | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Kitchen | DHW Sch | Saturdays | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
Kitchen | DHW Sch | Weekdays | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
Kitchen | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Elec Equip Sch | AllOtherDays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Kitchen | Elec Equip Sch | Saturdays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Kitchen | Elec Equip Sch | Weekdays | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Kitchen | Heating Setpoint Schedule | AllOtherDays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Heating Setpoint Schedule | Saturdays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Heating Setpoint Schedule | Weekdays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Lighting Schedule | AllOtherDays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
Kitchen | Lighting Schedule | Saturdays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Kitchen | Lighting Schedule | Weekdays | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Kitchen | OA Schedule | AllOtherDays | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | OA Schedule | Saturdays | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | OA Schedule | Weekdays | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Occupant Sch | AllOtherDays | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Kitchen | Occupant Sch | Saturdays | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
Kitchen | Occupant Sch | Weekdays | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Office | Cooling Setpoint Schedule | AllOtherDays | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Office | Cooling Setpoint Schedule | Saturday | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Office | Cooling Setpoint Schedule | Weekdays | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Office | DHW Sch | AllOtherDays | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Office | DHW Sch | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
Office | DHW Sch | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
Office | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Elec Equip Sch | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Elec Equip Sch | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Elec Equip Sch | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Office | Heating Setpoint Schedule | AllOtherDays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Office | Heating Setpoint Schedule | Saturday | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Office | Heating Setpoint Schedule | Weekdays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Office | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Lighting Schedule | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Lighting Schedule | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Lighting Schedule | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Office | OA Schedule | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office | OA Schedule | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Office | OA Schedule | Weekdays | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Occupant Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Office | Occupant Sch | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
Office | Occupant Sch | Weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
Plenum | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## Energy Usage
Energy Consumption - Health/Medical - Hospital
Climate Zone | HVAC Type | Vintage | Total Floorspace (Excluding Plenums and Crawl Space) (ft²) | Annual Electricity Intensity (kBtu/ft²) | Annual Gas Intensity (kBtu/ft²) | Notes
CZ01 | cAVVG | Existing | 250010.12 | 30.7031 | 9.8239
CZ01 | cAVVG | New Construction | 250010.12 | 27.1678 | 9.3578
CZ01 | cDXGF | Existing | 250010.12 | 34.5083 | 9.0078
CZ01 | cDXGF | New Construction | 250010.12 | 30.1316 | 8.3698
CZ01 | cDXHP | Existing | 250010.12 | 34.6519 | 8.4332
CZ01 | cDXHP | New Construction | 250010.12 | 30.298 | 7.6959
CZ01 | cDXOH | Existing | 250010.12 | 34.5007 | 8.5277
CZ01 | cDXOH | New Construction | 250010.12 | 30.1182 | 7.8257
CZ01 | cPVVG | Existing | 250010.12 | 32.5104 | 9.4452
CZ01 | cPVVG | New Construction | 250010.12 | 28.48 | 8.805
CZ02 | cAVVG | Existing | 250010.12 | 35.7604 | 9.3299
CZ02 | cAVVG | New Construction | 250010.12 | 31.5009 | 11.2013
CZ02 | cDXGF | Existing | 250010.12 | 41.9815 | 8.5351
CZ02 | cDXGF | New Construction | 250010.12 | 36.8534 | 9.9308
CZ02 | cDXHP | Existing | 250010.12 | 42.1052 | 8.0904
CZ02 | cDXHP | New Construction | 250010.12 | 37.0753 | 9.1266
CZ02 | cDXOH | Existing | 250010.12 | 41.9713 | 8.1518
CZ02 | cDXOH | New Construction | 250010.12 | 36.846 | 9.214
CZ02 | cPVVG | Existing | 250010.12 | 39.8492 | 8.9068
CZ02 | cPVVG | New Construction | 250010.12 | 34.8354 | 10.4723
CZ03 | cAVVG | Existing | 250010.12 | 33.3229 | 7.3303
CZ03 | cAVVG | New Construction | 250010.12 | 29.2843 | 9.0111
CZ03 | cDXGF | Existing | 250010.12 | 38.9441 | 6.8542
CZ03 | cDXGF | New Construction | 250010.12 | 34.2748 | 8.1396
CZ03 | cDXHP | Existing | 250010.12 | 39.0019 | 6.6102
CZ03 | cDXHP | New Construction | 250010.12 | 34.389 | 7.6691
CZ03 | cDXOH | Existing | 250010.12 | 38.9377 | 6.6413
CZ03 | cDXOH | New Construction | 250010.12 | 34.2672 | 7.7133
CZ03 | cPVVG | Existing | 250010.12 | 36.8996 | 7.0943
CZ03 | cPVVG | New Construction | 250010.12 | 32.3576 | 8.5264
CZ04 | cAVVG | Existing | 250010.12 | 36.7448 | 7.2238
CZ04 | cAVVG | New Construction | 250010.12 | 32.3705 | 8.6624
CZ04 | cDXGF | Existing | 250010.12 | 43.0379 | 6.7004
CZ04 | cDXGF | New Construction | 250010.12 | 37.97 | 7.7889
CZ04 | cDXHP | Existing | 250010.12 | 43.0912 | 6.4793
CZ04 | cDXHP | New Construction | 250010.12 | 38.0677 | 7.3886
CZ04 | cDXOH | Existing | 250010.12 | 43.0326 | 6.5054
CZ04 | cDXOH | New Construction | 250010.12 | 37.9606 | 7.4242
CZ04 | cPVVG | Existing | 250010.12 | 40.9243 | 6.9321
CZ04 | cPVVG | New Construction | 250010.12 | 35.965 | 8.1451
CZ05 | cAVVG | Existing | 250010.12 | 34.26 | 7.4123
CZ05 | cAVVG | New Construction | 250010.12 | 30.087 | 9.1384
CZ05 | cDXGF | Existing | 250010.12 | 40.1014 | 6.9478
CZ05 | cDXGF | New Construction | 250010.12 | 35.1964 | 8.2925
CZ05 | cDXHP | Existing | 250010.12 | 40.1653 | 6.7004
CZ05 | cDXHP | New Construction | 250010.12 | 35.3217 | 7.8087
CZ05 | cDXOH | Existing | 250010.12 | 40.0975 | 6.7309
CZ05 | cDXOH | New Construction | 250010.12 | 35.1855 | 7.8497
CZ05 | cPVVG | Existing | 250010.12 | 38.0749 | 7.1728
CZ05 | cPVVG | New Construction | 250010.12 | 33.3119 | 8.6657
CZ06 | cAVVG | Existing | 250010.12 | 37.3673 | 4.9663
CZ06 | cAVVG | New Construction | 250010.12 | 32.6634 | 5.7558
CZ06 | cDXGF | Existing | 250010.12 | 44.2628 | 4.8035
CZ06 | cDXGF | New Construction | 250010.12 | 38.7229 | 5.4176
CZ06 | cDXHP | Existing | 250010.12 | 44.2393 | 4.7619
CZ06 | cDXHP | New Construction | 250010.12 | 38.7111 | 5.3262
CZ06 | cDXOH | Existing | 250010.12 | 44.2617 | 4.7649
CZ06 | cDXOH | New Construction | 250010.12 | 38.7201 | 5.3318
CZ06 | cPVVG | Existing | 250010.12 | 42.3253 | 4.8719
CZ06 | cPVVG | New Construction | 250010.12 | 36.8907 | 5.5431
CZ07 | cAVVG | Existing | 250010.12 | 38.2897 | 5.042
CZ07 | cAVVG | New Construction | 250010.12 | 33.5223 | 5.7408
CZ07 | cDXGF | Existing | 250010.12 | 45.3564 | 4.8097
CZ07 | cDXGF | New Construction | 250010.12 | 39.572 | 5.3015
CZ07 | cDXHP | Existing | 250010.12 | 45.3434 | 4.7693
CZ07 | cDXHP | New Construction | 250010.12 | 39.5672 | 5.222
CZ07 | cDXOH | Existing | 250010.12 | 45.3553 | 4.7725
CZ07 | cDXOH | New Construction | 250010.12 | 39.5699 | 5.227
CZ07 | cPVVG | Existing | 250010.12 | 43.3827 | 4.8734
CZ07 | cPVVG | New Construction | 250010.12 | 37.7392 | 5.4111
CZ08 | cAVVG | Existing | 250010.12 | 39.7675 | 5.5167
CZ08 | cAVVG | New Construction | 250010.12 | 34.9714 | 6.4545
CZ08 | cDXGF | Existing | 250010.12 | 47.0667 | 5.248
CZ08 | cDXGF | New Construction | 250010.12 | 41.3745 | 5.9113
CZ08 | cDXHP | Existing | 250010.12 | 47.0678 | 5.1836
CZ08 | cDXHP | New Construction | 250010.12 | 41.3917 | 5.7812
CZ08 | cDXOH | Existing | 250010.12 | 47.0647 | 5.1897
CZ08 | cDXOH | New Construction | 250010.12 | 41.37 | 5.7899
CZ08 | cPVVG | Existing | 250010.12 | 45.0306 | 5.3375
CZ08 | cPVVG | New Construction | 250010.12 | 39.422 | 6.0692
CZ09 | cAVVG | Existing | 250010.12 | 41.3771 | 5.4955
CZ09 | cAVVG | New Construction | 250010.12 | 36.3878 | 6.3283
CZ09 | cDXGF | Existing | 250010.12 | 48.8328 | 5.2066
CZ09 | cDXGF | New Construction | 250010.12 | 43.0018 | 5.7682
CZ09 | cDXHP | Existing | 250010.12 | 48.8295 | 5.161
CZ09 | cDXHP | New Construction | 250010.12 | 43.0096 | 5.6747
CZ09 | cDXOH | Existing | 250010.12 | 48.8314 | 5.1649
CZ09 | cDXOH | New Construction | 250010.12 | 42.9991 | 5.6813
CZ09 | cPVVG | Existing | 250010.12 | 46.7407 | 5.2865
CZ09 | cPVVG | New Construction | 250010.12 | 40.9852 | 5.909
CZ10 | cAVVG | Existing | 250010.12 | 44.1286 | 7.4747
CZ10 | cAVVG | New Construction | 250010.12 | 38.5982 | 8.103
CZ10 | cDXGF | Existing | 250010.12 | 51.8062 | 6.7384
CZ10 | cDXGF | New Construction | 250010.12 | 45.4654 | 7.0515
CZ10 | cDXHP | Existing | 250010.12 | 51.856 | 6.5602
CZ10 | cDXHP | New Construction | 250010.12 | 45.5444 | 6.768
CZ10 | cDXOH | Existing | 250010.12 | 51.8012 | 6.5803
CZ10 | cDXOH | New Construction | 250010.12 | 45.4554 | 6.7926
CZ10 | cPVVG | Existing | 250010.12 | 49.5471 | 6.9316
CZ10 | cPVVG | New Construction | 250010.12 | 43.3682 | 7.3115
CZ11 | cAVVG | Existing | 250010.12 | 43.2149 | 9.6541
CZ11 | cAVVG | New Construction | 250010.12 | 36.318 | 7.4519
CZ11 | cDXGF | Existing | 250010.12 | 51.0301 | 8.5249
CZ11 | cDXGF | New Construction | 250010.12 | 42.7196 | 6.7899
CZ11 | cDXHP | Existing | 250010.12 | 51.1597 | 8.1333
CZ11 | cDXHP | New Construction | 250010.12 | 42.8393 | 6.4254
CZ11 | cDXOH | Existing | 250010.12 | 51.0238 | 8.1888
CZ11 | cDXOH | New Construction | 250010.12 | 42.7138 | 6.5062
CZ11 | cPVVG | Existing | 250010.12 | 48.883 | 8.8957
CZ11 | cPVVG | New Construction | 250010.12 | 41.0937 | 7.0889
CZ12 | cAVVG | Existing | 250010.12 | 40.9308 | 9.1135
CZ12 | cAVVG | New Construction | 250010.12 | 34.9081 | 7.6897
CZ12 | cDXGF | Existing | 250010.12 | 48.554 | 8.2257
CZ12 | cDXGF | New Construction | 250010.12 | 41.1355 | 7.0082
CZ12 | cDXHP | Existing | 250010.12 | 48.6755 | 7.8356
CZ12 | cDXHP | New Construction | 250010.12 | 41.2603 | 6.5915
CZ12 | cDXOH | Existing | 250010.12 | 48.5458 | 7.8905
CZ12 | cDXOH | New Construction | 250010.12 | 41.1209 | 6.6784
CZ12 | cPVVG | Existing | 250010.12 | 46.4737 | 8.5676
CZ12 | cPVVG | New Construction | 250010.12 | 39.4779 | 7.3073
CZ13 | cAVVG | Existing | 250010.12 | 44.3859 | 8.3554
CZ13 | cAVVG | New Construction | 250010.12 | 37.4133 | 6.807
CZ13 | cDXGF | Existing | 250010.12 | 52.4805 | 7.367
CZ13 | cDXGF | New Construction | 250010.12 | 44.0659 | 6.2451
CZ13 | cDXHP | Existing | 250010.12 | 52.5684 | 7.0885
CZ13 | cDXHP | New Construction | 250010.12 | 44.154 | 5.9525
CZ13 | cDXOH | Existing | 250010.12 | 52.4768 | 7.1354
CZ13 | cDXOH | New Construction | 250010.12 | 44.0573 | 6.0096
CZ13 | cPVVG | Existing | 250010.12 | 50.3798 | 7.6575
CZ13 | cPVVG | New Construction | 250010.12 | 42.4269 | 6.4821
CZ14 | cAVVG | Existing | 250010.12 | 48.2134 | 7.0732
CZ14 | cAVVG | New Construction | 250010.12 | 40.5089 | 6.111
CZ14 | cDXGF | Existing | 250010.12 | 56.2088 | 6.3666
CZ14 | cDXGF | New Construction | 250010.12 | 47.0816 | 5.6819
CZ14 | cDXHP | Existing | 250010.12 | 56.2708 | 6.2014
CZ14 | cDXHP | New Construction | 250010.12 | 47.148 | 5.4913
CZ14 | cDXOH | Existing | 250010.12 | 56.2043 | 6.2249
CZ14 | cDXOH | New Construction | 250010.12 | 47.0757 | 5.5192
CZ14 | cPVVG | Existing | 250010.12 | 54.0645 | 6.5545
CZ14 | cPVVG | New Construction | 250010.12 | 45.4029 | 5.8454
CZ15 | cAVVG | Existing | 250010.12 | 53.716 | 6.4684
CZ15 | cAVVG | New Construction | 250010.12 | 44.9627 | 5.5386
CZ15 | cDXGF | Existing | 250010.12 | 62.0978 | 5.4389
CZ15 | cDXGF | New Construction | 250010.12 | 51.9415 | 5.0865
CZ15 | cDXHP | Existing | 250010.12 | 62.1108 | 5.3937
CZ15 | cDXHP | New Construction | 250010.12 | 51.9576 | 5.0283
CZ15 | cDXOH | Existing | 250010.12 | 62.0955 | 5.3966
CZ15 | cDXOH | New Construction | 250010.12 | 51.935 | 5.0317
CZ15 | cPVVG | Existing | 250010.12 | 60.1354 | 5.5023
CZ15 | cPVVG | New Construction | 250010.12 | 50.425 | 5.1443
CZ16 | cAVVG | Existing | 250010.12 | 43.6472 | 11.3726
CZ16 | cAVVG | New Construction | 250010.12 | 36.6824 | 9.2461
CZ16 | cDXGF | Existing | 250010.12 | 52.4091 | 10.2151
CZ16 | cDXGF | New Construction | 250010.12 | 43.9071 | 8.2521
CZ16 | cDXHP | Existing | 250010.12 | 52.6662 | 9.5716
CZ16 | cDXHP | New Construction | 250010.12 | 44.1863 | 7.5482
CZ16 | cDXOH | Existing | 250010.12 | 52.4032 | 9.6669
CZ16 | cDXOH | New Construction | 250010.12 | 43.8879 | 7.6925
CZ16 | cPVVG | Existing | 250010.12 | 50.1226 | 10.7207
CZ16 | cPVVG | New Construction | 250010.12 | 42.0874 | 8.7002

## Energy Usage_Figures
Energy Figures (from 'Energy Usage' Tab)
cAVVG ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cAVVG ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 30.7031 | 27.1678 | CZ01 | 9.8239 | 9.3578
CZ02 | 35.7604 | 31.5009 | CZ02 | 9.3299 | 11.2013
CZ03 | 33.3229 | 29.2843 | CZ03 | 7.3303 | 9.0111
CZ04 | 36.7448 | 32.3705 | CZ04 | 7.2238 | 8.6624
CZ05 | 34.26 | 30.087 | CZ05 | 7.4123 | 9.1384
CZ06 | 37.3673 | 32.6634 | CZ06 | 4.9663 | 5.7558
CZ07 | 38.2897 | 33.5223 | CZ07 | 5.042 | 5.7408
CZ08 | 39.7675 | 34.9714 | CZ08 | 5.5167 | 6.4545
CZ09 | 41.3771 | 36.3878 | CZ09 | 5.4955 | 6.3283
CZ10 | 44.1286 | 38.5982 | CZ10 | 7.4747 | 8.103
CZ11 | 43.2149 | 36.318 | CZ11 | 9.6541 | 7.4519
CZ12 | 40.9308 | 34.9081 | CZ12 | 9.1135 | 7.6897
CZ13 | 44.3859 | 37.4133 | CZ13 | 8.3554 | 6.807
CZ14 | 48.2134 | 40.5089 | CZ14 | 7.0732 | 6.111
CZ15 | 53.716 | 44.9627 | CZ15 | 6.4684 | 5.5386
CZ16 | 43.6472 | 36.6824 | CZ16 | 11.3726 | 9.2461
cDXGF ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXGF ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 34.5083 | 30.1316 | CZ01 | 9.0078 | 8.3698
CZ02 | 41.9815 | 36.8534 | CZ02 | 8.5351 | 9.9308
CZ03 | 38.9441 | 34.2748 | CZ03 | 6.8542 | 8.1396
CZ04 | 43.0379 | 37.97 | CZ04 | 6.7004 | 7.7889
CZ05 | 40.1014 | 35.1964 | CZ05 | 6.9478 | 8.2925
CZ06 | 44.2628 | 38.7229 | CZ06 | 4.8035 | 5.4176
CZ07 | 45.3564 | 39.572 | CZ07 | 4.8097 | 5.3015
CZ08 | 47.0667 | 41.3745 | CZ08 | 5.248 | 5.9113
CZ09 | 48.8328 | 43.0018 | CZ09 | 5.2066 | 5.7682
CZ10 | 51.8062 | 45.4654 | CZ10 | 6.7384 | 7.0515
CZ11 | 51.0301 | 42.7196 | CZ11 | 8.5249 | 6.7899
CZ12 | 48.554 | 41.1355 | CZ12 | 8.2257 | 7.0082
CZ13 | 52.4805 | 44.0659 | CZ13 | 7.367 | 6.2451
CZ14 | 56.2088 | 47.0816 | CZ14 | 6.3666 | 5.6819
CZ15 | 62.0978 | 51.9415 | CZ15 | 5.4389 | 5.0865
CZ16 | 52.4091 | 43.9071 | CZ16 | 10.2151 | 8.2521
cDXHP ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXHP ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 34.6519 | 30.298 | CZ01 | 8.4332 | 7.6959
CZ02 | 42.1052 | 37.0753 | CZ02 | 8.0904 | 9.1266
CZ03 | 39.0019 | 34.389 | CZ03 | 6.6102 | 7.6691
CZ04 | 43.0912 | 38.0677 | CZ04 | 6.4793 | 7.3886
CZ05 | 40.1653 | 35.3217 | CZ05 | 6.7004 | 7.8087
CZ06 | 44.2393 | 38.7111 | CZ06 | 4.7619 | 5.3262
CZ07 | 45.3434 | 39.5672 | CZ07 | 4.7693 | 5.222
CZ08 | 47.0678 | 41.3917 | CZ08 | 5.1836 | 5.7812
CZ09 | 48.8295 | 43.0096 | CZ09 | 5.161 | 5.6747
CZ10 | 51.856 | 45.5444 | CZ10 | 6.5602 | 6.768
CZ11 | 51.1597 | 42.8393 | CZ11 | 8.1333 | 6.4254
CZ12 | 48.6755 | 41.2603 | CZ12 | 7.8356 | 6.5915
CZ13 | 52.5684 | 44.154 | CZ13 | 7.0885 | 5.9525
CZ14 | 56.2708 | 47.148 | CZ14 | 6.2014 | 5.4913
CZ15 | 62.1108 | 51.9576 | CZ15 | 5.3937 | 5.0283
CZ16 | 52.6662 | 44.1863 | CZ16 | 9.5716 | 7.5482
cDXOH ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXOH ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 34.5007 | 30.1182 | CZ01 | 8.5277 | 7.8257
CZ02 | 41.9713 | 36.846 | CZ02 | 8.1518 | 9.214
CZ03 | 38.9377 | 34.2672 | CZ03 | 6.6413 | 7.7133
CZ04 | 43.0326 | 37.9606 | CZ04 | 6.5054 | 7.4242
CZ05 | 40.0975 | 35.1855 | CZ05 | 6.7309 | 7.8497
CZ06 | 44.2617 | 38.7201 | CZ06 | 4.7649 | 5.3318
CZ07 | 45.3553 | 39.5699 | CZ07 | 4.7725 | 5.227
CZ08 | 47.0647 | 41.37 | CZ08 | 5.1897 | 5.7899
CZ09 | 48.8314 | 42.9991 | CZ09 | 5.1649 | 5.6813
CZ10 | 51.8012 | 45.4554 | CZ10 | 6.5803 | 6.7926
CZ11 | 51.0238 | 42.7138 | CZ11 | 8.1888 | 6.5062
CZ12 | 48.5458 | 41.1209 | CZ12 | 7.8905 | 6.6784
CZ13 | 52.4768 | 44.0573 | CZ13 | 7.1354 | 6.0096
CZ14 | 56.2043 | 47.0757 | CZ14 | 6.2249 | 5.5192
CZ15 | 62.0955 | 51.935 | CZ15 | 5.3966 | 5.0317
CZ16 | 52.4032 | 43.8879 | CZ16 | 9.6669 | 7.6925
cPVVG ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cPVVG ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 32.5104 | 28.48 | CZ01 | 9.4452 | 8.805
CZ02 | 39.8492 | 34.8354 | CZ02 | 8.9068 | 10.4723
CZ03 | 36.8996 | 32.3576 | CZ03 | 7.0943 | 8.5264
CZ04 | 40.9243 | 35.965 | CZ04 | 6.9321 | 8.1451
CZ05 | 38.0749 | 33.3119 | CZ05 | 7.1728 | 8.6657
CZ06 | 42.3253 | 36.8907 | CZ06 | 4.8719 | 5.5431
CZ07 | 43.3827 | 37.7392 | CZ07 | 4.8734 | 5.4111
CZ08 | 45.0306 | 39.422 | CZ08 | 5.3375 | 6.0692
CZ09 | 46.7407 | 40.9852 | CZ09 | 5.2865 | 5.909
CZ10 | 49.5471 | 43.3682 | CZ10 | 6.9316 | 7.3115
CZ11 | 48.883 | 41.0937 | CZ11 | 8.8957 | 7.0889
CZ12 | 46.4737 | 39.4779 | CZ12 | 8.5676 | 7.3073
CZ13 | 50.3798 | 42.4269 | CZ13 | 7.6575 | 6.4821
CZ14 | 54.0645 | 45.4029 | CZ14 | 6.5545 | 5.8454
CZ15 | 60.1354 | 50.425 | CZ15 | 5.5023 | 5.1443
CZ16 | 50.1226 | 42.0874 | CZ16 | 10.7207 | 8.7002

## Raw_totalendusesannual (hidden)
Vintage | Climate Zone | HVAC System | Electricity (kBtu) | Natural Gas (kBtu)
Existing | CZ01 | cAVVG | 7676076.47 | 2456071.48
Existing | CZ02 | cAVVG | 8940456.8 | 2332564.71
Existing | CZ03 | cAVVG | 8331051.13 | 1832646.81
Existing | CZ04 | cAVVG | 9186574.47 | 1806014.64
Existing | CZ05 | cAVVG | 8565342.6 | 1853153.46
Existing | CZ06 | cAVVG | 9342191.68 | 1241620.96
Existing | CZ07 | cAVVG | 9572808.91 | 1260562.21
Existing | CZ08 | cAVVG | 9942286.37 | 1379220
Existing | CZ09 | cAVVG | 10344684.87 | 1373934.55
Existing | CZ10 | cAVVG | 11032600.04 | 1868748.16
Existing | CZ11 | cAVVG | 10804159.29 | 2413617.23
Existing | CZ12 | cAVVG | 10233117.47 | 2278456.57
Existing | CZ13 | cAVVG | 11096924.64 | 2088936.39
Existing | CZ14 | cAVVG | 12053826.37 | 1768381.85
Existing | CZ15 | cAVVG | 13429554.61 | 1617175.07
Existing | CZ16 | cAVVG | 10912250.08 | 2843261.13
New Construction | CZ01 | cAVVG | 6792231.13 | 2339545.88
New Construction | CZ02 | cAVVG | 7875549.5 | 2800431.01
New Construction | CZ03 | cAVVG | 7321360.57 | 2252859.18
New Construction | CZ04 | cAVVG | 8092963.48 | 2165694.31
New Construction | CZ05 | cAVVG | 7522062.03 | 2284695.92
New Construction | CZ06 | cAVVG | 8166189.78 | 1439009.5
New Construction | CZ07 | cAVVG | 8380915.42 | 1435262.88
New Construction | CZ08 | cAVVG | 8743193.13 | 1613700.5
New Construction | CZ09 | cAVVG | 9097307.12 | 1582132.87
New Construction | CZ10 | cAVVG | 9649950.86 | 2025819.98
New Construction | CZ11 | cAVVG | 9079857.87 | 1863054.21
New Construction | CZ12 | cAVVG | 8727381.08 | 1922513.74
New Construction | CZ13 | cAVVG | 9353711.63 | 1701807.61
New Construction | CZ14 | cAVVG | 10127631.04 | 1527819.37
New Construction | CZ15 | cAVVG | 11241140.02 | 1384709.39
New Construction | CZ16 | cAVVG | 9170972.21 | 2311609.89
Existing | CZ01 | cDXGF | 8627425.17 | 2252034.6
Existing | CZ02 | cDXGF | 10495810.51 | 2133866.92
Existing | CZ03 | cDXGF | 9736419.56 | 1713623.86
Existing | CZ04 | cDXGF | 10759901.04 | 1675173.74
Existing | CZ05 | cDXGF | 10025756.11 | 1737022.33
Existing | CZ06 | cDXGF | 11066139.35 | 1200933.25
Existing | CZ07 | cDXGF | 11339556.84 | 1202464.42
Existing | CZ08 | cDXGF | 11767151.79 | 1312051.6
Existing | CZ09 | cDXGF | 12208685.26 | 1301691.34
Existing | CZ10 | cDXGF | 12952063.32 | 1684676.8
Existing | CZ11 | cDXGF | 12758039.08 | 2131321.32
Existing | CZ12 | cDXGF | 12139002.87 | 2056514.28
Existing | CZ13 | cDXGF | 13120649.09 | 1841823.34
Existing | CZ14 | cDXGF | 14052775.65 | 1591720.96
Existing | CZ15 | cDXGF | 15525089.38 | 1359782.32
Existing | CZ16 | cDXGF | 13102803.19 | 2553866.94
New Construction | CZ01 | cDXGF | 7533205.67 | 2092531.7
New Construction | CZ02 | cDXGF | 9213723.12 | 2482804.24
New Construction | CZ03 | cDXGF | 8569045.88 | 2034980.38
New Construction | CZ04 | cDXGF | 9492890.14 | 1947294.34
New Construction | CZ05 | cDXGF | 8799444.22 | 2073198.45
New Construction | CZ06 | cDXGF | 9681124.18 | 1354466.96
New Construction | CZ07 | cDXGF | 9893391.49 | 1325419.09
New Construction | CZ08 | cDXGF | 10344052.03 | 1477873.48
New Construction | CZ09 | cDXGF | 10750877.44 | 1442119.02
New Construction | CZ10 | cDXGF | 11366815.56 | 1762942.69
New Construction | CZ11 | cDXGF | 10680328.23 | 1697547.22
New Construction | CZ12 | cDXGF | 10284279.45 | 1752118.83
New Construction | CZ13 | cDXGF | 11016931.28 | 1561347.48
New Construction | CZ14 | cDXGF | 11770870.88 | 1420524.56
New Construction | CZ15 | cDXGF | 12985899.77 | 1271669.38
New Construction | CZ16 | cDXGF | 10977226.21 | 2063109.93
Existing | CZ01 | cDXHP | 8663317.19 | 2108394.97
Existing | CZ02 | cDXHP | 10526726.29 | 2022684.6
Existing | CZ03 | cDXHP | 9750874.24 | 1652628.51
Existing | CZ04 | cDXHP | 10773242.29 | 1619900.85
Existing | CZ05 | cDXHP | 10041743.14 | 1675177.33
Existing | CZ06 | cDXHP | 11060274.04 | 1190525.99
Existing | CZ07 | cDXHP | 11336309.32 | 1192382.3
Existing | CZ08 | cDXHP | 11767420.38 | 1295963.45
Existing | CZ09 | cDXHP | 12207878.25 | 1290294.19
Existing | CZ10 | cDXHP | 12964516.58 | 1640120.33
Existing | CZ11 | cDXHP | 12790453.06 | 2033400.29
Existing | CZ12 | cDXHP | 12169366.75 | 1958971.09
Existing | CZ13 | cDXHP | 13142643 | 1772187.24
Existing | CZ14 | cDXHP | 14068264.53 | 1550411.7
Existing | CZ15 | cDXHP | 15528330.85 | 1348475.78
Existing | CZ16 | cDXHP | 13167089.36 | 2392993.49
New Construction | CZ01 | cDXHP | 7574809.74 | 1924058.36
New Construction | CZ02 | cDXHP | 9269199.79 | 2281734.68
New Construction | CZ03 | cDXHP | 8597586.41 | 1917354.87
New Construction | CZ04 | cDXHP | 9517321.87 | 1847217.78
New Construction | CZ05 | cDXHP | 8830788.65 | 1952245.91
New Construction | CZ06 | cDXHP | 9678168.76 | 1331593.83
New Construction | CZ07 | cDXHP | 9892196.3 | 1305557.03
New Construction | CZ08 | cDXHP | 10348334.58 | 1445349.02
New Construction | CZ09 | cDXHP | 10752836.06 | 1418731.79
New Construction | CZ10 | cDXHP | 11386564.63 | 1692065.56
New Construction | CZ11 | cDXHP | 10710260.04 | 1606410.58
New Construction | CZ12 | cDXHP | 10315499.07 | 1647940.8
New Construction | CZ13 | cDXHP | 11038953.35 | 1488183.76
New Construction | CZ14 | cDXHP | 11787480.07 | 1372868.62
New Construction | CZ15 | cDXHP | 12989931.4 | 1257117.18
New Construction | CZ16 | cDXHP | 11047025.88 | 1887128.24
Existing | CZ01 | cDXOH | 8625531.23 | 2132012.04
Existing | CZ02 | cDXOH | 10493247.28 | 2038044.01
Existing | CZ03 | cDXOH | 9734811.23 | 1660386.52
Existing | CZ04 | cDXOH | 10758578.49 | 1626411.27
Existing | CZ05 | cDXOH | 10024788.05 | 1682802.88
Existing | CZ06 | cDXOH | 11065881.91 | 1191273.81
Existing | CZ07 | cDXOH | 11339277.87 | 1193165.63
Existing | CZ08 | cDXOH | 11766660.02 | 1297488.49
Existing | CZ09 | cDXOH | 12208345.37 | 1291266.01
Existing | CZ10 | cDXOH | 12950831.23 | 1645151.26
Existing | CZ11 | cDXOH | 12756477.58 | 2047289.47
Existing | CZ12 | cDXOH | 12136937.27 | 1972704.39
Existing | CZ13 | cDXOH | 13119732.29 | 1783923.83
Existing | CZ14 | cDXOH | 14051648.32 | 1556277.62
Existing | CZ15 | cDXOH | 15524499.9 | 1349207.12
Existing | CZ16 | cDXOH | 13101325.6 | 2416817.18
New Construction | CZ01 | cDXOH | 7529853.06 | 1956514.19
New Construction | CZ02 | cDXOH | 9211864.77 | 2303589.44
New Construction | CZ03 | cDXOH | 8567144.39 | 1928393.44
New Construction | CZ04 | cDXOH | 9490529.8 | 1856117.68
New Construction | CZ05 | cDXOH | 8796722.85 | 1962513.9
New Construction | CZ06 | cDXOH | 9680411.37 | 1333014.74
New Construction | CZ07 | cDXOH | 9892887.87 | 1306792.75
New Construction | CZ08 | cDXOH | 10342929.2 | 1447544.81
New Construction | CZ09 | cDXOH | 10750210.82 | 1420379.27
New Construction | CZ10 | cDXOH | 11364314.9 | 1698214.42
New Construction | CZ11 | cDXOH | 10678884.42 | 1626607.98
New Construction | CZ12 | cDXOH | 10280642.76 | 1669659.4
New Construction | CZ13 | cDXOH | 11014769.3 | 1502465.28
New Construction | CZ14 | cDXOH | 11769392 | 1379858.33
New Construction | CZ15 | cDXOH | 12984272.22 | 1257983.04
New Construction | CZ16 | cDXOH | 10972411.82 | 1923196.51
Existing | CZ01 | cPVVG | 8127923.07 | 2361389.96
Existing | CZ02 | cPVVG | 9962705.57 | 2226793.1
Existing | CZ03 | cPVVG | 9225275.21 | 1773650.35
Existing | CZ04 | cPVVG | 10231488.66 | 1733093.81
Existing | CZ05 | cPVVG | 9519107.12 | 1793277.73
Existing | CZ06 | cPVVG | 10581746.08 | 1218024.14
Existing | CZ07 | cPVVG | 10846104.85 | 1218397.33
Existing | CZ08 | cPVVG | 11258112.1 | 1334441.02
Existing | CZ09 | cPVVG | 11685649.14 | 1321683.03
Existing | CZ10 | cPVVG | 12387275.27 | 1732961.89
Existing | CZ11 | cPVVG | 12221250.5 | 2224013.09
Existing | CZ12 | cPVVG | 11618889.5 | 2141997.74
Existing | CZ13 | cPVVG | 12595466.46 | 1914460.52
Existing | CZ14 | cPVVG | 13516681.92 | 1638680.74
Existing | CZ15 | cPVVG | 15034465.07 | 1375633.55
Existing | CZ16 | cPVVG | 12531146.86 | 2680285.23
New Construction | CZ01 | cPVVG | 7120297.08 | 2201330.33
New Construction | CZ02 | cPVVG | 8709198.22 | 2618171.94
New Construction | CZ03 | cPVVG | 8089728.08 | 2131675.22
New Construction | CZ04 | cPVVG | 8991623.95 | 2036364.2
New Construction | CZ05 | cPVVG | 8328317.5 | 2166519.7
New Construction | CZ06 | cPVVG | 9223045.42 | 1385833.88
New Construction | CZ07 | cPVVG | 9435186.93 | 1352817.76
New Construction | CZ08 | cPVVG | 9855908.15 | 1517354.2
New Construction | CZ09 | cPVVG | 10246723.97 | 1477317.15
New Construction | CZ10 | cPVVG | 10842488.19 | 1827954.7
New Construction | CZ11 | cPVVG | 10273844.91 | 1772305.48
New Construction | CZ12 | cPVVG | 9869882.26 | 1826897.4
New Construction | CZ13 | cPVVG | 10607159.5 | 1620596.12
New Construction | CZ14 | cPVVG | 11351177.38 | 1461411.23
New Construction | CZ15 | cPVVG | 12606771.97 | 1286117.25
New Construction | CZ16 | cPVVG | 10522275.51 | 2175136.32

## Energy Usage by End Use
Energy Consumption by End Use - Health/Medical - Hospital
Climate Zone | HVAC System | Vintage | End Use | Electricity (kBtu) | Natural Gas (kBtu) | Note
CZ01 | cAVVG | Existing | Heating | 0 | 1283456.41
CZ01 | cAVVG | Existing | Cooling | 109234.67 | 0
CZ01 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ01 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ01 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ01 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ01 | cAVVG | Existing | Fans | 714438.74 | 0
CZ01 | cAVVG | Existing | Pumps | 26421.54 | 0
CZ01 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ01 | cAVVG | Existing | Humidification | 0 | 0
CZ01 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ01 | cAVVG | Existing | Water Systems | 0 | 1023276.86
CZ01 | cAVVG | Existing | Refrigeration | 0 | 0
CZ01 | cAVVG | Existing | Generators | 0 | 0
CZ01 | cAVVG | Existing | Total End Uses | 7676076.47 | 2456071.48
CZ02 | cAVVG | Existing | Heating | 0 | 1243119.58
CZ02 | cAVVG | Existing | Cooling | 1060648.51 | 0
CZ02 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ02 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ02 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ02 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ02 | cAVVG | Existing | Fans | 983224.69 | 0
CZ02 | cAVVG | Existing | Pumps | 70602.09 | 0
CZ02 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ02 | cAVVG | Existing | Humidification | 0 | 0
CZ02 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ02 | cAVVG | Existing | Water Systems | 0 | 940106.92
CZ02 | cAVVG | Existing | Refrigeration | 0 | 0
CZ02 | cAVVG | Existing | Generators | 0 | 0
CZ02 | cAVVG | Existing | Total End Uses | 8940456.8 | 2332564.71
CZ03 | cAVVG | Existing | Heating | 0 | 746943.07
CZ03 | cAVVG | Existing | Cooling | 643397.1 | 0
CZ03 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ03 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ03 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ03 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ03 | cAVVG | Existing | Fans | 803318.71 | 0
CZ03 | cAVVG | Existing | Pumps | 58353.8 | 0
CZ03 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ03 | cAVVG | Existing | Humidification | 0 | 0
CZ03 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ03 | cAVVG | Existing | Water Systems | 0 | 936365.53
CZ03 | cAVVG | Existing | Refrigeration | 0 | 0
CZ03 | cAVVG | Existing | Generators | 0 | 0
CZ03 | cAVVG | Existing | Total End Uses | 8331051.13 | 1832646.81
CZ04 | cAVVG | Existing | Heating | 0 | 752498.32
CZ04 | cAVVG | Existing | Cooling | 1243258.69 | 0
CZ04 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ04 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ04 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ04 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ04 | cAVVG | Existing | Fans | 1039791.09 | 0
CZ04 | cAVVG | Existing | Pumps | 77543.17 | 0
CZ04 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ04 | cAVVG | Existing | Humidification | 0 | 0
CZ04 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ04 | cAVVG | Existing | Water Systems | 0 | 904178.1
CZ04 | cAVVG | Existing | Refrigeration | 0 | 0
CZ04 | cAVVG | Existing | Generators | 0 | 0
CZ04 | cAVVG | Existing | Total End Uses | 9186574.47 | 1806014.64
CZ05 | cAVVG | Existing | Heating | 0 | 767357.96
CZ05 | cAVVG | Existing | Cooling | 804641.04 | 0
CZ05 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ05 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ05 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ05 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ05 | cAVVG | Existing | Fans | 877027.03 | 0
CZ05 | cAVVG | Existing | Pumps | 57693.01 | 0
CZ05 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ05 | cAVVG | Existing | Humidification | 0 | 0
CZ05 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ05 | cAVVG | Existing | Water Systems | 0 | 936457.29
CZ05 | cAVVG | Existing | Refrigeration | 0 | 0
CZ05 | cAVVG | Existing | Generators | 0 | 0
CZ05 | cAVVG | Existing | Total End Uses | 8565342.6 | 1853153.46
CZ06 | cAVVG | Existing | Heating | 0 | 229775.68
CZ06 | cAVVG | Existing | Cooling | 1393407.89 | 0
CZ06 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ06 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ06 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ06 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ06 | cAVVG | Existing | Fans | 1034314.48 | 0
CZ06 | cAVVG | Existing | Pumps | 88487.8 | 0
CZ06 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ06 | cAVVG | Existing | Humidification | 0 | 0
CZ06 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ06 | cAVVG | Existing | Water Systems | 0 | 862507.07
CZ06 | cAVVG | Existing | Refrigeration | 0 | 0
CZ06 | cAVVG | Existing | Generators | 0 | 0
CZ06 | cAVVG | Existing | Total End Uses | 9342191.68 | 1241620.96
CZ07 | cAVVG | Existing | Heating | 0 | 259714.13
CZ07 | cAVVG | Existing | Cooling | 1557403.78 | 0
CZ07 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ07 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ07 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ07 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ07 | cAVVG | Existing | Fans | 1093024.29 | 0
CZ07 | cAVVG | Existing | Pumps | 96399.32 | 0
CZ07 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ07 | cAVVG | Existing | Humidification | 0 | 0
CZ07 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ07 | cAVVG | Existing | Water Systems | 0 | 851509.86
CZ07 | cAVVG | Existing | Refrigeration | 0 | 0
CZ07 | cAVVG | Existing | Generators | 0 | 0
CZ07 | cAVVG | Existing | Total End Uses | 9572808.91 | 1260562.21
CZ08 | cAVVG | Existing | Heating | 0 | 379592.55
CZ08 | cAVVG | Existing | Cooling | 1814943.26 | 0
CZ08 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ08 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ08 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ08 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ08 | cAVVG | Existing | Fans | 1200556.62 | 0
CZ08 | cAVVG | Existing | Pumps | 100804.97 | 0
CZ08 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ08 | cAVVG | Existing | Humidification | 0 | 0
CZ08 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ08 | cAVVG | Existing | Water Systems | 0 | 850289.24
CZ08 | cAVVG | Existing | Refrigeration | 0 | 0
CZ08 | cAVVG | Existing | Generators | 0 | 0
CZ08 | cAVVG | Existing | Total End Uses | 9942286.37 | 1379220
CZ09 | cAVVG | Existing | Heating | 0 | 386071.65
CZ09 | cAVVG | Existing | Cooling | 2062703.42 | 0
CZ09 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ09 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ09 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ09 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ09 | cAVVG | Existing | Fans | 1349056.86 | 0
CZ09 | cAVVG | Existing | Pumps | 106943.07 | 0
CZ09 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ09 | cAVVG | Existing | Humidification | 0 | 0
CZ09 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ09 | cAVVG | Existing | Water Systems | 0 | 838524.69
CZ09 | cAVVG | Existing | Refrigeration | 0 | 0
CZ09 | cAVVG | Existing | Generators | 0 | 0
CZ09 | cAVVG | Existing | Total End Uses | 10344684.87 | 1373934.55
CZ10 | cAVVG | Existing | Heating | 0 | 887668.66
CZ10 | cAVVG | Existing | Cooling | 2556095.17 | 0
CZ10 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ10 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ10 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ10 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ10 | cAVVG | Existing | Fans | 1536981.36 | 0
CZ10 | cAVVG | Existing | Pumps | 113541.99 | 0
CZ10 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ10 | cAVVG | Existing | Humidification | 0 | 0
CZ10 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ10 | cAVVG | Existing | Water Systems | 0 | 831741.28
CZ10 | cAVVG | Existing | Refrigeration | 0 | 0
CZ10 | cAVVG | Existing | Generators | 0 | 0
CZ10 | cAVVG | Existing | Total End Uses | 11032600.04 | 1868748.16
CZ11 | cAVVG | Existing | Heating | 0 | 1414029.29
CZ11 | cAVVG | Existing | Cooling | 2419902.45 | 0
CZ11 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ11 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ11 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ11 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ11 | cAVVG | Existing | Fans | 1466930.31 | 0
CZ11 | cAVVG | Existing | Pumps | 91345.02 | 0
CZ11 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ11 | cAVVG | Existing | Humidification | 0 | 0
CZ11 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ11 | cAVVG | Existing | Water Systems | 0 | 850249.71
CZ11 | cAVVG | Existing | Refrigeration | 0 | 0
CZ11 | cAVVG | Existing | Generators | 0 | 0
CZ11 | cAVVG | Existing | Total End Uses | 10804159.29 | 2413617.23
CZ12 | cAVVG | Existing | Heating | 0 | 1254816.83
CZ12 | cAVVG | Existing | Cooling | 2017036.99 | 0
CZ12 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ12 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ12 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ12 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ12 | cAVVG | Existing | Fans | 1310664.44 | 0
CZ12 | cAVVG | Existing | Pumps | 79434.52 | 0
CZ12 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ12 | cAVVG | Existing | Humidification | 0 | 0
CZ12 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ12 | cAVVG | Existing | Water Systems | 0 | 874301.53
CZ12 | cAVVG | Existing | Refrigeration | 0 | 0
CZ12 | cAVVG | Existing | Generators | 0 | 0
CZ12 | cAVVG | Existing | Total End Uses | 10233117.47 | 2278456.57
CZ13 | cAVVG | Existing | Heating | 0 | 1114072.66
CZ13 | cAVVG | Existing | Cooling | 2658162.29 | 0
CZ13 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ13 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ13 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ13 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ13 | cAVVG | Existing | Fans | 1523985.59 | 0
CZ13 | cAVVG | Existing | Pumps | 88795.24 | 0
CZ13 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ13 | cAVVG | Existing | Humidification | 0 | 0
CZ13 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ13 | cAVVG | Existing | Water Systems | 0 | 825525.52
CZ13 | cAVVG | Existing | Refrigeration | 0 | 0
CZ13 | cAVVG | Existing | Generators | 0 | 0
CZ13 | cAVVG | Existing | Total End Uses | 11096924.64 | 2088936.39
CZ14 | cAVVG | Existing | Heating | 0 | 835511.87
CZ14 | cAVVG | Existing | Cooling | 3294721.95 | 0
CZ14 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ14 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ14 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ14 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ14 | cAVVG | Existing | Fans | 1814180.78 | 0
CZ14 | cAVVG | Existing | Pumps | 118942.12 | 0
CZ14 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ14 | cAVVG | Existing | Humidification | 0 | 0
CZ14 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ14 | cAVVG | Existing | Water Systems | 0 | 783531.76
CZ14 | cAVVG | Existing | Refrigeration | 0 | 0
CZ14 | cAVVG | Existing | Generators | 0 | 0
CZ14 | cAVVG | Existing | Total End Uses | 12053826.37 | 1768381.85
CZ15 | cAVVG | Existing | Heating | 0 | 772396.65
CZ15 | cAVVG | Existing | Cooling | 4560334.77 | 0
CZ15 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ15 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ15 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ15 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ15 | cAVVG | Existing | Fans | 1934866.78 | 0
CZ15 | cAVVG | Existing | Pumps | 108371.54 | 0
CZ15 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ15 | cAVVG | Existing | Humidification | 0 | 0
CZ15 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ15 | cAVVG | Existing | Water Systems | 0 | 695440.21
CZ15 | cAVVG | Existing | Refrigeration | 0 | 0
CZ15 | cAVVG | Existing | Generators | 0 | 0
CZ15 | cAVVG | Existing | Total End Uses | 13429554.61 | 1617175.07
CZ16 | cAVVG | Existing | Heating | 0 | 1769322.13
CZ16 | cAVVG | Existing | Cooling | 2239778.01 | 0
CZ16 | cAVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ16 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ16 | cAVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ16 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ16 | cAVVG | Existing | Fans | 1753556.96 | 0
CZ16 | cAVVG | Existing | Pumps | 92933.59 | 0
CZ16 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ16 | cAVVG | Existing | Humidification | 0 | 0
CZ16 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ16 | cAVVG | Existing | Water Systems | 0 | 924600.78
CZ16 | cAVVG | Existing | Refrigeration | 0 | 0
CZ16 | cAVVG | Existing | Generators | 0 | 0
CZ16 | cAVVG | Existing | Total End Uses | 10912250.08 | 2843261.13
CZ01 | cAVVG | New Construction | Heating | 0 | 1167557.94
CZ01 | cAVVG | New Construction | Cooling | 84246.18 | 0
CZ01 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ01 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ01 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ01 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ01 | cAVVG | New Construction | Fans | 648586.63 | 0
CZ01 | cAVVG | New Construction | Pumps | 21876.96 | 0
CZ01 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ01 | cAVVG | New Construction | Humidification | 0 | 0
CZ01 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ01 | cAVVG | New Construction | Water Systems | 0 | 1022649.72
CZ01 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ01 | cAVVG | New Construction | Generators | 0 | 0
CZ01 | cAVVG | New Construction | Total End Uses | 6792231.13 | 2339545.88
CZ02 | cAVVG | New Construction | Heating | 0 | 1711393.06
CZ02 | cAVVG | New Construction | Cooling | 936379.73 | 0
CZ02 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ02 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ02 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ02 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ02 | cAVVG | New Construction | Fans | 839878.59 | 0
CZ02 | cAVVG | New Construction | Pumps | 61769.83 | 0
CZ02 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ02 | cAVVG | New Construction | Humidification | 0 | 0
CZ02 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ02 | cAVVG | New Construction | Water Systems | 0 | 939699.73
CZ02 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ02 | cAVVG | New Construction | Generators | 0 | 0
CZ02 | cAVVG | New Construction | Total End Uses | 7875549.5 | 2800431.01
CZ03 | cAVVG | New Construction | Heating | 0 | 1167421.89
CZ03 | cAVVG | New Construction | Cooling | 554729.69 | 0
CZ03 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ03 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ03 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ03 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ03 | cAVVG | New Construction | Fans | 678018.66 | 0
CZ03 | cAVVG | New Construction | Pumps | 51090.87 | 0
CZ03 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ03 | cAVVG | New Construction | Humidification | 0 | 0
CZ03 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ03 | cAVVG | New Construction | Water Systems | 0 | 936099.07
CZ03 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ03 | cAVVG | New Construction | Generators | 0 | 0
CZ03 | cAVVG | New Construction | Total End Uses | 7321360.57 | 2252859.18
CZ04 | cAVVG | New Construction | Heating | 0 | 1112419.74
CZ04 | cAVVG | New Construction | Cooling | 1107503.5 | 0
CZ04 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ04 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ04 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ04 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ04 | cAVVG | New Construction | Fans | 878393.41 | 0
CZ04 | cAVVG | New Construction | Pumps | 69545.22 | 0
CZ04 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ04 | cAVVG | New Construction | Humidification | 0 | 0
CZ04 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ04 | cAVVG | New Construction | Water Systems | 0 | 903936.35
CZ04 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ04 | cAVVG | New Construction | Generators | 0 | 0
CZ04 | cAVVG | New Construction | Total End Uses | 8092963.48 | 2165694.31
CZ05 | cAVVG | New Construction | Heating | 0 | 1199174.21
CZ05 | cAVVG | New Construction | Cooling | 692573.47 | 0
CZ05 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ05 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ05 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ05 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ05 | cAVVG | New Construction | Fans | 741930.98 | 0
CZ05 | cAVVG | New Construction | Pumps | 50036.23 | 0
CZ05 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ05 | cAVVG | New Construction | Humidification | 0 | 0
CZ05 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ05 | cAVVG | New Construction | Water Systems | 0 | 936183.48
CZ05 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ05 | cAVVG | New Construction | Generators | 0 | 0
CZ05 | cAVVG | New Construction | Total End Uses | 7522062.03 | 2284695.92
CZ06 | cAVVG | New Construction | Heating | 0 | 427343.85
CZ06 | cAVVG | New Construction | Cooling | 1199245.56 | 0
CZ06 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ06 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ06 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ06 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ06 | cAVVG | New Construction | Fans | 850929.81 | 0
CZ06 | cAVVG | New Construction | Pumps | 78493.06 | 0
CZ06 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ06 | cAVVG | New Construction | Humidification | 0 | 0
CZ06 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ06 | cAVVG | New Construction | Water Systems | 0 | 862327.43
CZ06 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ06 | cAVVG | New Construction | Generators | 0 | 0
CZ06 | cAVVG | New Construction | Total End Uses | 8166189.78 | 1439009.5
CZ07 | cAVVG | New Construction | Heating | 0 | 434652.46
CZ07 | cAVVG | New Construction | Cooling | 1347234.15 | 0
CZ07 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ07 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ07 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ07 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ07 | cAVVG | New Construction | Fans | 910947.99 | 0
CZ07 | cAVVG | New Construction | Pumps | 85211.93 | 0
CZ07 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ07 | cAVVG | New Construction | Humidification | 0 | 0
CZ07 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ07 | cAVVG | New Construction | Water Systems | 0 | 851272.2
CZ07 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ07 | cAVVG | New Construction | Generators | 0 | 0
CZ07 | cAVVG | New Construction | Total End Uses | 8380915.42 | 1435262.88
CZ08 | cAVVG | New Construction | Heating | 0 | 614198.81
CZ08 | cAVVG | New Construction | Cooling | 1609380.49 | 0
CZ08 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ08 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ08 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ08 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ08 | cAVVG | New Construction | Fans | 1005112.8 | 0
CZ08 | cAVVG | New Construction | Pumps | 91178.49 | 0
CZ08 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ08 | cAVVG | New Construction | Humidification | 0 | 0
CZ08 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ08 | cAVVG | New Construction | Water Systems | 0 | 850163.47
CZ08 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ08 | cAVVG | New Construction | Generators | 0 | 0
CZ08 | cAVVG | New Construction | Total End Uses | 8743193.13 | 1613700.5
CZ09 | cAVVG | New Construction | Heating | 0 | 594412.66
CZ09 | cAVVG | New Construction | Cooling | 1836769.29 | 0
CZ09 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ09 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ09 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ09 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ09 | cAVVG | New Construction | Fans | 1125640.01 | 0
CZ09 | cAVVG | New Construction | Pumps | 97376.47 | 0
CZ09 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ09 | cAVVG | New Construction | Humidification | 0 | 0
CZ09 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ09 | cAVVG | New Construction | Water Systems | 0 | 838381.99
CZ09 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ09 | cAVVG | New Construction | Generators | 0 | 0
CZ09 | cAVVG | New Construction | Total End Uses | 9097307.12 | 1582132.87
CZ10 | cAVVG | New Construction | Heating | 0 | 1044865.02
CZ10 | cAVVG | New Construction | Cooling | 2238029.1 | 0
CZ10 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ10 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ10 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ10 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ10 | cAVVG | New Construction | Fans | 1280115.76 | 0
CZ10 | cAVVG | New Construction | Pumps | 94284.66 | 0
CZ10 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ10 | cAVVG | New Construction | Humidification | 0 | 0
CZ10 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ10 | cAVVG | New Construction | Water Systems | 0 | 831616.75
CZ10 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ10 | cAVVG | New Construction | Generators | 0 | 0
CZ10 | cAVVG | New Construction | Total End Uses | 9649950.86 | 2025819.98
CZ11 | cAVVG | New Construction | Heating | 0 | 863928.79
CZ11 | cAVVG | New Construction | Cooling | 1896292.24 | 0
CZ11 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ11 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ11 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ11 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ11 | cAVVG | New Construction | Fans | 1079778.05 | 0
CZ11 | cAVVG | New Construction | Pumps | 66266.23 | 0
CZ11 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ11 | cAVVG | New Construction | Humidification | 0 | 0
CZ11 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ11 | cAVVG | New Construction | Water Systems | 0 | 849787.2
CZ11 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ11 | cAVVG | New Construction | Generators | 0 | 0
CZ11 | cAVVG | New Construction | Total End Uses | 9079857.87 | 1863054.21
CZ12 | cAVVG | New Construction | Heating | 0 | 899332.38
CZ12 | cAVVG | New Construction | Cooling | 1618779.5 | 0
CZ12 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ12 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ12 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ12 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ12 | cAVVG | New Construction | Fans | 1005185.56 | 0
CZ12 | cAVVG | New Construction | Pumps | 65894.68 | 0
CZ12 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ12 | cAVVG | New Construction | Humidification | 0 | 0
CZ12 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ12 | cAVVG | New Construction | Water Systems | 0 | 873843.14
CZ12 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ12 | cAVVG | New Construction | Generators | 0 | 0
CZ12 | cAVVG | New Construction | Total End Uses | 8727381.08 | 1922513.74
CZ13 | cAVVG | New Construction | Heating | 0 | 727417.34
CZ13 | cAVVG | New Construction | Cooling | 2105888.68 | 0
CZ13 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ13 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ13 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ13 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ13 | cAVVG | New Construction | Fans | 1137024.5 | 0
CZ13 | cAVVG | New Construction | Pumps | 73277.1 | 0
CZ13 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ13 | cAVVG | New Construction | Humidification | 0 | 0
CZ13 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ13 | cAVVG | New Construction | Water Systems | 0 | 825052.05
CZ13 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ13 | cAVVG | New Construction | Generators | 0 | 0
CZ13 | cAVVG | New Construction | Total End Uses | 9353711.63 | 1701807.61
CZ14 | cAVVG | New Construction | Heating | 0 | 595366.2
CZ14 | cAVVG | New Construction | Cooling | 2650272.25 | 0
CZ14 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ14 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ14 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ14 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ14 | cAVVG | New Construction | Fans | 1342648.66 | 0
CZ14 | cAVVG | New Construction | Pumps | 97188.77 | 0
CZ14 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ14 | cAVVG | New Construction | Humidification | 0 | 0
CZ14 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ14 | cAVVG | New Construction | Water Systems | 0 | 783114.95
CZ14 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ14 | cAVVG | New Construction | Generators | 0 | 0
CZ14 | cAVVG | New Construction | Total End Uses | 10127631.04 | 1527819.37
CZ15 | cAVVG | New Construction | Heating | 0 | 540360.22
CZ15 | cAVVG | New Construction | Cooling | 3716297.99 | 0
CZ15 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ15 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ15 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ15 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ15 | cAVVG | New Construction | Fans | 1397623.98 | 0
CZ15 | cAVVG | New Construction | Pumps | 89696.71 | 0
CZ15 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ15 | cAVVG | New Construction | Humidification | 0 | 0
CZ15 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ15 | cAVVG | New Construction | Water Systems | 0 | 695010.95
CZ15 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ15 | cAVVG | New Construction | Generators | 0 | 0
CZ15 | cAVVG | New Construction | Total End Uses | 11241140.02 | 1384709.39
CZ16 | cAVVG | New Construction | Heating | 0 | 1238199.41
CZ16 | cAVVG | New Construction | Cooling | 1765664.47 | 0
CZ16 | cAVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ16 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ16 | cAVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ16 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ16 | cAVVG | New Construction | Fans | 1294970.02 | 0
CZ16 | cAVVG | New Construction | Pumps | 72816.37 | 0
CZ16 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ16 | cAVVG | New Construction | Humidification | 0 | 0
CZ16 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ16 | cAVVG | New Construction | Water Systems | 0 | 924072.26
CZ16 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ16 | cAVVG | New Construction | Generators | 0 | 0
CZ16 | cAVVG | New Construction | Total End Uses | 9170972.21 | 2311609.89
CZ01 | cDXGF | Existing | Heating | 0 | 1079447.09
CZ01 | cDXGF | Existing | Cooling | 423966.39 | 0
CZ01 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ01 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ01 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXGF | Existing | Fans | 1284784.08 | 0
CZ01 | cDXGF | Existing | Pumps | 92693.19 | 0
CZ01 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ01 | cDXGF | Existing | Humidification | 0 | 0
CZ01 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ01 | cDXGF | Existing | Water Systems | 0 | 1023249.29
CZ01 | cDXGF | Existing | Refrigeration | 0 | 0
CZ01 | cDXGF | Existing | Generators | 0 | 0
CZ01 | cDXGF | Existing | Total End Uses | 8627425.17 | 2252034.6
CZ02 | cDXGF | Existing | Heating | 0 | 1044488.81
CZ02 | cDXGF | Existing | Cooling | 1946908.39 | 0
CZ02 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ02 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ02 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXGF | Existing | Fans | 1595833.35 | 0
CZ02 | cDXGF | Existing | Pumps | 127087.26 | 0
CZ02 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ02 | cDXGF | Existing | Humidification | 0 | 0
CZ02 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ02 | cDXGF | Existing | Water Systems | 0 | 940039.9
CZ02 | cDXGF | Existing | Refrigeration | 0 | 0
CZ02 | cDXGF | Existing | Generators | 0 | 0
CZ02 | cDXGF | Existing | Total End Uses | 10495810.51 | 2133866.92
CZ03 | cDXGF | Existing | Heating | 0 | 627951.87
CZ03 | cDXGF | Existing | Cooling | 1358307.23 | 0
CZ03 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ03 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ03 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXGF | Existing | Fans | 1434648.51 | 0
CZ03 | cDXGF | Existing | Pumps | 117482.31 | 0
CZ03 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ03 | cDXGF | Existing | Humidification | 0 | 0
CZ03 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ03 | cDXGF | Existing | Water Systems | 0 | 936333.77
CZ03 | cDXGF | Existing | Refrigeration | 0 | 0
CZ03 | cDXGF | Existing | Generators | 0 | 0
CZ03 | cDXGF | Existing | Total End Uses | 9736419.56 | 1713623.86
CZ04 | cDXGF | Existing | Heating | 0 | 621592.13
CZ04 | cDXGF | Existing | Cooling | 2160153.51 | 0
CZ04 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ04 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ04 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXGF | Existing | Fans | 1644093.47 | 0
CZ04 | cDXGF | Existing | Pumps | 129672.55 | 0
CZ04 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ04 | cDXGF | Existing | Humidification | 0 | 0
CZ04 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ04 | cDXGF | Existing | Water Systems | 0 | 904243.4
CZ04 | cDXGF | Existing | Refrigeration | 0 | 0
CZ04 | cDXGF | Existing | Generators | 0 | 0
CZ04 | cDXGF | Existing | Total End Uses | 10759901.04 | 1675173.74
CZ05 | cDXGF | Existing | Heating | 0 | 651242.61
CZ05 | cDXGF | Existing | Cooling | 1589603.62 | 0
CZ05 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ05 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ05 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXGF | Existing | Fans | 1496824.62 | 0
CZ05 | cDXGF | Existing | Pumps | 113346.36 | 0
CZ05 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ05 | cDXGF | Existing | Humidification | 0 | 0
CZ05 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ05 | cDXGF | Existing | Water Systems | 0 | 936441.5
CZ05 | cDXGF | Existing | Refrigeration | 0 | 0
CZ05 | cDXGF | Existing | Generators | 0 | 0
CZ05 | cDXGF | Existing | Total End Uses | 10025756.11 | 1737022.33
CZ06 | cDXGF | Existing | Heating | 0 | 189167.42
CZ06 | cDXGF | Existing | Cooling | 2531461.26 | 0
CZ06 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ06 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ06 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXGF | Existing | Fans | 1584966.95 | 0
CZ06 | cDXGF | Existing | Pumps | 123729.62 | 0
CZ06 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ06 | cDXGF | Existing | Humidification | 0 | 0
CZ06 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ06 | cDXGF | Existing | Water Systems | 0 | 862427.62
CZ06 | cDXGF | Existing | Refrigeration | 0 | 0
CZ06 | cDXGF | Existing | Generators | 0 | 0
CZ06 | cDXGF | Existing | Total End Uses | 11066139.35 | 1200933.25
CZ07 | cDXGF | Existing | Heating | 0 | 201645.36
CZ07 | cDXGF | Existing | Cooling | 2775137.07 | 0
CZ07 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ07 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ07 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXGF | Existing | Fans | 1608371.21 | 0
CZ07 | cDXGF | Existing | Pumps | 130067.04 | 0
CZ07 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ07 | cDXGF | Existing | Humidification | 0 | 0
CZ07 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ07 | cDXGF | Existing | Water Systems | 0 | 851480.84
CZ07 | cDXGF | Existing | Refrigeration | 0 | 0
CZ07 | cDXGF | Existing | Generators | 0 | 0
CZ07 | cDXGF | Existing | Total End Uses | 11339556.84 | 1202464.42
CZ08 | cDXGF | Existing | Heating | 0 | 312413.84
CZ08 | cDXGF | Existing | Cooling | 3063180.58 | 0
CZ08 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ08 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ08 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXGF | Existing | Fans | 1740360.82 | 0
CZ08 | cDXGF | Existing | Pumps | 137628.87 | 0
CZ08 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ08 | cDXGF | Existing | Humidification | 0 | 0
CZ08 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ08 | cDXGF | Existing | Water Systems | 0 | 850299.54
CZ08 | cDXGF | Existing | Refrigeration | 0 | 0
CZ08 | cDXGF | Existing | Generators | 0 | 0
CZ08 | cDXGF | Existing | Total End Uses | 11767151.79 | 1312051.6
CZ09 | cDXGF | Existing | Heating | 0 | 313856.5
CZ09 | cDXGF | Existing | Cooling | 3367312.68 | 0
CZ09 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ09 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ09 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXGF | Existing | Fans | 1875048.72 | 0
CZ09 | cDXGF | Existing | Pumps | 140342.34 | 0
CZ09 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ09 | cDXGF | Existing | Humidification | 0 | 0
CZ09 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ09 | cDXGF | Existing | Water Systems | 0 | 838496.62
CZ09 | cDXGF | Existing | Refrigeration | 0 | 0
CZ09 | cDXGF | Existing | Generators | 0 | 0
CZ09 | cDXGF | Existing | Total End Uses | 12208685.26 | 1301691.34
CZ10 | cDXGF | Existing | Heating | 0 | 703648.3
CZ10 | cDXGF | Existing | Cooling | 3901864.95 | 0
CZ10 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ10 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ10 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXGF | Existing | Fans | 2070710.27 | 0
CZ10 | cDXGF | Existing | Pumps | 153506.59 | 0
CZ10 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ10 | cDXGF | Existing | Humidification | 0 | 0
CZ10 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ10 | cDXGF | Existing | Water Systems | 0 | 831690.28
CZ10 | cDXGF | Existing | Refrigeration | 0 | 0
CZ10 | cDXGF | Existing | Generators | 0 | 0
CZ10 | cDXGF | Existing | Total End Uses | 12952063.32 | 1684676.8
CZ11 | cDXGF | Existing | Heating | 0 | 1131728.46
CZ11 | cDXGF | Existing | Cooling | 3773572 | 0
CZ11 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ11 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ11 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXGF | Existing | Fans | 2005491.96 | 0
CZ11 | cDXGF | Existing | Pumps | 152993.61 | 0
CZ11 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ11 | cDXGF | Existing | Humidification | 0 | 0
CZ11 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ11 | cDXGF | Existing | Water Systems | 0 | 850254.64
CZ11 | cDXGF | Existing | Refrigeration | 0 | 0
CZ11 | cDXGF | Existing | Generators | 0 | 0
CZ11 | cDXGF | Existing | Total End Uses | 12758039.08 | 2131321.32
CZ12 | cDXGF | Existing | Heating | 0 | 1032911.91
CZ12 | cDXGF | Existing | Cooling | 3310307.89 | 0
CZ12 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ12 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ12 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXGF | Existing | Fans | 1853026.25 | 0
CZ12 | cDXGF | Existing | Pumps | 149687.21 | 0
CZ12 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ12 | cDXGF | Existing | Humidification | 0 | 0
CZ12 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ12 | cDXGF | Existing | Water Systems | 0 | 874264.16
CZ12 | cDXGF | Existing | Refrigeration | 0 | 0
CZ12 | cDXGF | Existing | Generators | 0 | 0
CZ12 | cDXGF | Existing | Total End Uses | 12139002.87 | 2056514.28
CZ13 | cDXGF | Existing | Heating | 0 | 866974.33
CZ13 | cDXGF | Existing | Cooling | 4113657.88 | 0
CZ13 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ13 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ13 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXGF | Existing | Fans | 2023137.68 | 0
CZ13 | cDXGF | Existing | Pumps | 157872.01 | 0
CZ13 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ13 | cDXGF | Existing | Humidification | 0 | 0
CZ13 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ13 | cDXGF | Existing | Water Systems | 0 | 825510.79
CZ13 | cDXGF | Existing | Refrigeration | 0 | 0
CZ13 | cDXGF | Existing | Generators | 0 | 0
CZ13 | cDXGF | Existing | Total End Uses | 13120649.09 | 1841823.34
CZ14 | cDXGF | Existing | Heating | 0 | 658763.41
CZ14 | cDXGF | Existing | Cooling | 4786720.46 | 0
CZ14 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ14 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ14 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXGF | Existing | Fans | 2281483.6 | 0
CZ14 | cDXGF | Existing | Pumps | 158590.07 | 0
CZ14 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ14 | cDXGF | Existing | Humidification | 0 | 0
CZ14 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ14 | cDXGF | Existing | Water Systems | 0 | 783619.34
CZ14 | cDXGF | Existing | Refrigeration | 0 | 0
CZ14 | cDXGF | Existing | Generators | 0 | 0
CZ14 | cDXGF | Existing | Total End Uses | 14052775.65 | 1591720.96
CZ15 | cDXGF | Existing | Heating | 0 | 515012.8
CZ15 | cDXGF | Existing | Cooling | 6213004.2 | 0
CZ15 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ15 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ15 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXGF | Existing | Fans | 2319042.22 | 0
CZ15 | cDXGF | Existing | Pumps | 167061.45 | 0
CZ15 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ15 | cDXGF | Existing | Humidification | 0 | 0
CZ15 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ15 | cDXGF | Existing | Water Systems | 0 | 695431.3
CZ15 | cDXGF | Existing | Refrigeration | 0 | 0
CZ15 | cDXGF | Existing | Generators | 0 | 0
CZ15 | cDXGF | Existing | Total End Uses | 15525089.38 | 1359782.32
CZ16 | cDXGF | Existing | Heating | 0 | 1480022.65
CZ16 | cDXGF | Existing | Cooling | 3827252.84 | 0
CZ16 | cDXGF | Existing | Interior Lighting | 2929105.9 | 0
CZ16 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXGF | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ16 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXGF | Existing | Fans | 2304717.63 | 0
CZ16 | cDXGF | Existing | Pumps | 144851.21 | 0
CZ16 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ16 | cDXGF | Existing | Humidification | 0 | 0
CZ16 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ16 | cDXGF | Existing | Water Systems | 0 | 924506.07
CZ16 | cDXGF | Existing | Refrigeration | 0 | 0
CZ16 | cDXGF | Existing | Generators | 0 | 0
CZ16 | cDXGF | Existing | Total End Uses | 13102803.19 | 2553866.94
CZ01 | cDXGF | New Construction | Heating | 0 | 920533.57
CZ01 | cDXGF | New Construction | Cooling | 323513.02 | 0
CZ01 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ01 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ01 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXGF | New Construction | Fans | 1093962.08 | 0
CZ01 | cDXGF | New Construction | Pumps | 78209.23 | 0
CZ01 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXGF | New Construction | Humidification | 0 | 0
CZ01 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXGF | New Construction | Water Systems | 0 | 1022659.91
CZ01 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ01 | cDXGF | New Construction | Generators | 0 | 0
CZ01 | cDXGF | New Construction | Total End Uses | 7533205.67 | 2092531.7
CZ02 | cDXGF | New Construction | Heating | 0 | 1393668.95
CZ02 | cDXGF | New Construction | Cooling | 1658392.47 | 0
CZ02 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ02 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ02 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXGF | New Construction | Fans | 1408925.06 | 0
CZ02 | cDXGF | New Construction | Pumps | 108884.24 | 0
CZ02 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXGF | New Construction | Humidification | 0 | 0
CZ02 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXGF | New Construction | Water Systems | 0 | 939797.08
CZ02 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ02 | cDXGF | New Construction | Generators | 0 | 0
CZ02 | cDXGF | New Construction | Total End Uses | 9213723.12 | 2482804.24
CZ03 | cDXGF | New Construction | Heating | 0 | 949544.3
CZ03 | cDXGF | New Construction | Cooling | 1163282.93 | 0
CZ03 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ03 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ03 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXGF | New Construction | Fans | 1265814.83 | 0
CZ03 | cDXGF | New Construction | Pumps | 102426.78 | 0
CZ03 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXGF | New Construction | Humidification | 0 | 0
CZ03 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXGF | New Construction | Water Systems | 0 | 936097.86
CZ03 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ03 | cDXGF | New Construction | Generators | 0 | 0
CZ03 | cDXGF | New Construction | Total End Uses | 8569045.88 | 2034980.38
CZ04 | cDXGF | New Construction | Heating | 0 | 893987.99
CZ04 | cDXGF | New Construction | Cooling | 1889756.56 | 0
CZ04 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ04 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ04 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXGF | New Construction | Fans | 1450357.98 | 0
CZ04 | cDXGF | New Construction | Pumps | 115254.24 | 0
CZ04 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXGF | New Construction | Humidification | 0 | 0
CZ04 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXGF | New Construction | Water Systems | 0 | 903968.14
CZ04 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ04 | cDXGF | New Construction | Generators | 0 | 0
CZ04 | cDXGF | New Construction | Total End Uses | 9492890.14 | 1947294.34
CZ05 | cDXGF | New Construction | Heating | 0 | 987725.22
CZ05 | cDXGF | New Construction | Cooling | 1353735.84 | 0
CZ05 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ05 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ05 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXGF | New Construction | Fans | 1309681.03 | 0
CZ05 | cDXGF | New Construction | Pumps | 98506 | 0
CZ05 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXGF | New Construction | Humidification | 0 | 0
CZ05 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXGF | New Construction | Water Systems | 0 | 936135.01
CZ05 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ05 | cDXGF | New Construction | Generators | 0 | 0
CZ05 | cDXGF | New Construction | Total End Uses | 8799444.22 | 2073198.45
CZ06 | cDXGF | New Construction | Heating | 0 | 342849.61
CZ06 | cDXGF | New Construction | Cooling | 2153484.35 | 0
CZ06 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ06 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ06 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXGF | New Construction | Fans | 1380060.9 | 0
CZ06 | cDXGF | New Construction | Pumps | 110057.59 | 0
CZ06 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXGF | New Construction | Humidification | 0 | 0
CZ06 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXGF | New Construction | Water Systems | 0 | 862279.13
CZ06 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ06 | cDXGF | New Construction | Generators | 0 | 0
CZ06 | cDXGF | New Construction | Total End Uses | 9681124.18 | 1354466.96
CZ07 | cDXGF | New Construction | Heating | 0 | 324838.63
CZ07 | cDXGF | New Construction | Cooling | 2357386.21 | 0
CZ07 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ07 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ07 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXGF | New Construction | Fans | 1383700.93 | 0
CZ07 | cDXGF | New Construction | Pumps | 114783 | 0
CZ07 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXGF | New Construction | Humidification | 0 | 0
CZ07 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXGF | New Construction | Water Systems | 0 | 851242.24
CZ07 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ07 | cDXGF | New Construction | Generators | 0 | 0
CZ07 | cDXGF | New Construction | Total End Uses | 9893391.49 | 1325419.09
CZ08 | cDXGF | New Construction | Heating | 0 | 478454.9
CZ08 | cDXGF | New Construction | Cooling | 2661434.88 | 0
CZ08 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ08 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ08 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXGF | New Construction | Fans | 1521088.55 | 0
CZ08 | cDXGF | New Construction | Pumps | 124007.25 | 0
CZ08 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXGF | New Construction | Humidification | 0 | 0
CZ08 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXGF | New Construction | Water Systems | 0 | 850080.36
CZ08 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ08 | cDXGF | New Construction | Generators | 0 | 0
CZ08 | cDXGF | New Construction | Total End Uses | 10344052.03 | 1477873.48
CZ09 | cDXGF | New Construction | Heating | 0 | 454511.12
CZ09 | cDXGF | New Construction | Cooling | 2940857.59 | 0
CZ09 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ09 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ09 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXGF | New Construction | Fans | 1645314.52 | 0
CZ09 | cDXGF | New Construction | Pumps | 127183.98 | 0
CZ09 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXGF | New Construction | Humidification | 0 | 0
CZ09 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXGF | New Construction | Water Systems | 0 | 838269.68
CZ09 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ09 | cDXGF | New Construction | Generators | 0 | 0
CZ09 | cDXGF | New Construction | Total End Uses | 10750877.44 | 1442119.02
CZ10 | cDXGF | New Construction | Heating | 0 | 782089.91
CZ10 | cDXGF | New Construction | Cooling | 3399557.77 | 0
CZ10 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ10 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ10 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXGF | New Construction | Fans | 1793298.46 | 0
CZ10 | cDXGF | New Construction | Pumps | 136437.98 | 0
CZ10 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXGF | New Construction | Humidification | 0 | 0
CZ10 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXGF | New Construction | Water Systems | 0 | 831514.56
CZ10 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ10 | cDXGF | New Construction | Generators | 0 | 0
CZ10 | cDXGF | New Construction | Total End Uses | 11366815.56 | 1762942.69
CZ11 | cDXGF | New Construction | Heating | 0 | 698418.27
CZ11 | cDXGF | New Construction | Cooling | 2990443.98 | 0
CZ11 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ11 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ11 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXGF | New Construction | Fans | 1526308.09 | 0
CZ11 | cDXGF | New Construction | Pumps | 126054.81 | 0
CZ11 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXGF | New Construction | Humidification | 0 | 0
CZ11 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXGF | New Construction | Water Systems | 0 | 849790.72
CZ11 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ11 | cDXGF | New Construction | Generators | 0 | 0
CZ11 | cDXGF | New Construction | Total End Uses | 10680328.23 | 1697547.22
CZ12 | cDXGF | New Construction | Heating | 0 | 728908.11
CZ12 | cDXGF | New Construction | Cooling | 2665120.37 | 0
CZ12 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ12 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ12 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXGF | New Construction | Fans | 1455828.92 | 0
CZ12 | cDXGF | New Construction | Pumps | 125808.81 | 0
CZ12 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXGF | New Construction | Humidification | 0 | 0
CZ12 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXGF | New Construction | Water Systems | 0 | 873872.51
CZ12 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ12 | cDXGF | New Construction | Generators | 0 | 0
CZ12 | cDXGF | New Construction | Total End Uses | 10284279.45 | 1752118.83
CZ13 | cDXGF | New Construction | Heating | 0 | 587068.88
CZ13 | cDXGF | New Construction | Cooling | 3281751.07 | 0
CZ13 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ13 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ13 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXGF | New Construction | Fans | 1566082.53 | 0
CZ13 | cDXGF | New Construction | Pumps | 131576.34 | 0
CZ13 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXGF | New Construction | Humidification | 0 | 0
CZ13 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXGF | New Construction | Water Systems | 0 | 824940.38
CZ13 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ13 | cDXGF | New Construction | Generators | 0 | 0
CZ13 | cDXGF | New Construction | Total End Uses | 11016931.28 | 1561347.48
CZ14 | cDXGF | New Construction | Heating | 0 | 488215.44
CZ14 | cDXGF | New Construction | Cooling | 3843011.91 | 0
CZ14 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ14 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ14 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXGF | New Construction | Fans | 1759101.26 | 0
CZ14 | cDXGF | New Construction | Pumps | 131236.37 | 0
CZ14 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXGF | New Construction | Humidification | 0 | 0
CZ14 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXGF | New Construction | Water Systems | 0 | 782970.9
CZ14 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ14 | cDXGF | New Construction | Generators | 0 | 0
CZ14 | cDXGF | New Construction | Total End Uses | 11770870.88 | 1420524.56
CZ15 | cDXGF | New Construction | Heating | 0 | 427454.66
CZ15 | cDXGF | New Construction | Cooling | 5035860.57 | 0
CZ15 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ15 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ15 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXGF | New Construction | Fans | 1773675 | 0
CZ15 | cDXGF | New Construction | Pumps | 138842.85 | 0
CZ15 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXGF | New Construction | Humidification | 0 | 0
CZ15 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXGF | New Construction | Water Systems | 0 | 694876.5
CZ15 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ15 | cDXGF | New Construction | Generators | 0 | 0
CZ15 | cDXGF | New Construction | Total End Uses | 12985899.77 | 1271669.38
CZ16 | cDXGF | New Construction | Heating | 0 | 989578.64
CZ16 | cDXGF | New Construction | Cooling | 3027601.13 | 0
CZ16 | cDXGF | New Construction | Interior Lighting | 2140645.73 | 0
CZ16 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXGF | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ16 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXGF | New Construction | Fans | 1792939.12 | 0
CZ16 | cDXGF | New Construction | Pumps | 119164.62 | 0
CZ16 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXGF | New Construction | Humidification | 0 | 0
CZ16 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXGF | New Construction | Water Systems | 0 | 924193.07
CZ16 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ16 | cDXGF | New Construction | Generators | 0 | 0
CZ16 | cDXGF | New Construction | Total End Uses | 10977226.21 | 2063109.93
CZ01 | cDXHP | Existing | Heating | 36180.57 | 935783.17
CZ01 | cDXHP | Existing | Cooling | 423681.44 | 0
CZ01 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ01 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ01 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXHP | Existing | Fans | 1284781.16 | 0
CZ01 | cDXHP | Existing | Pumps | 92692.51 | 0
CZ01 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ01 | cDXHP | Existing | Humidification | 0 | 0
CZ01 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ01 | cDXHP | Existing | Water Systems | 0 | 1023273.58
CZ01 | cDXHP | Existing | Refrigeration | 0 | 0
CZ01 | cDXHP | Existing | Generators | 0 | 0
CZ01 | cDXHP | Existing | Total End Uses | 8663317.19 | 2108394.97
CZ02 | cDXHP | Existing | Heating | 32667.53 | 933258.49
CZ02 | cDXHP | Existing | Cooling | 1945150.41 | 0
CZ02 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ02 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ02 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXHP | Existing | Fans | 1595836.78 | 0
CZ02 | cDXHP | Existing | Pumps | 127090.05 | 0
CZ02 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ02 | cDXHP | Existing | Humidification | 0 | 0
CZ02 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ02 | cDXHP | Existing | Water Systems | 0 | 940087.89
CZ02 | cDXHP | Existing | Refrigeration | 0 | 0
CZ02 | cDXHP | Existing | Generators | 0 | 0
CZ02 | cDXHP | Existing | Total End Uses | 10526726.29 | 2022684.6
CZ03 | cDXHP | Existing | Heating | 15899.95 | 566948.32
CZ03 | cDXHP | Existing | Cooling | 1356860.97 | 0
CZ03 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ03 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ03 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXHP | Existing | Fans | 1434649.55 | 0
CZ03 | cDXHP | Existing | Pumps | 117482.25 | 0
CZ03 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ03 | cDXHP | Existing | Humidification | 0 | 0
CZ03 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ03 | cDXHP | Existing | Water Systems | 0 | 936341.98
CZ03 | cDXHP | Existing | Refrigeration | 0 | 0
CZ03 | cDXHP | Existing | Generators | 0 | 0
CZ03 | cDXHP | Existing | Total End Uses | 9750874.24 | 1652628.51
CZ04 | cDXHP | Existing | Heating | 14526.18 | 566322.62
CZ04 | cDXHP | Existing | Cooling | 2158967.69 | 0
CZ04 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ04 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ04 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXHP | Existing | Fans | 1644094.35 | 0
CZ04 | cDXHP | Existing | Pumps | 129672.56 | 0
CZ04 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ04 | cDXHP | Existing | Humidification | 0 | 0
CZ04 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ04 | cDXHP | Existing | Water Systems | 0 | 904240.01
CZ04 | cDXHP | Existing | Refrigeration | 0 | 0
CZ04 | cDXHP | Existing | Generators | 0 | 0
CZ04 | cDXHP | Existing | Total End Uses | 10773242.29 | 1619900.85
CZ05 | cDXHP | Existing | Heating | 16714.08 | 589399.37
CZ05 | cDXHP | Existing | Cooling | 1588878.99 | 0
CZ05 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ05 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ05 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXHP | Existing | Fans | 1496822.23 | 0
CZ05 | cDXHP | Existing | Pumps | 113346.33 | 0
CZ05 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ05 | cDXHP | Existing | Humidification | 0 | 0
CZ05 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ05 | cDXHP | Existing | Water Systems | 0 | 936439.75
CZ05 | cDXHP | Existing | Refrigeration | 0 | 0
CZ05 | cDXHP | Existing | Generators | 0 | 0
CZ05 | cDXHP | Existing | Total End Uses | 10041743.14 | 1675177.33
CZ06 | cDXHP | Existing | Heating | 2503.83 | 178763.95
CZ06 | cDXHP | Existing | Cooling | 2523086.72 | 0
CZ06 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ06 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ06 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXHP | Existing | Fans | 1584972.36 | 0
CZ06 | cDXHP | Existing | Pumps | 123729.62 | 0
CZ06 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ06 | cDXHP | Existing | Humidification | 0 | 0
CZ06 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ06 | cDXHP | Existing | Water Systems | 0 | 862423.82
CZ06 | cDXHP | Existing | Refrigeration | 0 | 0
CZ06 | cDXHP | Existing | Generators | 0 | 0
CZ06 | cDXHP | Existing | Total End Uses | 11060274.04 | 1190525.99
CZ07 | cDXHP | Existing | Heating | 2437.89 | 191551.06
CZ07 | cDXHP | Existing | Cooling | 2769447.93 | 0
CZ07 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ07 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ07 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXHP | Existing | Fans | 1608374.94 | 0
CZ07 | cDXHP | Existing | Pumps | 130067.04 | 0
CZ07 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ07 | cDXHP | Existing | Humidification | 0 | 0
CZ07 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ07 | cDXHP | Existing | Water Systems | 0 | 851493.03
CZ07 | cDXHP | Existing | Refrigeration | 0 | 0
CZ07 | cDXHP | Existing | Generators | 0 | 0
CZ07 | cDXHP | Existing | Total End Uses | 11336309.32 | 1192382.3
CZ08 | cDXHP | Existing | Heating | 3954.96 | 296328.3
CZ08 | cDXHP | Existing | Cooling | 3059497.63 | 0
CZ08 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ08 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ08 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXHP | Existing | Fans | 1740357.4 | 0
CZ08 | cDXHP | Existing | Pumps | 137628.87 | 0
CZ08 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ08 | cDXHP | Existing | Humidification | 0 | 0
CZ08 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ08 | cDXHP | Existing | Water Systems | 0 | 850296.93
CZ08 | cDXHP | Existing | Refrigeration | 0 | 0
CZ08 | cDXHP | Existing | Generators | 0 | 0
CZ08 | cDXHP | Existing | Total End Uses | 11767420.38 | 1295963.45
CZ09 | cDXHP | Existing | Heating | 2796.3 | 302467.32
CZ09 | cDXHP | Existing | Cooling | 3363703.46 | 0
CZ09 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ09 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ09 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXHP | Existing | Fans | 1875054.62 | 0
CZ09 | cDXHP | Existing | Pumps | 140342.34 | 0
CZ09 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ09 | cDXHP | Existing | Humidification | 0 | 0
CZ09 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ09 | cDXHP | Existing | Water Systems | 0 | 838488.65
CZ09 | cDXHP | Existing | Refrigeration | 0 | 0
CZ09 | cDXHP | Existing | Generators | 0 | 0
CZ09 | cDXHP | Existing | Total End Uses | 12207878.25 | 1290294.19
CZ10 | cDXHP | Existing | Heating | 12748.39 | 659093.66
CZ10 | cDXHP | Existing | Cooling | 3901570.75 | 0
CZ10 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ10 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ10 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXHP | Existing | Fans | 2070709.36 | 0
CZ10 | cDXHP | Existing | Pumps | 153506.58 | 0
CZ10 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ10 | cDXHP | Existing | Humidification | 0 | 0
CZ10 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ10 | cDXHP | Existing | Water Systems | 0 | 831688.46
CZ10 | cDXHP | Existing | Refrigeration | 0 | 0
CZ10 | cDXHP | Existing | Generators | 0 | 0
CZ10 | cDXHP | Existing | Total End Uses | 12964516.58 | 1640120.33
CZ11 | cDXHP | Existing | Heating | 27805.63 | 1033797.91
CZ11 | cDXHP | Existing | Cooling | 3778184.29 | 0
CZ11 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ11 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ11 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXHP | Existing | Fans | 2005487.44 | 0
CZ11 | cDXHP | Existing | Pumps | 152994.17 | 0
CZ11 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ11 | cDXHP | Existing | Humidification | 0 | 0
CZ11 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ11 | cDXHP | Existing | Water Systems | 0 | 850264.16
CZ11 | cDXHP | Existing | Refrigeration | 0 | 0
CZ11 | cDXHP | Existing | Generators | 0 | 0
CZ11 | cDXHP | Existing | Total End Uses | 12790453.06 | 2033400.29
CZ12 | cDXHP | Existing | Heating | 28424.5 | 935358.6
CZ12 | cDXHP | Existing | Cooling | 3312259.7 | 0
CZ12 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ12 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ12 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXHP | Existing | Fans | 1853013.79 | 0
CZ12 | cDXHP | Existing | Pumps | 149687.25 | 0
CZ12 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ12 | cDXHP | Existing | Humidification | 0 | 0
CZ12 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ12 | cDXHP | Existing | Water Systems | 0 | 874274.28
CZ12 | cDXHP | Existing | Refrigeration | 0 | 0
CZ12 | cDXHP | Existing | Generators | 0 | 0
CZ12 | cDXHP | Existing | Total End Uses | 12169366.75 | 1958971.09
CZ13 | cDXHP | Existing | Heating | 19469.3 | 797345.9
CZ13 | cDXHP | Existing | Cooling | 4116182.21 | 0
CZ13 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ13 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ13 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXHP | Existing | Fans | 2023137.95 | 0
CZ13 | cDXHP | Existing | Pumps | 157872.02 | 0
CZ13 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ13 | cDXHP | Existing | Humidification | 0 | 0
CZ13 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ13 | cDXHP | Existing | Water Systems | 0 | 825503.12
CZ13 | cDXHP | Existing | Refrigeration | 0 | 0
CZ13 | cDXHP | Existing | Generators | 0 | 0
CZ13 | cDXHP | Existing | Total End Uses | 13142643 | 1772187.24
CZ14 | cDXHP | Existing | Heating | 12009.57 | 617452.01
CZ14 | cDXHP | Existing | Cooling | 4790199.29 | 0
CZ14 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ14 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ14 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXHP | Existing | Fans | 2281484.11 | 0
CZ14 | cDXHP | Existing | Pumps | 158590.05 | 0
CZ14 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ14 | cDXHP | Existing | Humidification | 0 | 0
CZ14 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ14 | cDXHP | Existing | Water Systems | 0 | 783621.48
CZ14 | cDXHP | Existing | Refrigeration | 0 | 0
CZ14 | cDXHP | Existing | Generators | 0 | 0
CZ14 | cDXHP | Existing | Total End Uses | 14068264.53 | 1550411.7
CZ15 | cDXHP | Existing | Heating | 3085.45 | 503705.36
CZ15 | cDXHP | Existing | Cooling | 6213160.23 | 0
CZ15 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ15 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ15 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXHP | Existing | Fans | 2319042.2 | 0
CZ15 | cDXHP | Existing | Pumps | 167061.46 | 0
CZ15 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ15 | cDXHP | Existing | Humidification | 0 | 0
CZ15 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ15 | cDXHP | Existing | Water Systems | 0 | 695432.2
CZ15 | cDXHP | Existing | Refrigeration | 0 | 0
CZ15 | cDXHP | Existing | Generators | 0 | 0
CZ15 | cDXHP | Existing | Total End Uses | 15528330.85 | 1348475.78
CZ16 | cDXHP | Existing | Heating | 58955.35 | 1319158.66
CZ16 | cDXHP | Existing | Cooling | 3832558.57 | 0
CZ16 | cDXHP | Existing | Interior Lighting | 2929105.9 | 0
CZ16 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXHP | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ16 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXHP | Existing | Fans | 2304742.68 | 0
CZ16 | cDXHP | Existing | Pumps | 144851.23 | 0
CZ16 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ16 | cDXHP | Existing | Humidification | 0 | 0
CZ16 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ16 | cDXHP | Existing | Water Systems | 0 | 924496.62
CZ16 | cDXHP | Existing | Refrigeration | 0 | 0
CZ16 | cDXHP | Existing | Generators | 0 | 0
CZ16 | cDXHP | Existing | Total End Uses | 13167089.36 | 2392993.49
CZ01 | cDXHP | New Construction | Heating | 42090.99 | 752038
CZ01 | cDXHP | New Construction | Cooling | 323026.01 | 0
CZ01 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ01 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ01 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXHP | New Construction | Fans | 1093962.15 | 0
CZ01 | cDXHP | New Construction | Pumps | 78209.23 | 0
CZ01 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXHP | New Construction | Humidification | 0 | 0
CZ01 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXHP | New Construction | Water Systems | 0 | 1022682.14
CZ01 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ01 | cDXHP | New Construction | Generators | 0 | 0
CZ01 | cDXHP | New Construction | Total End Uses | 7574809.74 | 1924058.36
CZ02 | cDXHP | New Construction | Heating | 57103.17 | 1192573.56
CZ02 | cDXHP | New Construction | Cooling | 1656766.55 | 0
CZ02 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ02 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ02 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXHP | New Construction | Fans | 1408932.19 | 0
CZ02 | cDXHP | New Construction | Pumps | 108876.52 | 0
CZ02 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXHP | New Construction | Humidification | 0 | 0
CZ02 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXHP | New Construction | Water Systems | 0 | 939822.9
CZ02 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ02 | cDXHP | New Construction | Generators | 0 | 0
CZ02 | cDXHP | New Construction | Total End Uses | 9269199.79 | 2281734.68
CZ03 | cDXHP | New Construction | Heating | 29837.26 | 831923.46
CZ03 | cDXHP | New Construction | Cooling | 1161984.92 | 0
CZ03 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ03 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ03 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXHP | New Construction | Fans | 1265816.11 | 0
CZ03 | cDXHP | New Construction | Pumps | 102426.78 | 0
CZ03 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXHP | New Construction | Humidification | 0 | 0
CZ03 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXHP | New Construction | Water Systems | 0 | 936093.19
CZ03 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ03 | cDXHP | New Construction | Generators | 0 | 0
CZ03 | cDXHP | New Construction | Total End Uses | 8597586.41 | 1917354.87
CZ04 | cDXHP | New Construction | Heating | 25561.21 | 793931.88
CZ04 | cDXHP | New Construction | Cooling | 1888624.98 | 0
CZ04 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ04 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ04 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXHP | New Construction | Fans | 1450358.18 | 0
CZ04 | cDXHP | New Construction | Pumps | 115256.14 | 0
CZ04 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXHP | New Construction | Humidification | 0 | 0
CZ04 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXHP | New Construction | Water Systems | 0 | 903947.68
CZ04 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ04 | cDXHP | New Construction | Generators | 0 | 0
CZ04 | cDXHP | New Construction | Total End Uses | 9517321.87 | 1847217.78
CZ05 | cDXHP | New Construction | Heating | 31852.75 | 866722.34
CZ05 | cDXHP | New Construction | Cooling | 1353234.68 | 0
CZ05 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ05 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ05 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXHP | New Construction | Fans | 1309673.9 | 0
CZ05 | cDXHP | New Construction | Pumps | 98505.98 | 0
CZ05 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXHP | New Construction | Humidification | 0 | 0
CZ05 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXHP | New Construction | Water Systems | 0 | 936185.35
CZ05 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ05 | cDXHP | New Construction | Generators | 0 | 0
CZ05 | cDXHP | New Construction | Total End Uses | 8830788.65 | 1952245.91
CZ06 | cDXHP | New Construction | Heating | 5443.11 | 319982.44
CZ06 | cDXHP | New Construction | Cooling | 2145086.48 | 0
CZ06 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ06 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ06 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXHP | New Construction | Fans | 1380060.23 | 0
CZ06 | cDXHP | New Construction | Pumps | 110057.59 | 0
CZ06 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXHP | New Construction | Humidification | 0 | 0
CZ06 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXHP | New Construction | Water Systems | 0 | 862273.17
CZ06 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ06 | cDXHP | New Construction | Generators | 0 | 0
CZ06 | cDXHP | New Construction | Total End Uses | 9678168.76 | 1331593.83
CZ07 | cDXHP | New Construction | Heating | 4749.25 | 304979.32
CZ07 | cDXHP | New Construction | Cooling | 2351442.81 | 0
CZ07 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ07 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ07 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXHP | New Construction | Fans | 1383699.92 | 0
CZ07 | cDXHP | New Construction | Pumps | 114782.97 | 0
CZ07 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXHP | New Construction | Humidification | 0 | 0
CZ07 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXHP | New Construction | Water Systems | 0 | 851239.49
CZ07 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ07 | cDXHP | New Construction | Generators | 0 | 0
CZ07 | cDXHP | New Construction | Total End Uses | 9892196.3 | 1305557.03
CZ08 | cDXHP | New Construction | Heating | 7928.86 | 445921.43
CZ08 | cDXHP | New Construction | Cooling | 2657806.99 | 0
CZ08 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ08 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ08 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXHP | New Construction | Fans | 1521086.36 | 0
CZ08 | cDXHP | New Construction | Pumps | 123991.02 | 0
CZ08 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXHP | New Construction | Humidification | 0 | 0
CZ08 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXHP | New Construction | Water Systems | 0 | 850089.38
CZ08 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ08 | cDXHP | New Construction | Generators | 0 | 0
CZ08 | cDXHP | New Construction | Total End Uses | 10348334.58 | 1445349.02
CZ09 | cDXHP | New Construction | Heating | 5681.83 | 431110.29
CZ09 | cDXHP | New Construction | Cooling | 2937134.66 | 0
CZ09 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ09 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ09 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXHP | New Construction | Fans | 1645314.24 | 0
CZ09 | cDXHP | New Construction | Pumps | 127183.99 | 0
CZ09 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXHP | New Construction | Humidification | 0 | 0
CZ09 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXHP | New Construction | Water Systems | 0 | 838283.29
CZ09 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ09 | cDXHP | New Construction | Generators | 0 | 0
CZ09 | cDXHP | New Construction | Total End Uses | 10752836.06 | 1418731.79
CZ10 | cDXHP | New Construction | Heating | 20017.92 | 711219.24
CZ10 | cDXHP | New Construction | Cooling | 3399291.22 | 0
CZ10 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ10 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ10 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXHP | New Construction | Fans | 1793296.18 | 0
CZ10 | cDXHP | New Construction | Pumps | 136437.97 | 0
CZ10 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXHP | New Construction | Humidification | 0 | 0
CZ10 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXHP | New Construction | Water Systems | 0 | 831508.09
CZ10 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ10 | cDXHP | New Construction | Generators | 0 | 0
CZ10 | cDXHP | New Construction | Total End Uses | 11386564.63 | 1692065.56
CZ11 | cDXHP | New Construction | Heating | 25950.65 | 607262.32
CZ11 | cDXHP | New Construction | Cooling | 2994427.41 | 0
CZ11 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ11 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ11 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXHP | New Construction | Fans | 1526305.81 | 0
CZ11 | cDXHP | New Construction | Pumps | 126054.82 | 0
CZ11 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXHP | New Construction | Humidification | 0 | 0
CZ11 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXHP | New Construction | Water Systems | 0 | 849810.04
CZ11 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ11 | cDXHP | New Construction | Generators | 0 | 0
CZ11 | cDXHP | New Construction | Total End Uses | 10710260.04 | 1606410.58
CZ12 | cDXHP | New Construction | Heating | 30243.16 | 624804.45
CZ12 | cDXHP | New Construction | Cooling | 2666121.75 | 0
CZ12 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ12 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ12 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXHP | New Construction | Fans | 1455803.94 | 0
CZ12 | cDXHP | New Construction | Pumps | 125808.87 | 0
CZ12 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXHP | New Construction | Humidification | 0 | 0
CZ12 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXHP | New Construction | Water Systems | 0 | 873798.14
CZ12 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ12 | cDXHP | New Construction | Generators | 0 | 0
CZ12 | cDXHP | New Construction | Total End Uses | 10315499.07 | 1647940.8
CZ13 | cDXHP | New Construction | Heating | 20347.8 | 513867.16
CZ13 | cDXHP | New Construction | Cooling | 3283425.28 | 0
CZ13 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ13 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ13 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXHP | New Construction | Fans | 1566082.57 | 0
CZ13 | cDXHP | New Construction | Pumps | 131576.34 | 0
CZ13 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXHP | New Construction | Humidification | 0 | 0
CZ13 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXHP | New Construction | Water Systems | 0 | 824978.38
CZ13 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ13 | cDXHP | New Construction | Generators | 0 | 0
CZ13 | cDXHP | New Construction | Total End Uses | 11038953.35 | 1488183.76
CZ14 | cDXHP | New Construction | Heating | 13633.53 | 440464.63
CZ14 | cDXHP | New Construction | Cooling | 3846042.88 | 0
CZ14 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ14 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ14 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXHP | New Construction | Fans | 1759050.84 | 0
CZ14 | cDXHP | New Construction | Pumps | 131231.48 | 0
CZ14 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXHP | New Construction | Humidification | 0 | 0
CZ14 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXHP | New Construction | Water Systems | 0 | 783065.76
CZ14 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ14 | cDXHP | New Construction | Generators | 0 | 0
CZ14 | cDXHP | New Construction | Total End Uses | 11787480.07 | 1372868.62
CZ15 | cDXHP | New Construction | Heating | 3934.02 | 412852.22
CZ15 | cDXHP | New Construction | Cooling | 5035956.4 | 0
CZ15 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ15 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ15 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXHP | New Construction | Fans | 1773676.84 | 0
CZ15 | cDXHP | New Construction | Pumps | 138842.8 | 0
CZ15 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXHP | New Construction | Humidification | 0 | 0
CZ15 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXHP | New Construction | Water Systems | 0 | 694926.74
CZ15 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ15 | cDXHP | New Construction | Generators | 0 | 0
CZ15 | cDXHP | New Construction | Total End Uses | 12989931.4 | 1257117.18
CZ16 | cDXHP | New Construction | Heating | 64033.07 | 813596.91
CZ16 | cDXHP | New Construction | Cooling | 3033428.67 | 0
CZ16 | cDXHP | New Construction | Interior Lighting | 2140645.73 | 0
CZ16 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXHP | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ16 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXHP | New Construction | Fans | 1792860.96 | 0
CZ16 | cDXHP | New Construction | Pumps | 119181.83 | 0
CZ16 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXHP | New Construction | Humidification | 0 | 0
CZ16 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXHP | New Construction | Water Systems | 0 | 924193.12
CZ16 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ16 | cDXHP | New Construction | Generators | 0 | 0
CZ16 | cDXHP | New Construction | Total End Uses | 11047025.88 | 1887128.24
CZ01 | cDXOH | Existing | Heating | 0 | 959435.67
CZ01 | cDXOH | Existing | Cooling | 421979.27 | 0
CZ01 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ01 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ01 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXOH | Existing | Fans | 1285427.26 | 0
CZ01 | cDXOH | Existing | Pumps | 92143.19 | 0
CZ01 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ01 | cDXOH | Existing | Humidification | 0 | 0
CZ01 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ01 | cDXOH | Existing | Water Systems | 0 | 1023238.16
CZ01 | cDXOH | Existing | Refrigeration | 0 | 0
CZ01 | cDXOH | Existing | Generators | 0 | 0
CZ01 | cDXOH | Existing | Total End Uses | 8625531.23 | 2132012.04
CZ02 | cDXOH | Existing | Heating | 0 | 948602.96
CZ02 | cDXOH | Existing | Cooling | 1944424.87 | 0
CZ02 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ02 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ02 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXOH | Existing | Fans | 1596253.91 | 0
CZ02 | cDXOH | Existing | Pumps | 126586.99 | 0
CZ02 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ02 | cDXOH | Existing | Humidification | 0 | 0
CZ02 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ02 | cDXOH | Existing | Water Systems | 0 | 940102.83
CZ02 | cDXOH | Existing | Refrigeration | 0 | 0
CZ02 | cDXOH | Existing | Generators | 0 | 0
CZ02 | cDXOH | Existing | Total End Uses | 10493247.28 | 2038044.01
CZ03 | cDXOH | Existing | Heating | 0 | 574725.69
CZ03 | cDXOH | Existing | Cooling | 1356905.62 | 0
CZ03 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ03 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ03 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXOH | Existing | Fans | 1434668.9 | 0
CZ03 | cDXOH | Existing | Pumps | 117255.19 | 0
CZ03 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ03 | cDXOH | Existing | Humidification | 0 | 0
CZ03 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ03 | cDXOH | Existing | Water Systems | 0 | 936322.61
CZ03 | cDXOH | Existing | Refrigeration | 0 | 0
CZ03 | cDXOH | Existing | Generators | 0 | 0
CZ03 | cDXOH | Existing | Total End Uses | 9734811.23 | 1660386.52
CZ04 | cDXOH | Existing | Heating | 0 | 572825.82
CZ04 | cDXOH | Existing | Cooling | 2158961.78 | 0
CZ04 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ04 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ04 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXOH | Existing | Fans | 1644137.29 | 0
CZ04 | cDXOH | Existing | Pumps | 129497.9 | 0
CZ04 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ04 | cDXOH | Existing | Humidification | 0 | 0
CZ04 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ04 | cDXOH | Existing | Water Systems | 0 | 904247.23
CZ04 | cDXOH | Existing | Refrigeration | 0 | 0
CZ04 | cDXOH | Existing | Generators | 0 | 0
CZ04 | cDXOH | Existing | Total End Uses | 10758578.49 | 1626411.27
CZ05 | cDXOH | Existing | Heating | 0 | 597026.86
CZ05 | cDXOH | Existing | Cooling | 1588746.4 | 0
CZ05 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ05 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ05 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXOH | Existing | Fans | 1496806.99 | 0
CZ05 | cDXOH | Existing | Pumps | 113253.14 | 0
CZ05 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ05 | cDXOH | Existing | Humidification | 0 | 0
CZ05 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ05 | cDXOH | Existing | Water Systems | 0 | 936437.8
CZ05 | cDXOH | Existing | Refrigeration | 0 | 0
CZ05 | cDXOH | Existing | Generators | 0 | 0
CZ05 | cDXOH | Existing | Total End Uses | 10024788.05 | 1682802.88
CZ06 | cDXOH | Existing | Heating | 0 | 179506.64
CZ06 | cDXOH | Existing | Cooling | 2531253.45 | 0
CZ06 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ06 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ06 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXOH | Existing | Fans | 1584914.93 | 0
CZ06 | cDXOH | Existing | Pumps | 123732 | 0
CZ06 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ06 | cDXOH | Existing | Humidification | 0 | 0
CZ06 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ06 | cDXOH | Existing | Water Systems | 0 | 862428.95
CZ06 | cDXOH | Existing | Refrigeration | 0 | 0
CZ06 | cDXOH | Existing | Generators | 0 | 0
CZ06 | cDXOH | Existing | Total End Uses | 11065881.91 | 1191273.81
CZ07 | cDXOH | Existing | Heating | 0 | 192396.64
CZ07 | cDXOH | Existing | Cooling | 2774907.9 | 0
CZ07 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ07 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ07 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXOH | Existing | Fans | 1608326.52 | 0
CZ07 | cDXOH | Existing | Pumps | 130061.93 | 0
CZ07 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ07 | cDXOH | Existing | Humidification | 0 | 0
CZ07 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ07 | cDXOH | Existing | Water Systems | 0 | 851430.77
CZ07 | cDXOH | Existing | Refrigeration | 0 | 0
CZ07 | cDXOH | Existing | Generators | 0 | 0
CZ07 | cDXOH | Existing | Total End Uses | 11339277.87 | 1193165.63
CZ08 | cDXOH | Existing | Heating | 0 | 297890.89
CZ08 | cDXOH | Existing | Cooling | 3062744.61 | 0
CZ08 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ08 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ08 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXOH | Existing | Fans | 1740325.27 | 0
CZ08 | cDXOH | Existing | Pumps | 137608.63 | 0
CZ08 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ08 | cDXOH | Existing | Humidification | 0 | 0
CZ08 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ08 | cDXOH | Existing | Water Systems | 0 | 850259.39
CZ08 | cDXOH | Existing | Refrigeration | 0 | 0
CZ08 | cDXOH | Existing | Generators | 0 | 0
CZ08 | cDXOH | Existing | Total End Uses | 11766660.02 | 1297488.49
CZ09 | cDXOH | Existing | Heating | 0 | 303436.95
CZ09 | cDXOH | Existing | Cooling | 3367040.27 | 0
CZ09 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ09 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ09 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXOH | Existing | Fans | 1874998.61 | 0
CZ09 | cDXOH | Existing | Pumps | 140324.97 | 0
CZ09 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ09 | cDXOH | Existing | Humidification | 0 | 0
CZ09 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ09 | cDXOH | Existing | Water Systems | 0 | 838490.84
CZ09 | cDXOH | Existing | Refrigeration | 0 | 0
CZ09 | cDXOH | Existing | Generators | 0 | 0
CZ09 | cDXOH | Existing | Total End Uses | 12208345.37 | 1291266.01
CZ10 | cDXOH | Existing | Heating | 0 | 664110.99
CZ10 | cDXOH | Existing | Cooling | 3900756.97 | 0
CZ10 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ10 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ10 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXOH | Existing | Fans | 2070743.9 | 0
CZ10 | cDXOH | Existing | Pumps | 153348.84 | 0
CZ10 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ10 | cDXOH | Existing | Humidification | 0 | 0
CZ10 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ10 | cDXOH | Existing | Water Systems | 0 | 831702.06
CZ10 | cDXOH | Existing | Refrigeration | 0 | 0
CZ10 | cDXOH | Existing | Generators | 0 | 0
CZ10 | cDXOH | Existing | Total End Uses | 12950831.23 | 1645151.26
CZ11 | cDXOH | Existing | Heating | 0 | 1047675.46
CZ11 | cDXOH | Existing | Cooling | 3771511.77 | 0
CZ11 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ11 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ11 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXOH | Existing | Fans | 2006483.38 | 0
CZ11 | cDXOH | Existing | Pumps | 152500.91 | 0
CZ11 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ11 | cDXOH | Existing | Humidification | 0 | 0
CZ11 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ11 | cDXOH | Existing | Water Systems | 0 | 850275.79
CZ11 | cDXOH | Existing | Refrigeration | 0 | 0
CZ11 | cDXOH | Existing | Generators | 0 | 0
CZ11 | cDXOH | Existing | Total End Uses | 12756477.58 | 2047289.47
CZ12 | cDXOH | Existing | Heating | 0 | 949100.6
CZ12 | cDXOH | Existing | Cooling | 3308060.37 | 0
CZ12 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ12 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ12 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXOH | Existing | Fans | 1853695.69 | 0
CZ12 | cDXOH | Existing | Pumps | 149199.69 | 0
CZ12 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ12 | cDXOH | Existing | Humidification | 0 | 0
CZ12 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ12 | cDXOH | Existing | Water Systems | 0 | 874265.58
CZ12 | cDXOH | Existing | Refrigeration | 0 | 0
CZ12 | cDXOH | Existing | Generators | 0 | 0
CZ12 | cDXOH | Existing | Total End Uses | 12136937.27 | 1972704.39
CZ13 | cDXOH | Existing | Heating | 0 | 809100.63
CZ13 | cDXOH | Existing | Cooling | 4112392.81 | 0
CZ13 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ13 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ13 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXOH | Existing | Fans | 2023731.95 | 0
CZ13 | cDXOH | Existing | Pumps | 157626.02 | 0
CZ13 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ13 | cDXOH | Existing | Humidification | 0 | 0
CZ13 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ13 | cDXOH | Existing | Water Systems | 0 | 825484.99
CZ13 | cDXOH | Existing | Refrigeration | 0 | 0
CZ13 | cDXOH | Existing | Generators | 0 | 0
CZ13 | cDXOH | Existing | Total End Uses | 13119732.29 | 1783923.83
CZ14 | cDXOH | Existing | Heating | 0 | 623387.91
CZ14 | cDXOH | Existing | Cooling | 4785699.29 | 0
CZ14 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ14 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ14 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXOH | Existing | Fans | 2281466.96 | 0
CZ14 | cDXOH | Existing | Pumps | 158500.55 | 0
CZ14 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ14 | cDXOH | Existing | Humidification | 0 | 0
CZ14 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ14 | cDXOH | Existing | Water Systems | 0 | 783551.49
CZ14 | cDXOH | Existing | Refrigeration | 0 | 0
CZ14 | cDXOH | Existing | Generators | 0 | 0
CZ14 | cDXOH | Existing | Total End Uses | 14051648.32 | 1556277.62
CZ15 | cDXOH | Existing | Heating | 0 | 504407.47
CZ15 | cDXOH | Existing | Cooling | 6212500.72 | 0
CZ15 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ15 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ15 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXOH | Existing | Fans | 2318958.31 | 0
CZ15 | cDXOH | Existing | Pumps | 167059.35 | 0
CZ15 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ15 | cDXOH | Existing | Humidification | 0 | 0
CZ15 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ15 | cDXOH | Existing | Water Systems | 0 | 695461.44
CZ15 | cDXOH | Existing | Refrigeration | 0 | 0
CZ15 | cDXOH | Existing | Generators | 0 | 0
CZ15 | cDXOH | Existing | Total End Uses | 15524499.9 | 1349207.12
CZ16 | cDXOH | Existing | Heating | 0 | 1342950.42
CZ16 | cDXOH | Existing | Cooling | 3823553.08 | 0
CZ16 | cDXOH | Existing | Interior Lighting | 2929105.9 | 0
CZ16 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXOH | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ16 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXOH | Existing | Fans | 2307389.76 | 0
CZ16 | cDXOH | Existing | Pumps | 144401.25 | 0
CZ16 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ16 | cDXOH | Existing | Humidification | 0 | 0
CZ16 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ16 | cDXOH | Existing | Water Systems | 0 | 924528.54
CZ16 | cDXOH | Existing | Refrigeration | 0 | 0
CZ16 | cDXOH | Existing | Generators | 0 | 0
CZ16 | cDXOH | Existing | Total End Uses | 13101325.6 | 2416817.18
CZ01 | cDXOH | New Construction | Heating | 0 | 784589.86
CZ01 | cDXOH | New Construction | Cooling | 319965.71 | 0
CZ01 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ01 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ01 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXOH | New Construction | Fans | 1094999.83 | 0
CZ01 | cDXOH | New Construction | Pumps | 77366.17 | 0
CZ01 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXOH | New Construction | Humidification | 0 | 0
CZ01 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXOH | New Construction | Water Systems | 0 | 1022586.11
CZ01 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ01 | cDXOH | New Construction | Generators | 0 | 0
CZ01 | cDXOH | New Construction | Total End Uses | 7529853.06 | 1956514.19
CZ02 | cDXOH | New Construction | Heating | 0 | 1214479.41
CZ02 | cDXOH | New Construction | Cooling | 1654994.54 | 0
CZ02 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ02 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ02 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXOH | New Construction | Fans | 1411256.87 | 0
CZ02 | cDXOH | New Construction | Pumps | 108092.01 | 0
CZ02 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXOH | New Construction | Humidification | 0 | 0
CZ02 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXOH | New Construction | Water Systems | 0 | 939771.81
CZ02 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ02 | cDXOH | New Construction | Generators | 0 | 0
CZ02 | cDXOH | New Construction | Total End Uses | 9211864.77 | 2303589.44
CZ03 | cDXOH | New Construction | Heating | 0 | 842945
CZ03 | cDXOH | New Construction | Cooling | 1161713.92 | 0
CZ03 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ03 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ03 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXOH | New Construction | Fans | 1265966.56 | 0
CZ03 | cDXOH | New Construction | Pumps | 101942.55 | 0
CZ03 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXOH | New Construction | Humidification | 0 | 0
CZ03 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXOH | New Construction | Water Systems | 0 | 936110.22
CZ03 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ03 | cDXOH | New Construction | Generators | 0 | 0
CZ03 | cDXOH | New Construction | Total End Uses | 8567144.39 | 1928393.44
CZ04 | cDXOH | New Construction | Heating | 0 | 802844.77
CZ04 | cDXOH | New Construction | Cooling | 1887846.58 | 0
CZ04 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ04 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ04 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXOH | New Construction | Fans | 1450467.43 | 0
CZ04 | cDXOH | New Construction | Pumps | 114694.45 | 0
CZ04 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXOH | New Construction | Humidification | 0 | 0
CZ04 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXOH | New Construction | Water Systems | 0 | 903934.68
CZ04 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ04 | cDXOH | New Construction | Generators | 0 | 0
CZ04 | cDXOH | New Construction | Total End Uses | 9490529.8 | 1856117.68
CZ05 | cDXOH | New Construction | Heating | 0 | 877009.32
CZ05 | cDXOH | New Construction | Cooling | 1351363.35 | 0
CZ05 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ05 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ05 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXOH | New Construction | Fans | 1309715.43 | 0
CZ05 | cDXOH | New Construction | Pumps | 98122.72 | 0
CZ05 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXOH | New Construction | Humidification | 0 | 0
CZ05 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXOH | New Construction | Water Systems | 0 | 936166.37
CZ05 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ05 | cDXOH | New Construction | Generators | 0 | 0
CZ05 | cDXOH | New Construction | Total End Uses | 8796722.85 | 1962513.9
CZ06 | cDXOH | New Construction | Heating | 0 | 321394.63
CZ06 | cDXOH | New Construction | Cooling | 2152994.18 | 0
CZ06 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ06 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ06 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXOH | New Construction | Fans | 1379958.72 | 0
CZ06 | cDXOH | New Construction | Pumps | 109937.11 | 0
CZ06 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXOH | New Construction | Humidification | 0 | 0
CZ06 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXOH | New Construction | Water Systems | 0 | 862281.89
CZ06 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ06 | cDXOH | New Construction | Generators | 0 | 0
CZ06 | cDXOH | New Construction | Total End Uses | 9680411.37 | 1333014.74
CZ07 | cDXOH | New Construction | Heating | 0 | 306221.36
CZ07 | cDXOH | New Construction | Cooling | 2356995.24 | 0
CZ07 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ07 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ07 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXOH | New Construction | Fans | 1383642.35 | 0
CZ07 | cDXOH | New Construction | Pumps | 114728.94 | 0
CZ07 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXOH | New Construction | Humidification | 0 | 0
CZ07 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXOH | New Construction | Water Systems | 0 | 851233.17
CZ07 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ07 | cDXOH | New Construction | Generators | 0 | 0
CZ07 | cDXOH | New Construction | Total End Uses | 9892887.87 | 1306792.75
CZ08 | cDXOH | New Construction | Heating | 0 | 448130.25
CZ08 | cDXOH | New Construction | Cooling | 2660565.55 | 0
CZ08 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ08 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ08 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXOH | New Construction | Fans | 1520999.78 | 0
CZ08 | cDXOH | New Construction | Pumps | 123842.52 | 0
CZ08 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXOH | New Construction | Humidification | 0 | 0
CZ08 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXOH | New Construction | Water Systems | 0 | 850076.34
CZ08 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ08 | cDXOH | New Construction | Generators | 0 | 0
CZ08 | cDXOH | New Construction | Total End Uses | 10342929.2 | 1447544.81
CZ09 | cDXOH | New Construction | Heating | 0 | 432742.72
CZ09 | cDXOH | New Construction | Cooling | 2940414.15 | 0
CZ09 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ09 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ09 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXOH | New Construction | Fans | 1645179.25 | 0
CZ09 | cDXOH | New Construction | Pumps | 127096.07 | 0
CZ09 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXOH | New Construction | Humidification | 0 | 0
CZ09 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXOH | New Construction | Water Systems | 0 | 838298.33
CZ09 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ09 | cDXOH | New Construction | Generators | 0 | 0
CZ09 | cDXOH | New Construction | Total End Uses | 10750210.82 | 1420379.27
CZ10 | cDXOH | New Construction | Heating | 0 | 717291.5
CZ10 | cDXOH | New Construction | Cooling | 3397371.55 | 0
CZ10 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ10 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ10 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXOH | New Construction | Fans | 1793412.23 | 0
CZ10 | cDXOH | New Construction | Pumps | 136009.77 | 0
CZ10 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXOH | New Construction | Humidification | 0 | 0
CZ10 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXOH | New Construction | Water Systems | 0 | 831584.7
CZ10 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ10 | cDXOH | New Construction | Generators | 0 | 0
CZ10 | cDXOH | New Construction | Total End Uses | 11364314.9 | 1698214.42
CZ11 | cDXOH | New Construction | Heating | 0 | 627454.18
CZ11 | cDXOH | New Construction | Cooling | 2988946.71 | 0
CZ11 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ11 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ11 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXOH | New Construction | Fans | 1526617.38 | 0
CZ11 | cDXOH | New Construction | Pumps | 125798.99 | 0
CZ11 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXOH | New Construction | Humidification | 0 | 0
CZ11 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXOH | New Construction | Water Systems | 0 | 849815.58
CZ11 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ11 | cDXOH | New Construction | Generators | 0 | 0
CZ11 | cDXOH | New Construction | Total End Uses | 10678884.42 | 1626607.98
CZ12 | cDXOH | New Construction | Heating | 0 | 646448.91
CZ12 | cDXOH | New Construction | Cooling | 2661360.5 | 0
CZ12 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ12 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ12 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXOH | New Construction | Fans | 1456385.61 | 0
CZ12 | cDXOH | New Construction | Pumps | 125375.3 | 0
CZ12 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXOH | New Construction | Humidification | 0 | 0
CZ12 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXOH | New Construction | Water Systems | 0 | 873872.27
CZ12 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ12 | cDXOH | New Construction | Generators | 0 | 0
CZ12 | cDXOH | New Construction | Total End Uses | 10280642.76 | 1669659.4
CZ13 | cDXOH | New Construction | Heating | 0 | 528046.15
CZ13 | cDXOH | New Construction | Cooling | 3279774.71 | 0
CZ13 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ13 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ13 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXOH | New Construction | Fans | 1566208.85 | 0
CZ13 | cDXOH | New Construction | Pumps | 131264.38 | 0
CZ13 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXOH | New Construction | Humidification | 0 | 0
CZ13 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXOH | New Construction | Water Systems | 0 | 825080.91
CZ13 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ13 | cDXOH | New Construction | Generators | 0 | 0
CZ13 | cDXOH | New Construction | Total End Uses | 11014769.3 | 1502465.28
CZ14 | cDXOH | New Construction | Heating | 0 | 447400.52
CZ14 | cDXOH | New Construction | Cooling | 3841503.53 | 0
CZ14 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ14 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ14 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXOH | New Construction | Fans | 1758954.17 | 0
CZ14 | cDXOH | New Construction | Pumps | 131412.94 | 0
CZ14 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXOH | New Construction | Humidification | 0 | 0
CZ14 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXOH | New Construction | Water Systems | 0 | 783119.59
CZ14 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ14 | cDXOH | New Construction | Generators | 0 | 0
CZ14 | cDXOH | New Construction | Total End Uses | 11769392 | 1379858.33
CZ15 | cDXOH | New Construction | Heating | 0 | 413764.84
CZ15 | cDXOH | New Construction | Cooling | 5034410.11 | 0
CZ15 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ15 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ15 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXOH | New Construction | Fans | 1773508.2 | 0
CZ15 | cDXOH | New Construction | Pumps | 138832.57 | 0
CZ15 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXOH | New Construction | Humidification | 0 | 0
CZ15 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXOH | New Construction | Water Systems | 0 | 694879.98
CZ15 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ15 | cDXOH | New Construction | Generators | 0 | 0
CZ15 | cDXOH | New Construction | Total End Uses | 12984272.22 | 1257983.04
CZ16 | cDXOH | New Construction | Heating | 0 | 849675.67
CZ16 | cDXOH | New Construction | Cooling | 3022727.13 | 0
CZ16 | cDXOH | New Construction | Interior Lighting | 2140645.73 | 0
CZ16 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXOH | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ16 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXOH | New Construction | Fans | 1792967.77 | 0
CZ16 | cDXOH | New Construction | Pumps | 119195.57 | 0
CZ16 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXOH | New Construction | Humidification | 0 | 0
CZ16 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXOH | New Construction | Water Systems | 0 | 924182.62
CZ16 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ16 | cDXOH | New Construction | Generators | 0 | 0
CZ16 | cDXOH | New Construction | Total End Uses | 10972411.82 | 1923196.51
CZ01 | cPVVG | Existing | Heating | 0 | 1188855.86
CZ01 | cPVVG | Existing | Cooling | 426975.58 | 0
CZ01 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ01 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ01 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ01 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ01 | cPVVG | Existing | Fans | 782406.58 | 0
CZ01 | cPVVG | Existing | Pumps | 92559.39 | 0
CZ01 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ01 | cPVVG | Existing | Humidification | 0 | 0
CZ01 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ01 | cPVVG | Existing | Water Systems | 0 | 1023195.88
CZ01 | cPVVG | Existing | Refrigeration | 0 | 0
CZ01 | cPVVG | Existing | Generators | 0 | 0
CZ01 | cPVVG | Existing | Total End Uses | 8127923.07 | 2361389.96
CZ02 | cPVVG | Existing | Heating | 0 | 1137341.79
CZ02 | cPVVG | Existing | Cooling | 1937432.87 | 0
CZ02 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ02 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ02 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ02 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ02 | cPVVG | Existing | Fans | 1072362.61 | 0
CZ02 | cPVVG | Existing | Pumps | 126928.58 | 0
CZ02 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ02 | cPVVG | Existing | Humidification | 0 | 0
CZ02 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ02 | cPVVG | Existing | Water Systems | 0 | 940113.09
CZ02 | cPVVG | Existing | Refrigeration | 0 | 0
CZ02 | cPVVG | Existing | Generators | 0 | 0
CZ02 | cPVVG | Existing | Total End Uses | 9962705.57 | 2226793.1
CZ03 | cPVVG | Existing | Heating | 0 | 687968.06
CZ03 | cPVVG | Existing | Cooling | 1366874.36 | 0
CZ03 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ03 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ03 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ03 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ03 | cPVVG | Existing | Fans | 915038.87 | 0
CZ03 | cPVVG | Existing | Pumps | 117380.47 | 0
CZ03 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ03 | cPVVG | Existing | Humidification | 0 | 0
CZ03 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ03 | cPVVG | Existing | Water Systems | 0 | 936344.07
CZ03 | cPVVG | Existing | Refrigeration | 0 | 0
CZ03 | cPVVG | Existing | Generators | 0 | 0
CZ03 | cPVVG | Existing | Total End Uses | 9225275.21 | 1773650.35
CZ04 | cPVVG | Existing | Heating | 0 | 679518.82
CZ04 | cPVVG | Existing | Cooling | 2150996.68 | 0
CZ04 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ04 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ04 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ04 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ04 | cPVVG | Existing | Fans | 1124881.71 | 0
CZ04 | cPVVG | Existing | Pumps | 129628.75 | 0
CZ04 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ04 | cPVVG | Existing | Humidification | 0 | 0
CZ04 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ04 | cPVVG | Existing | Water Systems | 0 | 904236.77
CZ04 | cPVVG | Existing | Refrigeration | 0 | 0
CZ04 | cPVVG | Existing | Generators | 0 | 0
CZ04 | cPVVG | Existing | Total End Uses | 10231488.66 | 1733093.81
CZ05 | cPVVG | Existing | Heating | 0 | 707539.56
CZ05 | cPVVG | Existing | Cooling | 1591608.13 | 0
CZ05 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ05 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ05 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ05 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ05 | cPVVG | Existing | Fans | 988191.58 | 0
CZ05 | cPVVG | Existing | Pumps | 113325.89 | 0
CZ05 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ05 | cPVVG | Existing | Humidification | 0 | 0
CZ05 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ05 | cPVVG | Existing | Water Systems | 0 | 936399.95
CZ05 | cPVVG | Existing | Refrigeration | 0 | 0
CZ05 | cPVVG | Existing | Generators | 0 | 0
CZ05 | cPVVG | Existing | Total End Uses | 9519107.12 | 1793277.73
CZ06 | cPVVG | Existing | Heating | 0 | 206264.77
CZ06 | cPVVG | Existing | Cooling | 2537014.93 | 0
CZ06 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ06 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ06 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ06 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ06 | cPVVG | Existing | Fans | 1095017.1 | 0
CZ06 | cPVVG | Existing | Pumps | 123732.54 | 0
CZ06 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ06 | cPVVG | Existing | Humidification | 0 | 0
CZ06 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ06 | cPVVG | Existing | Water Systems | 0 | 862421.15
CZ06 | cPVVG | Existing | Refrigeration | 0 | 0
CZ06 | cPVVG | Existing | Generators | 0 | 0
CZ06 | cPVVG | Existing | Total End Uses | 10581746.08 | 1218024.14
CZ07 | cPVVG | Existing | Heating | 0 | 217587.22
CZ07 | cPVVG | Existing | Cooling | 2764758.17 | 0
CZ07 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ07 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ07 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ07 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ07 | cPVVG | Existing | Fans | 1125315.25 | 0
CZ07 | cPVVG | Existing | Pumps | 130049.92 | 0
CZ07 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ07 | cPVVG | Existing | Humidification | 0 | 0
CZ07 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ07 | cPVVG | Existing | Water Systems | 0 | 851471.89
CZ07 | cPVVG | Existing | Refrigeration | 0 | 0
CZ07 | cPVVG | Existing | Generators | 0 | 0
CZ07 | cPVVG | Existing | Total End Uses | 10846104.85 | 1218397.33
CZ08 | cPVVG | Existing | Heating | 0 | 334850.62
CZ08 | cPVVG | Existing | Cooling | 3049711.41 | 0
CZ08 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ08 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ08 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ08 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ08 | cPVVG | Existing | Fans | 1244787.81 | 0
CZ08 | cPVVG | Existing | Pumps | 137631.36 | 0
CZ08 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ08 | cPVVG | Existing | Humidification | 0 | 0
CZ08 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ08 | cPVVG | Existing | Water Systems | 0 | 850252.19
CZ08 | cPVVG | Existing | Refrigeration | 0 | 0
CZ08 | cPVVG | Existing | Generators | 0 | 0
CZ08 | cPVVG | Existing | Total End Uses | 11258112.1 | 1334441.02
CZ09 | cPVVG | Existing | Heating | 0 | 333854.77
CZ09 | cPVVG | Existing | Cooling | 3346958.35 | 0
CZ09 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ09 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ09 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ09 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ09 | cPVVG | Existing | Fans | 1372380.46 | 0
CZ09 | cPVVG | Existing | Pumps | 140328.82 | 0
CZ09 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ09 | cPVVG | Existing | Humidification | 0 | 0
CZ09 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ09 | cPVVG | Existing | Water Systems | 0 | 838490.04
CZ09 | cPVVG | Existing | Refrigeration | 0 | 0
CZ09 | cPVVG | Existing | Generators | 0 | 0
CZ09 | cPVVG | Existing | Total End Uses | 11685649.14 | 1321683.03
CZ10 | cPVVG | Existing | Heating | 0 | 751906.47
CZ10 | cPVVG | Existing | Cooling | 3864727.89 | 0
CZ10 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ10 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ10 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ10 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ10 | cPVVG | Existing | Fans | 1543098.92 | 0
CZ10 | cPVVG | Existing | Pumps | 153466.95 | 0
CZ10 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ10 | cPVVG | Existing | Humidification | 0 | 0
CZ10 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ10 | cPVVG | Existing | Water Systems | 0 | 831717.2
CZ10 | cPVVG | Existing | Refrigeration | 0 | 0
CZ10 | cPVVG | Existing | Generators | 0 | 0
CZ10 | cPVVG | Existing | Total End Uses | 12387275.27 | 1732961.89
CZ11 | cPVVG | Existing | Heating | 0 | 1224404.87
CZ11 | cPVVG | Existing | Cooling | 3740520.5 | 0
CZ11 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ11 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ11 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ11 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ11 | cPVVG | Existing | Fans | 1501822.84 | 0
CZ11 | cPVVG | Existing | Pumps | 152925.65 | 0
CZ11 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ11 | cPVVG | Existing | Humidification | 0 | 0
CZ11 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ11 | cPVVG | Existing | Water Systems | 0 | 850270
CZ11 | cPVVG | Existing | Refrigeration | 0 | 0
CZ11 | cPVVG | Existing | Generators | 0 | 0
CZ11 | cPVVG | Existing | Total End Uses | 12221250.5 | 2224013.09
CZ12 | cPVVG | Existing | Heating | 0 | 1118393.1
CZ12 | cPVVG | Existing | Cooling | 3283523.05 | 0
CZ12 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ12 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ12 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ12 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ12 | cPVVG | Existing | Fans | 1359849.88 | 0
CZ12 | cPVVG | Existing | Pumps | 149535.06 | 0
CZ12 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ12 | cPVVG | Existing | Humidification | 0 | 0
CZ12 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ12 | cPVVG | Existing | Water Systems | 0 | 874266.43
CZ12 | cPVVG | Existing | Refrigeration | 0 | 0
CZ12 | cPVVG | Existing | Generators | 0 | 0
CZ12 | cPVVG | Existing | Total End Uses | 11618889.5 | 2141997.74
CZ13 | cPVVG | Existing | Heating | 0 | 939631.62
CZ13 | cPVVG | Existing | Cooling | 4077762.68 | 0
CZ13 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ13 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ13 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ13 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ13 | cPVVG | Existing | Fans | 1533976.86 | 0
CZ13 | cPVVG | Existing | Pumps | 157745.41 | 0
CZ13 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ13 | cPVVG | Existing | Humidification | 0 | 0
CZ13 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ13 | cPVVG | Existing | Water Systems | 0 | 825490.68
CZ13 | cPVVG | Existing | Refrigeration | 0 | 0
CZ13 | cPVVG | Existing | Generators | 0 | 0
CZ13 | cPVVG | Existing | Total End Uses | 12595466.46 | 1914460.52
CZ14 | cPVVG | Existing | Heating | 0 | 705751.17
CZ14 | cPVVG | Existing | Cooling | 4740232.05 | 0
CZ14 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ14 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ14 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ14 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ14 | cPVVG | Existing | Fans | 1791964.72 | 0
CZ14 | cPVVG | Existing | Pumps | 158503.63 | 0
CZ14 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ14 | cPVVG | Existing | Humidification | 0 | 0
CZ14 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ14 | cPVVG | Existing | Water Systems | 0 | 783591.35
CZ14 | cPVVG | Existing | Refrigeration | 0 | 0
CZ14 | cPVVG | Existing | Generators | 0 | 0
CZ14 | cPVVG | Existing | Total End Uses | 13516681.92 | 1638680.74
CZ15 | cPVVG | Existing | Heating | 0 | 530793.57
CZ15 | cPVVG | Existing | Cooling | 6153567.98 | 0
CZ15 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ15 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ15 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ15 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ15 | cPVVG | Existing | Fans | 1887867.01 | 0
CZ15 | cPVVG | Existing | Pumps | 167048.56 | 0
CZ15 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ15 | cPVVG | Existing | Humidification | 0 | 0
CZ15 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ15 | cPVVG | Existing | Water Systems | 0 | 695501.76
CZ15 | cPVVG | Existing | Refrigeration | 0 | 0
CZ15 | cPVVG | Existing | Generators | 0 | 0
CZ15 | cPVVG | Existing | Total End Uses | 15034465.07 | 1375633.55
CZ16 | cPVVG | Existing | Heating | 0 | 1606429.18
CZ16 | cPVVG | Existing | Cooling | 3793868.87 | 0
CZ16 | cPVVG | Existing | Interior Lighting | 2929105.9 | 0
CZ16 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ16 | cPVVG | Existing | Interior Equipment | 3896875.61 | 149338.22
CZ16 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ16 | cPVVG | Existing | Fans | 1766485.93 | 0
CZ16 | cPVVG | Existing | Pumps | 144810.54 | 0
CZ16 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ16 | cPVVG | Existing | Humidification | 0 | 0
CZ16 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ16 | cPVVG | Existing | Water Systems | 0 | 924517.83
CZ16 | cPVVG | Existing | Refrigeration | 0 | 0
CZ16 | cPVVG | Existing | Generators | 0 | 0
CZ16 | cPVVG | Existing | Total End Uses | 12531146.86 | 2680285.23
CZ01 | cPVVG | New Construction | Heating | 0 | 1029451.79
CZ01 | cPVVG | New Construction | Cooling | 324617.32 | 0
CZ01 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ01 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ01 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ01 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ01 | cPVVG | New Construction | Fans | 680197.21 | 0
CZ01 | cPVVG | New Construction | Pumps | 77961.2 | 0
CZ01 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ01 | cPVVG | New Construction | Humidification | 0 | 0
CZ01 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ01 | cPVVG | New Construction | Water Systems | 0 | 1022540.32
CZ01 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ01 | cPVVG | New Construction | Generators | 0 | 0
CZ01 | cPVVG | New Construction | Total End Uses | 7120297.08 | 2201330.33
CZ02 | cPVVG | New Construction | Heating | 0 | 1529076.46
CZ02 | cPVVG | New Construction | Cooling | 1644901.23 | 0
CZ02 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ02 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ02 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ02 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ02 | cPVVG | New Construction | Fans | 918097.49 | 0
CZ02 | cPVVG | New Construction | Pumps | 108678.16 | 0
CZ02 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ02 | cPVVG | New Construction | Humidification | 0 | 0
CZ02 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ02 | cPVVG | New Construction | Water Systems | 0 | 939757.26
CZ02 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ02 | cPVVG | New Construction | Generators | 0 | 0
CZ02 | cPVVG | New Construction | Total End Uses | 8709198.22 | 2618171.94
CZ03 | cPVVG | New Construction | Heating | 0 | 1046256.71
CZ03 | cPVVG | New Construction | Cooling | 1164874.96 | 0
CZ03 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ03 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ03 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ03 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ03 | cPVVG | New Construction | Fans | 785067.2 | 0
CZ03 | cPVVG | New Construction | Pumps | 102264.58 | 0
CZ03 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ03 | cPVVG | New Construction | Humidification | 0 | 0
CZ03 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ03 | cPVVG | New Construction | Water Systems | 0 | 936080.29
CZ03 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ03 | cPVVG | New Construction | Generators | 0 | 0
CZ03 | cPVVG | New Construction | Total End Uses | 8089728.08 | 2131675.22
CZ04 | cPVVG | New Construction | Heating | 0 | 983107.4
CZ04 | cPVVG | New Construction | Cooling | 1875279.45 | 0
CZ04 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ04 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ04 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ04 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ04 | cPVVG | New Construction | Fans | 963766.57 | 0
CZ04 | cPVVG | New Construction | Pumps | 115056.57 | 0
CZ04 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ04 | cPVVG | New Construction | Humidification | 0 | 0
CZ04 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ04 | cPVVG | New Construction | Water Systems | 0 | 903918.59
CZ04 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ04 | cPVVG | New Construction | Generators | 0 | 0
CZ04 | cPVVG | New Construction | Total End Uses | 8991623.95 | 2036364.2
CZ05 | cPVVG | New Construction | Heating | 0 | 1080997.67
CZ05 | cPVVG | New Construction | Cooling | 1349885.63 | 0
CZ05 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ05 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ05 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ05 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ05 | cPVVG | New Construction | Fans | 842577.73 | 0
CZ05 | cPVVG | New Construction | Pumps | 98332.8 | 0
CZ05 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ05 | cPVVG | New Construction | Humidification | 0 | 0
CZ05 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ05 | cPVVG | New Construction | Water Systems | 0 | 936183.81
CZ05 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ05 | cPVVG | New Construction | Generators | 0 | 0
CZ05 | cPVVG | New Construction | Total End Uses | 8328317.5 | 2166519.7
CZ06 | cPVVG | New Construction | Heating | 0 | 374243.38
CZ06 | cPVVG | New Construction | Cooling | 2151927.39 | 0
CZ06 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ06 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ06 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ06 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ06 | cPVVG | New Construction | Fans | 923617.11 | 0
CZ06 | cPVVG | New Construction | Pumps | 109979.58 | 0
CZ06 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ06 | cPVVG | New Construction | Humidification | 0 | 0
CZ06 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ06 | cPVVG | New Construction | Water Systems | 0 | 862252.29
CZ06 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ06 | cPVVG | New Construction | Generators | 0 | 0
CZ06 | cPVVG | New Construction | Total End Uses | 9223045.42 | 1385833.88
CZ07 | cPVVG | New Construction | Heating | 0 | 352249.96
CZ07 | cPVVG | New Construction | Cooling | 2342123.8 | 0
CZ07 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ07 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ07 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ07 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ07 | cPVVG | New Construction | Fans | 940749.2 | 0
CZ07 | cPVVG | New Construction | Pumps | 114792.58 | 0
CZ07 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ07 | cPVVG | New Construction | Humidification | 0 | 0
CZ07 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ07 | cPVVG | New Construction | Water Systems | 0 | 851229.58
CZ07 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ07 | cPVVG | New Construction | Generators | 0 | 0
CZ07 | cPVVG | New Construction | Total End Uses | 9435186.93 | 1352817.76
CZ08 | cPVVG | New Construction | Heating | 0 | 518015.37
CZ08 | cPVVG | New Construction | Cooling | 2641299.27 | 0
CZ08 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ08 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ08 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ08 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ08 | cPVVG | New Construction | Fans | 1053236.55 | 0
CZ08 | cPVVG | New Construction | Pumps | 123850.98 | 0
CZ08 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ08 | cPVVG | New Construction | Humidification | 0 | 0
CZ08 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ08 | cPVVG | New Construction | Water Systems | 0 | 850000.61
CZ08 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ08 | cPVVG | New Construction | Generators | 0 | 0
CZ08 | cPVVG | New Construction | Total End Uses | 9855908.15 | 1517354.2
CZ09 | cPVVG | New Construction | Heating | 0 | 489649.95
CZ09 | cPVVG | New Construction | Cooling | 2915588.75 | 0
CZ09 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ09 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ09 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ09 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ09 | cPVVG | New Construction | Fans | 1166462.98 | 0
CZ09 | cPVVG | New Construction | Pumps | 127150.9 | 0
CZ09 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ09 | cPVVG | New Construction | Humidification | 0 | 0
CZ09 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ09 | cPVVG | New Construction | Water Systems | 0 | 838328.99
CZ09 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ09 | cPVVG | New Construction | Generators | 0 | 0
CZ09 | cPVVG | New Construction | Total End Uses | 10246723.97 | 1477317.15
CZ10 | cPVVG | New Construction | Heating | 0 | 847122.28
CZ10 | cPVVG | New Construction | Cooling | 3361606.02 | 0
CZ10 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ10 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ10 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ10 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ10 | cPVVG | New Construction | Fans | 1307107.32 | 0
CZ10 | cPVVG | New Construction | Pumps | 136253.5 | 0
CZ10 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ10 | cPVVG | New Construction | Humidification | 0 | 0
CZ10 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ10 | cPVVG | New Construction | Water Systems | 0 | 831494.21
CZ10 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ10 | cPVVG | New Construction | Generators | 0 | 0
CZ10 | cPVVG | New Construction | Total End Uses | 10842488.19 | 1827954.7
CZ11 | cPVVG | New Construction | Heating | 0 | 773099.77
CZ11 | cPVVG | New Construction | Cooling | 2965167.6 | 0
CZ11 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ11 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ11 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ11 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ11 | cPVVG | New Construction | Fans | 1144983.18 | 0
CZ11 | cPVVG | New Construction | Pumps | 126172.78 | 0
CZ11 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ11 | cPVVG | New Construction | Humidification | 0 | 0
CZ11 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ11 | cPVVG | New Construction | Water Systems | 0 | 849867.49
CZ11 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ11 | cPVVG | New Construction | Generators | 0 | 0
CZ11 | cPVVG | New Construction | Total End Uses | 10273844.91 | 1772305.48
CZ12 | cPVVG | New Construction | Heating | 0 | 803704.83
CZ12 | cPVVG | New Construction | Cooling | 2641419.46 | 0
CZ12 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ12 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ12 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ12 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ12 | cPVVG | New Construction | Fans | 1065201.4 | 0
CZ12 | cPVVG | New Construction | Pumps | 125740.05 | 0
CZ12 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ12 | cPVVG | New Construction | Humidification | 0 | 0
CZ12 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ12 | cPVVG | New Construction | Water Systems | 0 | 873854.35
CZ12 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ12 | cPVVG | New Construction | Generators | 0 | 0
CZ12 | cPVVG | New Construction | Total End Uses | 9869882.26 | 1826897.4
CZ13 | cPVVG | New Construction | Heating | 0 | 646187.03
CZ13 | cPVVG | New Construction | Cooling | 3252370.47 | 0
CZ13 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ13 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ13 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ13 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ13 | cPVVG | New Construction | Fans | 1185812.05 | 0
CZ13 | cPVVG | New Construction | Pumps | 131455.64 | 0
CZ13 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ13 | cPVVG | New Construction | Humidification | 0 | 0
CZ13 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ13 | cPVVG | New Construction | Water Systems | 0 | 825070.88
CZ13 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ13 | cPVVG | New Construction | Generators | 0 | 0
CZ13 | cPVVG | New Construction | Total End Uses | 10607159.5 | 1620596.12
CZ14 | cPVVG | New Construction | Heating | 0 | 529026.59
CZ14 | cPVVG | New Construction | Cooling | 3805842.74 | 0
CZ14 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ14 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ14 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ14 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ14 | cPVVG | New Construction | Fans | 1376475.59 | 0
CZ14 | cPVVG | New Construction | Pumps | 131337.71 | 0
CZ14 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ14 | cPVVG | New Construction | Humidification | 0 | 0
CZ14 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ14 | cPVVG | New Construction | Water Systems | 0 | 783046.43
CZ14 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ14 | cPVVG | New Construction | Generators | 0 | 0
CZ14 | cPVVG | New Construction | Total End Uses | 11351177.38 | 1461411.23
CZ15 | cPVVG | New Construction | Heating | 0 | 441814.58
CZ15 | cPVVG | New Construction | Cooling | 4989187.38 | 0
CZ15 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ15 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ15 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ15 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ15 | cPVVG | New Construction | Fans | 1441291.67 | 0
CZ15 | cPVVG | New Construction | Pumps | 138771.58 | 0
CZ15 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ15 | cPVVG | New Construction | Humidification | 0 | 0
CZ15 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ15 | cPVVG | New Construction | Water Systems | 0 | 694964.45
CZ15 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ15 | cPVVG | New Construction | Generators | 0 | 0
CZ15 | cPVVG | New Construction | Total End Uses | 12606771.97 | 1286117.25
CZ16 | cPVVG | New Construction | Heating | 0 | 1101646.03
CZ16 | cPVVG | New Construction | Cooling | 2998857.23 | 0
CZ16 | cPVVG | New Construction | Interior Lighting | 2140645.73 | 0
CZ16 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ16 | cPVVG | New Construction | Interior Equipment | 3896875.61 | 149338.22
CZ16 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ16 | cPVVG | New Construction | Fans | 1366757.71 | 0
CZ16 | cPVVG | New Construction | Pumps | 119139.22 | 0
CZ16 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ16 | cPVVG | New Construction | Humidification | 0 | 0
CZ16 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ16 | cPVVG | New Construction | Water Systems | 0 | 924152.07
CZ16 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ16 | cPVVG | New Construction | Generators | 0 | 0
CZ16 | cPVVG | New Construction | Total End Uses | 10522275.51 | 2175136.32

## Raw_endusebreakdownannual (hidden)
Vintage | Climate Zone | HVAC System | End Use | Electricity [kBtu] | Natural Gas [kBtu]
Existing | CZ01 | cAVVG | Heating | 0 | 1283456.41
Existing | CZ01 | cAVVG | Cooling | 109234.67 | 0
Existing | CZ01 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ01 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ01 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ01 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ01 | cAVVG | Fans | 714438.74 | 0
Existing | CZ01 | cAVVG | Pumps | 26421.54 | 0
Existing | CZ01 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ01 | cAVVG | Humidification | 0 | 0
Existing | CZ01 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ01 | cAVVG | Water Systems | 0 | 1023276.86
Existing | CZ01 | cAVVG | Refrigeration | 0 | 0
Existing | CZ01 | cAVVG | Generators | 0 | 0
Existing | CZ01 | cAVVG | Total End Uses | 7676076.47 | 2456071.48
Existing | CZ02 | cAVVG | Heating | 0 | 1243119.58
Existing | CZ02 | cAVVG | Cooling | 1060648.51 | 0
Existing | CZ02 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ02 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ02 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ02 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ02 | cAVVG | Fans | 983224.69 | 0
Existing | CZ02 | cAVVG | Pumps | 70602.09 | 0
Existing | CZ02 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ02 | cAVVG | Humidification | 0 | 0
Existing | CZ02 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ02 | cAVVG | Water Systems | 0 | 940106.92
Existing | CZ02 | cAVVG | Refrigeration | 0 | 0
Existing | CZ02 | cAVVG | Generators | 0 | 0
Existing | CZ02 | cAVVG | Total End Uses | 8940456.8 | 2332564.71
Existing | CZ03 | cAVVG | Heating | 0 | 746943.07
Existing | CZ03 | cAVVG | Cooling | 643397.1 | 0
Existing | CZ03 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ03 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ03 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ03 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ03 | cAVVG | Fans | 803318.71 | 0
Existing | CZ03 | cAVVG | Pumps | 58353.8 | 0
Existing | CZ03 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ03 | cAVVG | Humidification | 0 | 0
Existing | CZ03 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ03 | cAVVG | Water Systems | 0 | 936365.53
Existing | CZ03 | cAVVG | Refrigeration | 0 | 0
Existing | CZ03 | cAVVG | Generators | 0 | 0
Existing | CZ03 | cAVVG | Total End Uses | 8331051.13 | 1832646.81
Existing | CZ04 | cAVVG | Heating | 0 | 752498.32
Existing | CZ04 | cAVVG | Cooling | 1243258.69 | 0
Existing | CZ04 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ04 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ04 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ04 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ04 | cAVVG | Fans | 1039791.09 | 0
Existing | CZ04 | cAVVG | Pumps | 77543.17 | 0
Existing | CZ04 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ04 | cAVVG | Humidification | 0 | 0
Existing | CZ04 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ04 | cAVVG | Water Systems | 0 | 904178.1
Existing | CZ04 | cAVVG | Refrigeration | 0 | 0
Existing | CZ04 | cAVVG | Generators | 0 | 0
Existing | CZ04 | cAVVG | Total End Uses | 9186574.47 | 1806014.64
Existing | CZ05 | cAVVG | Heating | 0 | 767357.96
Existing | CZ05 | cAVVG | Cooling | 804641.04 | 0
Existing | CZ05 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ05 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ05 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ05 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ05 | cAVVG | Fans | 877027.03 | 0
Existing | CZ05 | cAVVG | Pumps | 57693.01 | 0
Existing | CZ05 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ05 | cAVVG | Humidification | 0 | 0
Existing | CZ05 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ05 | cAVVG | Water Systems | 0 | 936457.29
Existing | CZ05 | cAVVG | Refrigeration | 0 | 0
Existing | CZ05 | cAVVG | Generators | 0 | 0
Existing | CZ05 | cAVVG | Total End Uses | 8565342.6 | 1853153.46
Existing | CZ06 | cAVVG | Heating | 0 | 229775.68
Existing | CZ06 | cAVVG | Cooling | 1393407.89 | 0
Existing | CZ06 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ06 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ06 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ06 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ06 | cAVVG | Fans | 1034314.48 | 0
Existing | CZ06 | cAVVG | Pumps | 88487.8 | 0
Existing | CZ06 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ06 | cAVVG | Humidification | 0 | 0
Existing | CZ06 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ06 | cAVVG | Water Systems | 0 | 862507.07
Existing | CZ06 | cAVVG | Refrigeration | 0 | 0
Existing | CZ06 | cAVVG | Generators | 0 | 0
Existing | CZ06 | cAVVG | Total End Uses | 9342191.68 | 1241620.96
Existing | CZ07 | cAVVG | Heating | 0 | 259714.13
Existing | CZ07 | cAVVG | Cooling | 1557403.78 | 0
Existing | CZ07 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ07 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ07 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ07 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ07 | cAVVG | Fans | 1093024.29 | 0
Existing | CZ07 | cAVVG | Pumps | 96399.32 | 0
Existing | CZ07 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ07 | cAVVG | Humidification | 0 | 0
Existing | CZ07 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ07 | cAVVG | Water Systems | 0 | 851509.86
Existing | CZ07 | cAVVG | Refrigeration | 0 | 0
Existing | CZ07 | cAVVG | Generators | 0 | 0
Existing | CZ07 | cAVVG | Total End Uses | 9572808.91 | 1260562.21
Existing | CZ08 | cAVVG | Heating | 0 | 379592.55
Existing | CZ08 | cAVVG | Cooling | 1814943.26 | 0
Existing | CZ08 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ08 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ08 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ08 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ08 | cAVVG | Fans | 1200556.62 | 0
Existing | CZ08 | cAVVG | Pumps | 100804.97 | 0
Existing | CZ08 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ08 | cAVVG | Humidification | 0 | 0
Existing | CZ08 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ08 | cAVVG | Water Systems | 0 | 850289.24
Existing | CZ08 | cAVVG | Refrigeration | 0 | 0
Existing | CZ08 | cAVVG | Generators | 0 | 0
Existing | CZ08 | cAVVG | Total End Uses | 9942286.37 | 1379220
Existing | CZ09 | cAVVG | Heating | 0 | 386071.65
Existing | CZ09 | cAVVG | Cooling | 2062703.42 | 0
Existing | CZ09 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ09 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ09 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ09 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ09 | cAVVG | Fans | 1349056.86 | 0
Existing | CZ09 | cAVVG | Pumps | 106943.07 | 0
Existing | CZ09 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ09 | cAVVG | Humidification | 0 | 0
Existing | CZ09 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ09 | cAVVG | Water Systems | 0 | 838524.69
Existing | CZ09 | cAVVG | Refrigeration | 0 | 0
Existing | CZ09 | cAVVG | Generators | 0 | 0
Existing | CZ09 | cAVVG | Total End Uses | 10344684.87 | 1373934.55
Existing | CZ10 | cAVVG | Heating | 0 | 887668.66
Existing | CZ10 | cAVVG | Cooling | 2556095.17 | 0
Existing | CZ10 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ10 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ10 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ10 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ10 | cAVVG | Fans | 1536981.36 | 0
Existing | CZ10 | cAVVG | Pumps | 113541.99 | 0
Existing | CZ10 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ10 | cAVVG | Humidification | 0 | 0
Existing | CZ10 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ10 | cAVVG | Water Systems | 0 | 831741.28
Existing | CZ10 | cAVVG | Refrigeration | 0 | 0
Existing | CZ10 | cAVVG | Generators | 0 | 0
Existing | CZ10 | cAVVG | Total End Uses | 11032600.04 | 1868748.16
Existing | CZ11 | cAVVG | Heating | 0 | 1414029.29
Existing | CZ11 | cAVVG | Cooling | 2419902.45 | 0
Existing | CZ11 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ11 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ11 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ11 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ11 | cAVVG | Fans | 1466930.31 | 0
Existing | CZ11 | cAVVG | Pumps | 91345.02 | 0
Existing | CZ11 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ11 | cAVVG | Humidification | 0 | 0
Existing | CZ11 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ11 | cAVVG | Water Systems | 0 | 850249.71
Existing | CZ11 | cAVVG | Refrigeration | 0 | 0
Existing | CZ11 | cAVVG | Generators | 0 | 0
Existing | CZ11 | cAVVG | Total End Uses | 10804159.29 | 2413617.23
Existing | CZ12 | cAVVG | Heating | 0 | 1254816.83
Existing | CZ12 | cAVVG | Cooling | 2017036.99 | 0
Existing | CZ12 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ12 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ12 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ12 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ12 | cAVVG | Fans | 1310664.44 | 0
Existing | CZ12 | cAVVG | Pumps | 79434.52 | 0
Existing | CZ12 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ12 | cAVVG | Humidification | 0 | 0
Existing | CZ12 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ12 | cAVVG | Water Systems | 0 | 874301.53
Existing | CZ12 | cAVVG | Refrigeration | 0 | 0
Existing | CZ12 | cAVVG | Generators | 0 | 0
Existing | CZ12 | cAVVG | Total End Uses | 10233117.47 | 2278456.57
Existing | CZ13 | cAVVG | Heating | 0 | 1114072.66
Existing | CZ13 | cAVVG | Cooling | 2658162.29 | 0
Existing | CZ13 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ13 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ13 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ13 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ13 | cAVVG | Fans | 1523985.59 | 0
Existing | CZ13 | cAVVG | Pumps | 88795.24 | 0
Existing | CZ13 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ13 | cAVVG | Humidification | 0 | 0
Existing | CZ13 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ13 | cAVVG | Water Systems | 0 | 825525.52
Existing | CZ13 | cAVVG | Refrigeration | 0 | 0
Existing | CZ13 | cAVVG | Generators | 0 | 0
Existing | CZ13 | cAVVG | Total End Uses | 11096924.64 | 2088936.39
Existing | CZ14 | cAVVG | Heating | 0 | 835511.87
Existing | CZ14 | cAVVG | Cooling | 3294721.95 | 0
Existing | CZ14 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ14 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ14 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ14 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ14 | cAVVG | Fans | 1814180.78 | 0
Existing | CZ14 | cAVVG | Pumps | 118942.12 | 0
Existing | CZ14 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ14 | cAVVG | Humidification | 0 | 0
Existing | CZ14 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ14 | cAVVG | Water Systems | 0 | 783531.76
Existing | CZ14 | cAVVG | Refrigeration | 0 | 0
Existing | CZ14 | cAVVG | Generators | 0 | 0
Existing | CZ14 | cAVVG | Total End Uses | 12053826.37 | 1768381.85
Existing | CZ15 | cAVVG | Heating | 0 | 772396.65
Existing | CZ15 | cAVVG | Cooling | 4560334.77 | 0
Existing | CZ15 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ15 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ15 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ15 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ15 | cAVVG | Fans | 1934866.78 | 0
Existing | CZ15 | cAVVG | Pumps | 108371.54 | 0
Existing | CZ15 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ15 | cAVVG | Humidification | 0 | 0
Existing | CZ15 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ15 | cAVVG | Water Systems | 0 | 695440.21
Existing | CZ15 | cAVVG | Refrigeration | 0 | 0
Existing | CZ15 | cAVVG | Generators | 0 | 0
Existing | CZ15 | cAVVG | Total End Uses | 13429554.61 | 1617175.07
Existing | CZ16 | cAVVG | Heating | 0 | 1769322.13
Existing | CZ16 | cAVVG | Cooling | 2239778.01 | 0
Existing | CZ16 | cAVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ16 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ16 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ16 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ16 | cAVVG | Fans | 1753556.96 | 0
Existing | CZ16 | cAVVG | Pumps | 92933.59 | 0
Existing | CZ16 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ16 | cAVVG | Humidification | 0 | 0
Existing | CZ16 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ16 | cAVVG | Water Systems | 0 | 924600.78
Existing | CZ16 | cAVVG | Refrigeration | 0 | 0
Existing | CZ16 | cAVVG | Generators | 0 | 0
Existing | CZ16 | cAVVG | Total End Uses | 10912250.08 | 2843261.13
New Construction | CZ01 | cAVVG | Heating | 0 | 1167557.94
New Construction | CZ01 | cAVVG | Cooling | 84246.18 | 0
New Construction | CZ01 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ01 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ01 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ01 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ01 | cAVVG | Fans | 648586.63 | 0
New Construction | CZ01 | cAVVG | Pumps | 21876.96 | 0
New Construction | CZ01 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ01 | cAVVG | Humidification | 0 | 0
New Construction | CZ01 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ01 | cAVVG | Water Systems | 0 | 1022649.72
New Construction | CZ01 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ01 | cAVVG | Generators | 0 | 0
New Construction | CZ01 | cAVVG | Total End Uses | 6792231.13 | 2339545.88
New Construction | CZ02 | cAVVG | Heating | 0 | 1711393.06
New Construction | CZ02 | cAVVG | Cooling | 936379.73 | 0
New Construction | CZ02 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ02 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ02 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ02 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ02 | cAVVG | Fans | 839878.59 | 0
New Construction | CZ02 | cAVVG | Pumps | 61769.83 | 0
New Construction | CZ02 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ02 | cAVVG | Humidification | 0 | 0
New Construction | CZ02 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ02 | cAVVG | Water Systems | 0 | 939699.73
New Construction | CZ02 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ02 | cAVVG | Generators | 0 | 0
New Construction | CZ02 | cAVVG | Total End Uses | 7875549.5 | 2800431.01
New Construction | CZ03 | cAVVG | Heating | 0 | 1167421.89
New Construction | CZ03 | cAVVG | Cooling | 554729.69 | 0
New Construction | CZ03 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ03 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ03 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ03 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ03 | cAVVG | Fans | 678018.66 | 0
New Construction | CZ03 | cAVVG | Pumps | 51090.87 | 0
New Construction | CZ03 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ03 | cAVVG | Humidification | 0 | 0
New Construction | CZ03 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ03 | cAVVG | Water Systems | 0 | 936099.07
New Construction | CZ03 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ03 | cAVVG | Generators | 0 | 0
New Construction | CZ03 | cAVVG | Total End Uses | 7321360.57 | 2252859.18
New Construction | CZ04 | cAVVG | Heating | 0 | 1112419.74
New Construction | CZ04 | cAVVG | Cooling | 1107503.5 | 0
New Construction | CZ04 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ04 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ04 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ04 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ04 | cAVVG | Fans | 878393.41 | 0
New Construction | CZ04 | cAVVG | Pumps | 69545.22 | 0
New Construction | CZ04 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ04 | cAVVG | Humidification | 0 | 0
New Construction | CZ04 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ04 | cAVVG | Water Systems | 0 | 903936.35
New Construction | CZ04 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ04 | cAVVG | Generators | 0 | 0
New Construction | CZ04 | cAVVG | Total End Uses | 8092963.48 | 2165694.31
New Construction | CZ05 | cAVVG | Heating | 0 | 1199174.21
New Construction | CZ05 | cAVVG | Cooling | 692573.47 | 0
New Construction | CZ05 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ05 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ05 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ05 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ05 | cAVVG | Fans | 741930.98 | 0
New Construction | CZ05 | cAVVG | Pumps | 50036.23 | 0
New Construction | CZ05 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ05 | cAVVG | Humidification | 0 | 0
New Construction | CZ05 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ05 | cAVVG | Water Systems | 0 | 936183.48
New Construction | CZ05 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ05 | cAVVG | Generators | 0 | 0
New Construction | CZ05 | cAVVG | Total End Uses | 7522062.03 | 2284695.92
New Construction | CZ06 | cAVVG | Heating | 0 | 427343.85
New Construction | CZ06 | cAVVG | Cooling | 1199245.56 | 0
New Construction | CZ06 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ06 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ06 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ06 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ06 | cAVVG | Fans | 850929.81 | 0
New Construction | CZ06 | cAVVG | Pumps | 78493.06 | 0
New Construction | CZ06 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ06 | cAVVG | Humidification | 0 | 0
New Construction | CZ06 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ06 | cAVVG | Water Systems | 0 | 862327.43
New Construction | CZ06 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ06 | cAVVG | Generators | 0 | 0
New Construction | CZ06 | cAVVG | Total End Uses | 8166189.78 | 1439009.5
New Construction | CZ07 | cAVVG | Heating | 0 | 434652.46
New Construction | CZ07 | cAVVG | Cooling | 1347234.15 | 0
New Construction | CZ07 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ07 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ07 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ07 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ07 | cAVVG | Fans | 910947.99 | 0
New Construction | CZ07 | cAVVG | Pumps | 85211.93 | 0
New Construction | CZ07 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ07 | cAVVG | Humidification | 0 | 0
New Construction | CZ07 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ07 | cAVVG | Water Systems | 0 | 851272.2
New Construction | CZ07 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ07 | cAVVG | Generators | 0 | 0
New Construction | CZ07 | cAVVG | Total End Uses | 8380915.42 | 1435262.88
New Construction | CZ08 | cAVVG | Heating | 0 | 614198.81
New Construction | CZ08 | cAVVG | Cooling | 1609380.49 | 0
New Construction | CZ08 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ08 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ08 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ08 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ08 | cAVVG | Fans | 1005112.8 | 0
New Construction | CZ08 | cAVVG | Pumps | 91178.49 | 0
New Construction | CZ08 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ08 | cAVVG | Humidification | 0 | 0
New Construction | CZ08 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ08 | cAVVG | Water Systems | 0 | 850163.47
New Construction | CZ08 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ08 | cAVVG | Generators | 0 | 0
New Construction | CZ08 | cAVVG | Total End Uses | 8743193.13 | 1613700.5
New Construction | CZ09 | cAVVG | Heating | 0 | 594412.66
New Construction | CZ09 | cAVVG | Cooling | 1836769.29 | 0
New Construction | CZ09 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ09 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ09 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ09 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ09 | cAVVG | Fans | 1125640.01 | 0
New Construction | CZ09 | cAVVG | Pumps | 97376.47 | 0
New Construction | CZ09 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ09 | cAVVG | Humidification | 0 | 0
New Construction | CZ09 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ09 | cAVVG | Water Systems | 0 | 838381.99
New Construction | CZ09 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ09 | cAVVG | Generators | 0 | 0
New Construction | CZ09 | cAVVG | Total End Uses | 9097307.12 | 1582132.87
New Construction | CZ10 | cAVVG | Heating | 0 | 1044865.02
New Construction | CZ10 | cAVVG | Cooling | 2238029.1 | 0
New Construction | CZ10 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ10 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ10 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ10 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ10 | cAVVG | Fans | 1280115.76 | 0
New Construction | CZ10 | cAVVG | Pumps | 94284.66 | 0
New Construction | CZ10 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ10 | cAVVG | Humidification | 0 | 0
New Construction | CZ10 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ10 | cAVVG | Water Systems | 0 | 831616.75
New Construction | CZ10 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ10 | cAVVG | Generators | 0 | 0
New Construction | CZ10 | cAVVG | Total End Uses | 9649950.86 | 2025819.98
New Construction | CZ11 | cAVVG | Heating | 0 | 863928.79
New Construction | CZ11 | cAVVG | Cooling | 1896292.24 | 0
New Construction | CZ11 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ11 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ11 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ11 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ11 | cAVVG | Fans | 1079778.05 | 0
New Construction | CZ11 | cAVVG | Pumps | 66266.23 | 0
New Construction | CZ11 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ11 | cAVVG | Humidification | 0 | 0
New Construction | CZ11 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ11 | cAVVG | Water Systems | 0 | 849787.2
New Construction | CZ11 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ11 | cAVVG | Generators | 0 | 0
New Construction | CZ11 | cAVVG | Total End Uses | 9079857.87 | 1863054.21
New Construction | CZ12 | cAVVG | Heating | 0 | 899332.38
New Construction | CZ12 | cAVVG | Cooling | 1618779.5 | 0
New Construction | CZ12 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ12 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ12 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ12 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ12 | cAVVG | Fans | 1005185.56 | 0
New Construction | CZ12 | cAVVG | Pumps | 65894.68 | 0
New Construction | CZ12 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ12 | cAVVG | Humidification | 0 | 0
New Construction | CZ12 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ12 | cAVVG | Water Systems | 0 | 873843.14
New Construction | CZ12 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ12 | cAVVG | Generators | 0 | 0
New Construction | CZ12 | cAVVG | Total End Uses | 8727381.08 | 1922513.74
New Construction | CZ13 | cAVVG | Heating | 0 | 727417.34
New Construction | CZ13 | cAVVG | Cooling | 2105888.68 | 0
New Construction | CZ13 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ13 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ13 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ13 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ13 | cAVVG | Fans | 1137024.5 | 0
New Construction | CZ13 | cAVVG | Pumps | 73277.1 | 0
New Construction | CZ13 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ13 | cAVVG | Humidification | 0 | 0
New Construction | CZ13 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ13 | cAVVG | Water Systems | 0 | 825052.05
New Construction | CZ13 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ13 | cAVVG | Generators | 0 | 0
New Construction | CZ13 | cAVVG | Total End Uses | 9353711.63 | 1701807.61
New Construction | CZ14 | cAVVG | Heating | 0 | 595366.2
New Construction | CZ14 | cAVVG | Cooling | 2650272.25 | 0
New Construction | CZ14 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ14 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ14 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ14 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ14 | cAVVG | Fans | 1342648.66 | 0
New Construction | CZ14 | cAVVG | Pumps | 97188.77 | 0
New Construction | CZ14 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ14 | cAVVG | Humidification | 0 | 0
New Construction | CZ14 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ14 | cAVVG | Water Systems | 0 | 783114.95
New Construction | CZ14 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ14 | cAVVG | Generators | 0 | 0
New Construction | CZ14 | cAVVG | Total End Uses | 10127631.04 | 1527819.37
New Construction | CZ15 | cAVVG | Heating | 0 | 540360.22
New Construction | CZ15 | cAVVG | Cooling | 3716297.99 | 0
New Construction | CZ15 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ15 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ15 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ15 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ15 | cAVVG | Fans | 1397623.98 | 0
New Construction | CZ15 | cAVVG | Pumps | 89696.71 | 0
New Construction | CZ15 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ15 | cAVVG | Humidification | 0 | 0
New Construction | CZ15 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ15 | cAVVG | Water Systems | 0 | 695010.95
New Construction | CZ15 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ15 | cAVVG | Generators | 0 | 0
New Construction | CZ15 | cAVVG | Total End Uses | 11241140.02 | 1384709.39
New Construction | CZ16 | cAVVG | Heating | 0 | 1238199.41
New Construction | CZ16 | cAVVG | Cooling | 1765664.47 | 0
New Construction | CZ16 | cAVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ16 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ16 | cAVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ16 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ16 | cAVVG | Fans | 1294970.02 | 0
New Construction | CZ16 | cAVVG | Pumps | 72816.37 | 0
New Construction | CZ16 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ16 | cAVVG | Humidification | 0 | 0
New Construction | CZ16 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ16 | cAVVG | Water Systems | 0 | 924072.26
New Construction | CZ16 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ16 | cAVVG | Generators | 0 | 0
New Construction | CZ16 | cAVVG | Total End Uses | 9170972.21 | 2311609.89
Existing | CZ01 | cDXGF | Heating | 0 | 1079447.09
Existing | CZ01 | cDXGF | Cooling | 423966.39 | 0
Existing | CZ01 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ01 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ01 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXGF | Fans | 1284784.08 | 0
Existing | CZ01 | cDXGF | Pumps | 92693.19 | 0
Existing | CZ01 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ01 | cDXGF | Humidification | 0 | 0
Existing | CZ01 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ01 | cDXGF | Water Systems | 0 | 1023249.29
Existing | CZ01 | cDXGF | Refrigeration | 0 | 0
Existing | CZ01 | cDXGF | Generators | 0 | 0
Existing | CZ01 | cDXGF | Total End Uses | 8627425.17 | 2252034.6
Existing | CZ02 | cDXGF | Heating | 0 | 1044488.81
Existing | CZ02 | cDXGF | Cooling | 1946908.39 | 0
Existing | CZ02 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ02 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ02 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXGF | Fans | 1595833.35 | 0
Existing | CZ02 | cDXGF | Pumps | 127087.26 | 0
Existing | CZ02 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ02 | cDXGF | Humidification | 0 | 0
Existing | CZ02 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ02 | cDXGF | Water Systems | 0 | 940039.9
Existing | CZ02 | cDXGF | Refrigeration | 0 | 0
Existing | CZ02 | cDXGF | Generators | 0 | 0
Existing | CZ02 | cDXGF | Total End Uses | 10495810.51 | 2133866.92
Existing | CZ03 | cDXGF | Heating | 0 | 627951.87
Existing | CZ03 | cDXGF | Cooling | 1358307.23 | 0
Existing | CZ03 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ03 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ03 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXGF | Fans | 1434648.51 | 0
Existing | CZ03 | cDXGF | Pumps | 117482.31 | 0
Existing | CZ03 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ03 | cDXGF | Humidification | 0 | 0
Existing | CZ03 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ03 | cDXGF | Water Systems | 0 | 936333.77
Existing | CZ03 | cDXGF | Refrigeration | 0 | 0
Existing | CZ03 | cDXGF | Generators | 0 | 0
Existing | CZ03 | cDXGF | Total End Uses | 9736419.56 | 1713623.86
Existing | CZ04 | cDXGF | Heating | 0 | 621592.13
Existing | CZ04 | cDXGF | Cooling | 2160153.51 | 0
Existing | CZ04 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ04 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ04 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXGF | Fans | 1644093.47 | 0
Existing | CZ04 | cDXGF | Pumps | 129672.55 | 0
Existing | CZ04 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ04 | cDXGF | Humidification | 0 | 0
Existing | CZ04 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ04 | cDXGF | Water Systems | 0 | 904243.4
Existing | CZ04 | cDXGF | Refrigeration | 0 | 0
Existing | CZ04 | cDXGF | Generators | 0 | 0
Existing | CZ04 | cDXGF | Total End Uses | 10759901.04 | 1675173.74
Existing | CZ05 | cDXGF | Heating | 0 | 651242.61
Existing | CZ05 | cDXGF | Cooling | 1589603.62 | 0
Existing | CZ05 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ05 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ05 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXGF | Fans | 1496824.62 | 0
Existing | CZ05 | cDXGF | Pumps | 113346.36 | 0
Existing | CZ05 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ05 | cDXGF | Humidification | 0 | 0
Existing | CZ05 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ05 | cDXGF | Water Systems | 0 | 936441.5
Existing | CZ05 | cDXGF | Refrigeration | 0 | 0
Existing | CZ05 | cDXGF | Generators | 0 | 0
Existing | CZ05 | cDXGF | Total End Uses | 10025756.11 | 1737022.33
Existing | CZ06 | cDXGF | Heating | 0 | 189167.42
Existing | CZ06 | cDXGF | Cooling | 2531461.26 | 0
Existing | CZ06 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ06 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ06 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXGF | Fans | 1584966.95 | 0
Existing | CZ06 | cDXGF | Pumps | 123729.62 | 0
Existing | CZ06 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ06 | cDXGF | Humidification | 0 | 0
Existing | CZ06 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ06 | cDXGF | Water Systems | 0 | 862427.62
Existing | CZ06 | cDXGF | Refrigeration | 0 | 0
Existing | CZ06 | cDXGF | Generators | 0 | 0
Existing | CZ06 | cDXGF | Total End Uses | 11066139.35 | 1200933.25
Existing | CZ07 | cDXGF | Heating | 0 | 201645.36
Existing | CZ07 | cDXGF | Cooling | 2775137.07 | 0
Existing | CZ07 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ07 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ07 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXGF | Fans | 1608371.21 | 0
Existing | CZ07 | cDXGF | Pumps | 130067.04 | 0
Existing | CZ07 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ07 | cDXGF | Humidification | 0 | 0
Existing | CZ07 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ07 | cDXGF | Water Systems | 0 | 851480.84
Existing | CZ07 | cDXGF | Refrigeration | 0 | 0
Existing | CZ07 | cDXGF | Generators | 0 | 0
Existing | CZ07 | cDXGF | Total End Uses | 11339556.84 | 1202464.42
Existing | CZ08 | cDXGF | Heating | 0 | 312413.84
Existing | CZ08 | cDXGF | Cooling | 3063180.58 | 0
Existing | CZ08 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ08 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ08 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXGF | Fans | 1740360.82 | 0
Existing | CZ08 | cDXGF | Pumps | 137628.87 | 0
Existing | CZ08 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ08 | cDXGF | Humidification | 0 | 0
Existing | CZ08 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ08 | cDXGF | Water Systems | 0 | 850299.54
Existing | CZ08 | cDXGF | Refrigeration | 0 | 0
Existing | CZ08 | cDXGF | Generators | 0 | 0
Existing | CZ08 | cDXGF | Total End Uses | 11767151.79 | 1312051.6
Existing | CZ09 | cDXGF | Heating | 0 | 313856.5
Existing | CZ09 | cDXGF | Cooling | 3367312.68 | 0
Existing | CZ09 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ09 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ09 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXGF | Fans | 1875048.72 | 0
Existing | CZ09 | cDXGF | Pumps | 140342.34 | 0
Existing | CZ09 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ09 | cDXGF | Humidification | 0 | 0
Existing | CZ09 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ09 | cDXGF | Water Systems | 0 | 838496.62
Existing | CZ09 | cDXGF | Refrigeration | 0 | 0
Existing | CZ09 | cDXGF | Generators | 0 | 0
Existing | CZ09 | cDXGF | Total End Uses | 12208685.26 | 1301691.34
Existing | CZ10 | cDXGF | Heating | 0 | 703648.3
Existing | CZ10 | cDXGF | Cooling | 3901864.95 | 0
Existing | CZ10 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ10 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ10 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXGF | Fans | 2070710.27 | 0
Existing | CZ10 | cDXGF | Pumps | 153506.59 | 0
Existing | CZ10 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ10 | cDXGF | Humidification | 0 | 0
Existing | CZ10 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ10 | cDXGF | Water Systems | 0 | 831690.28
Existing | CZ10 | cDXGF | Refrigeration | 0 | 0
Existing | CZ10 | cDXGF | Generators | 0 | 0
Existing | CZ10 | cDXGF | Total End Uses | 12952063.32 | 1684676.8
Existing | CZ11 | cDXGF | Heating | 0 | 1131728.46
Existing | CZ11 | cDXGF | Cooling | 3773572 | 0
Existing | CZ11 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ11 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ11 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXGF | Fans | 2005491.96 | 0
Existing | CZ11 | cDXGF | Pumps | 152993.61 | 0
Existing | CZ11 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ11 | cDXGF | Humidification | 0 | 0
Existing | CZ11 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ11 | cDXGF | Water Systems | 0 | 850254.64
Existing | CZ11 | cDXGF | Refrigeration | 0 | 0
Existing | CZ11 | cDXGF | Generators | 0 | 0
Existing | CZ11 | cDXGF | Total End Uses | 12758039.08 | 2131321.32
Existing | CZ12 | cDXGF | Heating | 0 | 1032911.91
Existing | CZ12 | cDXGF | Cooling | 3310307.89 | 0
Existing | CZ12 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ12 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ12 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXGF | Fans | 1853026.25 | 0
Existing | CZ12 | cDXGF | Pumps | 149687.21 | 0
Existing | CZ12 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ12 | cDXGF | Humidification | 0 | 0
Existing | CZ12 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ12 | cDXGF | Water Systems | 0 | 874264.16
Existing | CZ12 | cDXGF | Refrigeration | 0 | 0
Existing | CZ12 | cDXGF | Generators | 0 | 0
Existing | CZ12 | cDXGF | Total End Uses | 12139002.87 | 2056514.28
Existing | CZ13 | cDXGF | Heating | 0 | 866974.33
Existing | CZ13 | cDXGF | Cooling | 4113657.88 | 0
Existing | CZ13 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ13 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ13 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXGF | Fans | 2023137.68 | 0
Existing | CZ13 | cDXGF | Pumps | 157872.01 | 0
Existing | CZ13 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ13 | cDXGF | Humidification | 0 | 0
Existing | CZ13 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ13 | cDXGF | Water Systems | 0 | 825510.79
Existing | CZ13 | cDXGF | Refrigeration | 0 | 0
Existing | CZ13 | cDXGF | Generators | 0 | 0
Existing | CZ13 | cDXGF | Total End Uses | 13120649.09 | 1841823.34
Existing | CZ14 | cDXGF | Heating | 0 | 658763.41
Existing | CZ14 | cDXGF | Cooling | 4786720.46 | 0
Existing | CZ14 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ14 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ14 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXGF | Fans | 2281483.6 | 0
Existing | CZ14 | cDXGF | Pumps | 158590.07 | 0
Existing | CZ14 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ14 | cDXGF | Humidification | 0 | 0
Existing | CZ14 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ14 | cDXGF | Water Systems | 0 | 783619.34
Existing | CZ14 | cDXGF | Refrigeration | 0 | 0
Existing | CZ14 | cDXGF | Generators | 0 | 0
Existing | CZ14 | cDXGF | Total End Uses | 14052775.65 | 1591720.96
Existing | CZ15 | cDXGF | Heating | 0 | 515012.8
Existing | CZ15 | cDXGF | Cooling | 6213004.2 | 0
Existing | CZ15 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ15 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ15 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXGF | Fans | 2319042.22 | 0
Existing | CZ15 | cDXGF | Pumps | 167061.45 | 0
Existing | CZ15 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ15 | cDXGF | Humidification | 0 | 0
Existing | CZ15 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ15 | cDXGF | Water Systems | 0 | 695431.3
Existing | CZ15 | cDXGF | Refrigeration | 0 | 0
Existing | CZ15 | cDXGF | Generators | 0 | 0
Existing | CZ15 | cDXGF | Total End Uses | 15525089.38 | 1359782.32
Existing | CZ16 | cDXGF | Heating | 0 | 1480022.65
Existing | CZ16 | cDXGF | Cooling | 3827252.84 | 0
Existing | CZ16 | cDXGF | Interior Lighting | 2929105.9 | 0
Existing | CZ16 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ16 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXGF | Fans | 2304717.63 | 0
Existing | CZ16 | cDXGF | Pumps | 144851.21 | 0
Existing | CZ16 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ16 | cDXGF | Humidification | 0 | 0
Existing | CZ16 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ16 | cDXGF | Water Systems | 0 | 924506.07
Existing | CZ16 | cDXGF | Refrigeration | 0 | 0
Existing | CZ16 | cDXGF | Generators | 0 | 0
Existing | CZ16 | cDXGF | Total End Uses | 13102803.19 | 2553866.94
New Construction | CZ01 | cDXGF | Heating | 0 | 920533.57
New Construction | CZ01 | cDXGF | Cooling | 323513.02 | 0
New Construction | CZ01 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ01 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ01 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXGF | Fans | 1093962.08 | 0
New Construction | CZ01 | cDXGF | Pumps | 78209.23 | 0
New Construction | CZ01 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXGF | Humidification | 0 | 0
New Construction | CZ01 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXGF | Water Systems | 0 | 1022659.91
New Construction | CZ01 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ01 | cDXGF | Generators | 0 | 0
New Construction | CZ01 | cDXGF | Total End Uses | 7533205.67 | 2092531.7
New Construction | CZ02 | cDXGF | Heating | 0 | 1393668.95
New Construction | CZ02 | cDXGF | Cooling | 1658392.47 | 0
New Construction | CZ02 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ02 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ02 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXGF | Fans | 1408925.06 | 0
New Construction | CZ02 | cDXGF | Pumps | 108884.24 | 0
New Construction | CZ02 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXGF | Humidification | 0 | 0
New Construction | CZ02 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXGF | Water Systems | 0 | 939797.08
New Construction | CZ02 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ02 | cDXGF | Generators | 0 | 0
New Construction | CZ02 | cDXGF | Total End Uses | 9213723.12 | 2482804.24
New Construction | CZ03 | cDXGF | Heating | 0 | 949544.3
New Construction | CZ03 | cDXGF | Cooling | 1163282.93 | 0
New Construction | CZ03 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ03 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ03 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXGF | Fans | 1265814.83 | 0
New Construction | CZ03 | cDXGF | Pumps | 102426.78 | 0
New Construction | CZ03 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXGF | Humidification | 0 | 0
New Construction | CZ03 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXGF | Water Systems | 0 | 936097.86
New Construction | CZ03 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ03 | cDXGF | Generators | 0 | 0
New Construction | CZ03 | cDXGF | Total End Uses | 8569045.88 | 2034980.38
New Construction | CZ04 | cDXGF | Heating | 0 | 893987.99
New Construction | CZ04 | cDXGF | Cooling | 1889756.56 | 0
New Construction | CZ04 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ04 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ04 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXGF | Fans | 1450357.98 | 0
New Construction | CZ04 | cDXGF | Pumps | 115254.24 | 0
New Construction | CZ04 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXGF | Humidification | 0 | 0
New Construction | CZ04 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXGF | Water Systems | 0 | 903968.14
New Construction | CZ04 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ04 | cDXGF | Generators | 0 | 0
New Construction | CZ04 | cDXGF | Total End Uses | 9492890.14 | 1947294.34
New Construction | CZ05 | cDXGF | Heating | 0 | 987725.22
New Construction | CZ05 | cDXGF | Cooling | 1353735.84 | 0
New Construction | CZ05 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ05 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ05 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXGF | Fans | 1309681.03 | 0
New Construction | CZ05 | cDXGF | Pumps | 98506 | 0
New Construction | CZ05 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXGF | Humidification | 0 | 0
New Construction | CZ05 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXGF | Water Systems | 0 | 936135.01
New Construction | CZ05 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ05 | cDXGF | Generators | 0 | 0
New Construction | CZ05 | cDXGF | Total End Uses | 8799444.22 | 2073198.45
New Construction | CZ06 | cDXGF | Heating | 0 | 342849.61
New Construction | CZ06 | cDXGF | Cooling | 2153484.35 | 0
New Construction | CZ06 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ06 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ06 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXGF | Fans | 1380060.9 | 0
New Construction | CZ06 | cDXGF | Pumps | 110057.59 | 0
New Construction | CZ06 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXGF | Humidification | 0 | 0
New Construction | CZ06 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXGF | Water Systems | 0 | 862279.13
New Construction | CZ06 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ06 | cDXGF | Generators | 0 | 0
New Construction | CZ06 | cDXGF | Total End Uses | 9681124.18 | 1354466.96
New Construction | CZ07 | cDXGF | Heating | 0 | 324838.63
New Construction | CZ07 | cDXGF | Cooling | 2357386.21 | 0
New Construction | CZ07 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ07 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ07 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXGF | Fans | 1383700.93 | 0
New Construction | CZ07 | cDXGF | Pumps | 114783 | 0
New Construction | CZ07 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXGF | Humidification | 0 | 0
New Construction | CZ07 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXGF | Water Systems | 0 | 851242.24
New Construction | CZ07 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ07 | cDXGF | Generators | 0 | 0
New Construction | CZ07 | cDXGF | Total End Uses | 9893391.49 | 1325419.09
New Construction | CZ08 | cDXGF | Heating | 0 | 478454.9
New Construction | CZ08 | cDXGF | Cooling | 2661434.88 | 0
New Construction | CZ08 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ08 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ08 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXGF | Fans | 1521088.55 | 0
New Construction | CZ08 | cDXGF | Pumps | 124007.25 | 0
New Construction | CZ08 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXGF | Humidification | 0 | 0
New Construction | CZ08 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXGF | Water Systems | 0 | 850080.36
New Construction | CZ08 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ08 | cDXGF | Generators | 0 | 0
New Construction | CZ08 | cDXGF | Total End Uses | 10344052.03 | 1477873.48
New Construction | CZ09 | cDXGF | Heating | 0 | 454511.12
New Construction | CZ09 | cDXGF | Cooling | 2940857.59 | 0
New Construction | CZ09 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ09 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ09 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXGF | Fans | 1645314.52 | 0
New Construction | CZ09 | cDXGF | Pumps | 127183.98 | 0
New Construction | CZ09 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXGF | Humidification | 0 | 0
New Construction | CZ09 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXGF | Water Systems | 0 | 838269.68
New Construction | CZ09 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ09 | cDXGF | Generators | 0 | 0
New Construction | CZ09 | cDXGF | Total End Uses | 10750877.44 | 1442119.02
New Construction | CZ10 | cDXGF | Heating | 0 | 782089.91
New Construction | CZ10 | cDXGF | Cooling | 3399557.77 | 0
New Construction | CZ10 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ10 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ10 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXGF | Fans | 1793298.46 | 0
New Construction | CZ10 | cDXGF | Pumps | 136437.98 | 0
New Construction | CZ10 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXGF | Humidification | 0 | 0
New Construction | CZ10 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXGF | Water Systems | 0 | 831514.56
New Construction | CZ10 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ10 | cDXGF | Generators | 0 | 0
New Construction | CZ10 | cDXGF | Total End Uses | 11366815.56 | 1762942.69
New Construction | CZ11 | cDXGF | Heating | 0 | 698418.27
New Construction | CZ11 | cDXGF | Cooling | 2990443.98 | 0
New Construction | CZ11 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ11 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ11 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXGF | Fans | 1526308.09 | 0
New Construction | CZ11 | cDXGF | Pumps | 126054.81 | 0
New Construction | CZ11 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXGF | Humidification | 0 | 0
New Construction | CZ11 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXGF | Water Systems | 0 | 849790.72
New Construction | CZ11 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ11 | cDXGF | Generators | 0 | 0
New Construction | CZ11 | cDXGF | Total End Uses | 10680328.23 | 1697547.22
New Construction | CZ12 | cDXGF | Heating | 0 | 728908.11
New Construction | CZ12 | cDXGF | Cooling | 2665120.37 | 0
New Construction | CZ12 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ12 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ12 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXGF | Fans | 1455828.92 | 0
New Construction | CZ12 | cDXGF | Pumps | 125808.81 | 0
New Construction | CZ12 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXGF | Humidification | 0 | 0
New Construction | CZ12 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXGF | Water Systems | 0 | 873872.51
New Construction | CZ12 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ12 | cDXGF | Generators | 0 | 0
New Construction | CZ12 | cDXGF | Total End Uses | 10284279.45 | 1752118.83
New Construction | CZ13 | cDXGF | Heating | 0 | 587068.88
New Construction | CZ13 | cDXGF | Cooling | 3281751.07 | 0
New Construction | CZ13 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ13 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ13 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXGF | Fans | 1566082.53 | 0
New Construction | CZ13 | cDXGF | Pumps | 131576.34 | 0
New Construction | CZ13 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXGF | Humidification | 0 | 0
New Construction | CZ13 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXGF | Water Systems | 0 | 824940.38
New Construction | CZ13 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ13 | cDXGF | Generators | 0 | 0
New Construction | CZ13 | cDXGF | Total End Uses | 11016931.28 | 1561347.48
New Construction | CZ14 | cDXGF | Heating | 0 | 488215.44
New Construction | CZ14 | cDXGF | Cooling | 3843011.91 | 0
New Construction | CZ14 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ14 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ14 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXGF | Fans | 1759101.26 | 0
New Construction | CZ14 | cDXGF | Pumps | 131236.37 | 0
New Construction | CZ14 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXGF | Humidification | 0 | 0
New Construction | CZ14 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXGF | Water Systems | 0 | 782970.9
New Construction | CZ14 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ14 | cDXGF | Generators | 0 | 0
New Construction | CZ14 | cDXGF | Total End Uses | 11770870.88 | 1420524.56
New Construction | CZ15 | cDXGF | Heating | 0 | 427454.66
New Construction | CZ15 | cDXGF | Cooling | 5035860.57 | 0
New Construction | CZ15 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ15 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ15 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXGF | Fans | 1773675 | 0
New Construction | CZ15 | cDXGF | Pumps | 138842.85 | 0
New Construction | CZ15 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXGF | Humidification | 0 | 0
New Construction | CZ15 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXGF | Water Systems | 0 | 694876.5
New Construction | CZ15 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ15 | cDXGF | Generators | 0 | 0
New Construction | CZ15 | cDXGF | Total End Uses | 12985899.77 | 1271669.38
New Construction | CZ16 | cDXGF | Heating | 0 | 989578.64
New Construction | CZ16 | cDXGF | Cooling | 3027601.13 | 0
New Construction | CZ16 | cDXGF | Interior Lighting | 2140645.73 | 0
New Construction | CZ16 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXGF | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ16 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXGF | Fans | 1792939.12 | 0
New Construction | CZ16 | cDXGF | Pumps | 119164.62 | 0
New Construction | CZ16 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXGF | Humidification | 0 | 0
New Construction | CZ16 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXGF | Water Systems | 0 | 924193.07
New Construction | CZ16 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ16 | cDXGF | Generators | 0 | 0
New Construction | CZ16 | cDXGF | Total End Uses | 10977226.21 | 2063109.93
Existing | CZ01 | cDXHP | Heating | 36180.57 | 935783.17
Existing | CZ01 | cDXHP | Cooling | 423681.44 | 0
Existing | CZ01 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ01 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ01 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXHP | Fans | 1284781.16 | 0
Existing | CZ01 | cDXHP | Pumps | 92692.51 | 0
Existing | CZ01 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ01 | cDXHP | Humidification | 0 | 0
Existing | CZ01 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ01 | cDXHP | Water Systems | 0 | 1023273.58
Existing | CZ01 | cDXHP | Refrigeration | 0 | 0
Existing | CZ01 | cDXHP | Generators | 0 | 0
Existing | CZ01 | cDXHP | Total End Uses | 8663317.19 | 2108394.97
Existing | CZ02 | cDXHP | Heating | 32667.53 | 933258.49
Existing | CZ02 | cDXHP | Cooling | 1945150.41 | 0
Existing | CZ02 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ02 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ02 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXHP | Fans | 1595836.78 | 0
Existing | CZ02 | cDXHP | Pumps | 127090.05 | 0
Existing | CZ02 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ02 | cDXHP | Humidification | 0 | 0
Existing | CZ02 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ02 | cDXHP | Water Systems | 0 | 940087.89
Existing | CZ02 | cDXHP | Refrigeration | 0 | 0
Existing | CZ02 | cDXHP | Generators | 0 | 0
Existing | CZ02 | cDXHP | Total End Uses | 10526726.29 | 2022684.6
Existing | CZ03 | cDXHP | Heating | 15899.95 | 566948.32
Existing | CZ03 | cDXHP | Cooling | 1356860.97 | 0
Existing | CZ03 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ03 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ03 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXHP | Fans | 1434649.55 | 0
Existing | CZ03 | cDXHP | Pumps | 117482.25 | 0
Existing | CZ03 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ03 | cDXHP | Humidification | 0 | 0
Existing | CZ03 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ03 | cDXHP | Water Systems | 0 | 936341.98
Existing | CZ03 | cDXHP | Refrigeration | 0 | 0
Existing | CZ03 | cDXHP | Generators | 0 | 0
Existing | CZ03 | cDXHP | Total End Uses | 9750874.24 | 1652628.51
Existing | CZ04 | cDXHP | Heating | 14526.18 | 566322.62
Existing | CZ04 | cDXHP | Cooling | 2158967.69 | 0
Existing | CZ04 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ04 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ04 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXHP | Fans | 1644094.35 | 0
Existing | CZ04 | cDXHP | Pumps | 129672.56 | 0
Existing | CZ04 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ04 | cDXHP | Humidification | 0 | 0
Existing | CZ04 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ04 | cDXHP | Water Systems | 0 | 904240.01
Existing | CZ04 | cDXHP | Refrigeration | 0 | 0
Existing | CZ04 | cDXHP | Generators | 0 | 0
Existing | CZ04 | cDXHP | Total End Uses | 10773242.29 | 1619900.85
Existing | CZ05 | cDXHP | Heating | 16714.08 | 589399.37
Existing | CZ05 | cDXHP | Cooling | 1588878.99 | 0
Existing | CZ05 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ05 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ05 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXHP | Fans | 1496822.23 | 0
Existing | CZ05 | cDXHP | Pumps | 113346.33 | 0
Existing | CZ05 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ05 | cDXHP | Humidification | 0 | 0
Existing | CZ05 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ05 | cDXHP | Water Systems | 0 | 936439.75
Existing | CZ05 | cDXHP | Refrigeration | 0 | 0
Existing | CZ05 | cDXHP | Generators | 0 | 0
Existing | CZ05 | cDXHP | Total End Uses | 10041743.14 | 1675177.33
Existing | CZ06 | cDXHP | Heating | 2503.83 | 178763.95
Existing | CZ06 | cDXHP | Cooling | 2523086.72 | 0
Existing | CZ06 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ06 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ06 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXHP | Fans | 1584972.36 | 0
Existing | CZ06 | cDXHP | Pumps | 123729.62 | 0
Existing | CZ06 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ06 | cDXHP | Humidification | 0 | 0
Existing | CZ06 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ06 | cDXHP | Water Systems | 0 | 862423.82
Existing | CZ06 | cDXHP | Refrigeration | 0 | 0
Existing | CZ06 | cDXHP | Generators | 0 | 0
Existing | CZ06 | cDXHP | Total End Uses | 11060274.04 | 1190525.99
Existing | CZ07 | cDXHP | Heating | 2437.89 | 191551.06
Existing | CZ07 | cDXHP | Cooling | 2769447.93 | 0
Existing | CZ07 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ07 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ07 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXHP | Fans | 1608374.94 | 0
Existing | CZ07 | cDXHP | Pumps | 130067.04 | 0
Existing | CZ07 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ07 | cDXHP | Humidification | 0 | 0
Existing | CZ07 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ07 | cDXHP | Water Systems | 0 | 851493.03
Existing | CZ07 | cDXHP | Refrigeration | 0 | 0
Existing | CZ07 | cDXHP | Generators | 0 | 0
Existing | CZ07 | cDXHP | Total End Uses | 11336309.32 | 1192382.3
Existing | CZ08 | cDXHP | Heating | 3954.96 | 296328.3
Existing | CZ08 | cDXHP | Cooling | 3059497.63 | 0
Existing | CZ08 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ08 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ08 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXHP | Fans | 1740357.4 | 0
Existing | CZ08 | cDXHP | Pumps | 137628.87 | 0
Existing | CZ08 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ08 | cDXHP | Humidification | 0 | 0
Existing | CZ08 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ08 | cDXHP | Water Systems | 0 | 850296.93
Existing | CZ08 | cDXHP | Refrigeration | 0 | 0
Existing | CZ08 | cDXHP | Generators | 0 | 0
Existing | CZ08 | cDXHP | Total End Uses | 11767420.38 | 1295963.45
Existing | CZ09 | cDXHP | Heating | 2796.3 | 302467.32
Existing | CZ09 | cDXHP | Cooling | 3363703.46 | 0
Existing | CZ09 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ09 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ09 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXHP | Fans | 1875054.62 | 0
Existing | CZ09 | cDXHP | Pumps | 140342.34 | 0
Existing | CZ09 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ09 | cDXHP | Humidification | 0 | 0
Existing | CZ09 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ09 | cDXHP | Water Systems | 0 | 838488.65
Existing | CZ09 | cDXHP | Refrigeration | 0 | 0
Existing | CZ09 | cDXHP | Generators | 0 | 0
Existing | CZ09 | cDXHP | Total End Uses | 12207878.25 | 1290294.19
Existing | CZ10 | cDXHP | Heating | 12748.39 | 659093.66
Existing | CZ10 | cDXHP | Cooling | 3901570.75 | 0
Existing | CZ10 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ10 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ10 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXHP | Fans | 2070709.36 | 0
Existing | CZ10 | cDXHP | Pumps | 153506.58 | 0
Existing | CZ10 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ10 | cDXHP | Humidification | 0 | 0
Existing | CZ10 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ10 | cDXHP | Water Systems | 0 | 831688.46
Existing | CZ10 | cDXHP | Refrigeration | 0 | 0
Existing | CZ10 | cDXHP | Generators | 0 | 0
Existing | CZ10 | cDXHP | Total End Uses | 12964516.58 | 1640120.33
Existing | CZ11 | cDXHP | Heating | 27805.63 | 1033797.91
Existing | CZ11 | cDXHP | Cooling | 3778184.29 | 0
Existing | CZ11 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ11 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ11 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXHP | Fans | 2005487.44 | 0
Existing | CZ11 | cDXHP | Pumps | 152994.17 | 0
Existing | CZ11 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ11 | cDXHP | Humidification | 0 | 0
Existing | CZ11 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ11 | cDXHP | Water Systems | 0 | 850264.16
Existing | CZ11 | cDXHP | Refrigeration | 0 | 0
Existing | CZ11 | cDXHP | Generators | 0 | 0
Existing | CZ11 | cDXHP | Total End Uses | 12790453.06 | 2033400.29
Existing | CZ12 | cDXHP | Heating | 28424.5 | 935358.6
Existing | CZ12 | cDXHP | Cooling | 3312259.7 | 0
Existing | CZ12 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ12 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ12 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXHP | Fans | 1853013.79 | 0
Existing | CZ12 | cDXHP | Pumps | 149687.25 | 0
Existing | CZ12 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ12 | cDXHP | Humidification | 0 | 0
Existing | CZ12 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ12 | cDXHP | Water Systems | 0 | 874274.28
Existing | CZ12 | cDXHP | Refrigeration | 0 | 0
Existing | CZ12 | cDXHP | Generators | 0 | 0
Existing | CZ12 | cDXHP | Total End Uses | 12169366.75 | 1958971.09
Existing | CZ13 | cDXHP | Heating | 19469.3 | 797345.9
Existing | CZ13 | cDXHP | Cooling | 4116182.21 | 0
Existing | CZ13 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ13 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ13 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXHP | Fans | 2023137.95 | 0
Existing | CZ13 | cDXHP | Pumps | 157872.02 | 0
Existing | CZ13 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ13 | cDXHP | Humidification | 0 | 0
Existing | CZ13 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ13 | cDXHP | Water Systems | 0 | 825503.12
Existing | CZ13 | cDXHP | Refrigeration | 0 | 0
Existing | CZ13 | cDXHP | Generators | 0 | 0
Existing | CZ13 | cDXHP | Total End Uses | 13142643 | 1772187.24
Existing | CZ14 | cDXHP | Heating | 12009.57 | 617452.01
Existing | CZ14 | cDXHP | Cooling | 4790199.29 | 0
Existing | CZ14 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ14 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ14 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXHP | Fans | 2281484.11 | 0
Existing | CZ14 | cDXHP | Pumps | 158590.05 | 0
Existing | CZ14 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ14 | cDXHP | Humidification | 0 | 0
Existing | CZ14 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ14 | cDXHP | Water Systems | 0 | 783621.48
Existing | CZ14 | cDXHP | Refrigeration | 0 | 0
Existing | CZ14 | cDXHP | Generators | 0 | 0
Existing | CZ14 | cDXHP | Total End Uses | 14068264.53 | 1550411.7
Existing | CZ15 | cDXHP | Heating | 3085.45 | 503705.36
Existing | CZ15 | cDXHP | Cooling | 6213160.23 | 0
Existing | CZ15 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ15 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ15 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXHP | Fans | 2319042.2 | 0
Existing | CZ15 | cDXHP | Pumps | 167061.46 | 0
Existing | CZ15 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ15 | cDXHP | Humidification | 0 | 0
Existing | CZ15 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ15 | cDXHP | Water Systems | 0 | 695432.2
Existing | CZ15 | cDXHP | Refrigeration | 0 | 0
Existing | CZ15 | cDXHP | Generators | 0 | 0
Existing | CZ15 | cDXHP | Total End Uses | 15528330.85 | 1348475.78
Existing | CZ16 | cDXHP | Heating | 58955.35 | 1319158.66
Existing | CZ16 | cDXHP | Cooling | 3832558.57 | 0
Existing | CZ16 | cDXHP | Interior Lighting | 2929105.9 | 0
Existing | CZ16 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ16 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXHP | Fans | 2304742.68 | 0
Existing | CZ16 | cDXHP | Pumps | 144851.23 | 0
Existing | CZ16 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ16 | cDXHP | Humidification | 0 | 0
Existing | CZ16 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ16 | cDXHP | Water Systems | 0 | 924496.62
Existing | CZ16 | cDXHP | Refrigeration | 0 | 0
Existing | CZ16 | cDXHP | Generators | 0 | 0
Existing | CZ16 | cDXHP | Total End Uses | 13167089.36 | 2392993.49
New Construction | CZ01 | cDXHP | Heating | 42090.99 | 752038
New Construction | CZ01 | cDXHP | Cooling | 323026.01 | 0
New Construction | CZ01 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ01 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ01 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXHP | Fans | 1093962.15 | 0
New Construction | CZ01 | cDXHP | Pumps | 78209.23 | 0
New Construction | CZ01 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXHP | Humidification | 0 | 0
New Construction | CZ01 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXHP | Water Systems | 0 | 1022682.14
New Construction | CZ01 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ01 | cDXHP | Generators | 0 | 0
New Construction | CZ01 | cDXHP | Total End Uses | 7574809.74 | 1924058.36
New Construction | CZ02 | cDXHP | Heating | 57103.17 | 1192573.56
New Construction | CZ02 | cDXHP | Cooling | 1656766.55 | 0
New Construction | CZ02 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ02 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ02 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXHP | Fans | 1408932.19 | 0
New Construction | CZ02 | cDXHP | Pumps | 108876.52 | 0
New Construction | CZ02 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXHP | Humidification | 0 | 0
New Construction | CZ02 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXHP | Water Systems | 0 | 939822.9
New Construction | CZ02 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ02 | cDXHP | Generators | 0 | 0
New Construction | CZ02 | cDXHP | Total End Uses | 9269199.79 | 2281734.68
New Construction | CZ03 | cDXHP | Heating | 29837.26 | 831923.46
New Construction | CZ03 | cDXHP | Cooling | 1161984.92 | 0
New Construction | CZ03 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ03 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ03 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXHP | Fans | 1265816.11 | 0
New Construction | CZ03 | cDXHP | Pumps | 102426.78 | 0
New Construction | CZ03 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXHP | Humidification | 0 | 0
New Construction | CZ03 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXHP | Water Systems | 0 | 936093.19
New Construction | CZ03 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ03 | cDXHP | Generators | 0 | 0
New Construction | CZ03 | cDXHP | Total End Uses | 8597586.41 | 1917354.87
New Construction | CZ04 | cDXHP | Heating | 25561.21 | 793931.88
New Construction | CZ04 | cDXHP | Cooling | 1888624.98 | 0
New Construction | CZ04 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ04 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ04 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXHP | Fans | 1450358.18 | 0
New Construction | CZ04 | cDXHP | Pumps | 115256.14 | 0
New Construction | CZ04 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXHP | Humidification | 0 | 0
New Construction | CZ04 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXHP | Water Systems | 0 | 903947.68
New Construction | CZ04 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ04 | cDXHP | Generators | 0 | 0
New Construction | CZ04 | cDXHP | Total End Uses | 9517321.87 | 1847217.78
New Construction | CZ05 | cDXHP | Heating | 31852.75 | 866722.34
New Construction | CZ05 | cDXHP | Cooling | 1353234.68 | 0
New Construction | CZ05 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ05 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ05 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXHP | Fans | 1309673.9 | 0
New Construction | CZ05 | cDXHP | Pumps | 98505.98 | 0
New Construction | CZ05 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXHP | Humidification | 0 | 0
New Construction | CZ05 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXHP | Water Systems | 0 | 936185.35
New Construction | CZ05 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ05 | cDXHP | Generators | 0 | 0
New Construction | CZ05 | cDXHP | Total End Uses | 8830788.65 | 1952245.91
New Construction | CZ06 | cDXHP | Heating | 5443.11 | 319982.44
New Construction | CZ06 | cDXHP | Cooling | 2145086.48 | 0
New Construction | CZ06 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ06 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ06 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXHP | Fans | 1380060.23 | 0
New Construction | CZ06 | cDXHP | Pumps | 110057.59 | 0
New Construction | CZ06 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXHP | Humidification | 0 | 0
New Construction | CZ06 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXHP | Water Systems | 0 | 862273.17
New Construction | CZ06 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ06 | cDXHP | Generators | 0 | 0
New Construction | CZ06 | cDXHP | Total End Uses | 9678168.76 | 1331593.83
New Construction | CZ07 | cDXHP | Heating | 4749.25 | 304979.32
New Construction | CZ07 | cDXHP | Cooling | 2351442.81 | 0
New Construction | CZ07 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ07 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ07 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXHP | Fans | 1383699.92 | 0
New Construction | CZ07 | cDXHP | Pumps | 114782.97 | 0
New Construction | CZ07 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXHP | Humidification | 0 | 0
New Construction | CZ07 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXHP | Water Systems | 0 | 851239.49
New Construction | CZ07 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ07 | cDXHP | Generators | 0 | 0
New Construction | CZ07 | cDXHP | Total End Uses | 9892196.3 | 1305557.03
New Construction | CZ08 | cDXHP | Heating | 7928.86 | 445921.43
New Construction | CZ08 | cDXHP | Cooling | 2657806.99 | 0
New Construction | CZ08 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ08 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ08 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXHP | Fans | 1521086.36 | 0
New Construction | CZ08 | cDXHP | Pumps | 123991.02 | 0
New Construction | CZ08 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXHP | Humidification | 0 | 0
New Construction | CZ08 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXHP | Water Systems | 0 | 850089.38
New Construction | CZ08 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ08 | cDXHP | Generators | 0 | 0
New Construction | CZ08 | cDXHP | Total End Uses | 10348334.58 | 1445349.02
New Construction | CZ09 | cDXHP | Heating | 5681.83 | 431110.29
New Construction | CZ09 | cDXHP | Cooling | 2937134.66 | 0
New Construction | CZ09 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ09 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ09 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXHP | Fans | 1645314.24 | 0
New Construction | CZ09 | cDXHP | Pumps | 127183.99 | 0
New Construction | CZ09 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXHP | Humidification | 0 | 0
New Construction | CZ09 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXHP | Water Systems | 0 | 838283.29
New Construction | CZ09 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ09 | cDXHP | Generators | 0 | 0
New Construction | CZ09 | cDXHP | Total End Uses | 10752836.06 | 1418731.79
New Construction | CZ10 | cDXHP | Heating | 20017.92 | 711219.24
New Construction | CZ10 | cDXHP | Cooling | 3399291.22 | 0
New Construction | CZ10 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ10 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ10 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXHP | Fans | 1793296.18 | 0
New Construction | CZ10 | cDXHP | Pumps | 136437.97 | 0
New Construction | CZ10 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXHP | Humidification | 0 | 0
New Construction | CZ10 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXHP | Water Systems | 0 | 831508.09
New Construction | CZ10 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ10 | cDXHP | Generators | 0 | 0
New Construction | CZ10 | cDXHP | Total End Uses | 11386564.63 | 1692065.56
New Construction | CZ11 | cDXHP | Heating | 25950.65 | 607262.32
New Construction | CZ11 | cDXHP | Cooling | 2994427.41 | 0
New Construction | CZ11 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ11 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ11 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXHP | Fans | 1526305.81 | 0
New Construction | CZ11 | cDXHP | Pumps | 126054.82 | 0
New Construction | CZ11 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXHP | Humidification | 0 | 0
New Construction | CZ11 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXHP | Water Systems | 0 | 849810.04
New Construction | CZ11 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ11 | cDXHP | Generators | 0 | 0
New Construction | CZ11 | cDXHP | Total End Uses | 10710260.04 | 1606410.58
New Construction | CZ12 | cDXHP | Heating | 30243.16 | 624804.45
New Construction | CZ12 | cDXHP | Cooling | 2666121.75 | 0
New Construction | CZ12 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ12 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ12 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXHP | Fans | 1455803.94 | 0
New Construction | CZ12 | cDXHP | Pumps | 125808.87 | 0
New Construction | CZ12 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXHP | Humidification | 0 | 0
New Construction | CZ12 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXHP | Water Systems | 0 | 873798.14
New Construction | CZ12 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ12 | cDXHP | Generators | 0 | 0
New Construction | CZ12 | cDXHP | Total End Uses | 10315499.07 | 1647940.8
New Construction | CZ13 | cDXHP | Heating | 20347.8 | 513867.16
New Construction | CZ13 | cDXHP | Cooling | 3283425.28 | 0
New Construction | CZ13 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ13 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ13 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXHP | Fans | 1566082.57 | 0
New Construction | CZ13 | cDXHP | Pumps | 131576.34 | 0
New Construction | CZ13 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXHP | Humidification | 0 | 0
New Construction | CZ13 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXHP | Water Systems | 0 | 824978.38
New Construction | CZ13 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ13 | cDXHP | Generators | 0 | 0
New Construction | CZ13 | cDXHP | Total End Uses | 11038953.35 | 1488183.76
New Construction | CZ14 | cDXHP | Heating | 13633.53 | 440464.63
New Construction | CZ14 | cDXHP | Cooling | 3846042.88 | 0
New Construction | CZ14 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ14 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ14 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXHP | Fans | 1759050.84 | 0
New Construction | CZ14 | cDXHP | Pumps | 131231.48 | 0
New Construction | CZ14 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXHP | Humidification | 0 | 0
New Construction | CZ14 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXHP | Water Systems | 0 | 783065.76
New Construction | CZ14 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ14 | cDXHP | Generators | 0 | 0
New Construction | CZ14 | cDXHP | Total End Uses | 11787480.07 | 1372868.62
New Construction | CZ15 | cDXHP | Heating | 3934.02 | 412852.22
New Construction | CZ15 | cDXHP | Cooling | 5035956.4 | 0
New Construction | CZ15 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ15 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ15 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXHP | Fans | 1773676.84 | 0
New Construction | CZ15 | cDXHP | Pumps | 138842.8 | 0
New Construction | CZ15 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXHP | Humidification | 0 | 0
New Construction | CZ15 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXHP | Water Systems | 0 | 694926.74
New Construction | CZ15 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ15 | cDXHP | Generators | 0 | 0
New Construction | CZ15 | cDXHP | Total End Uses | 12989931.4 | 1257117.18
New Construction | CZ16 | cDXHP | Heating | 64033.07 | 813596.91
New Construction | CZ16 | cDXHP | Cooling | 3033428.67 | 0
New Construction | CZ16 | cDXHP | Interior Lighting | 2140645.73 | 0
New Construction | CZ16 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXHP | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ16 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXHP | Fans | 1792860.96 | 0
New Construction | CZ16 | cDXHP | Pumps | 119181.83 | 0
New Construction | CZ16 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXHP | Humidification | 0 | 0
New Construction | CZ16 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXHP | Water Systems | 0 | 924193.12
New Construction | CZ16 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ16 | cDXHP | Generators | 0 | 0
New Construction | CZ16 | cDXHP | Total End Uses | 11047025.88 | 1887128.24
Existing | CZ01 | cDXOH | Heating | 0 | 959435.67
Existing | CZ01 | cDXOH | Cooling | 421979.27 | 0
Existing | CZ01 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ01 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ01 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXOH | Fans | 1285427.26 | 0
Existing | CZ01 | cDXOH | Pumps | 92143.19 | 0
Existing | CZ01 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ01 | cDXOH | Humidification | 0 | 0
Existing | CZ01 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ01 | cDXOH | Water Systems | 0 | 1023238.16
Existing | CZ01 | cDXOH | Refrigeration | 0 | 0
Existing | CZ01 | cDXOH | Generators | 0 | 0
Existing | CZ01 | cDXOH | Total End Uses | 8625531.23 | 2132012.04
Existing | CZ02 | cDXOH | Heating | 0 | 948602.96
Existing | CZ02 | cDXOH | Cooling | 1944424.87 | 0
Existing | CZ02 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ02 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ02 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXOH | Fans | 1596253.91 | 0
Existing | CZ02 | cDXOH | Pumps | 126586.99 | 0
Existing | CZ02 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ02 | cDXOH | Humidification | 0 | 0
Existing | CZ02 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ02 | cDXOH | Water Systems | 0 | 940102.83
Existing | CZ02 | cDXOH | Refrigeration | 0 | 0
Existing | CZ02 | cDXOH | Generators | 0 | 0
Existing | CZ02 | cDXOH | Total End Uses | 10493247.28 | 2038044.01
Existing | CZ03 | cDXOH | Heating | 0 | 574725.69
Existing | CZ03 | cDXOH | Cooling | 1356905.62 | 0
Existing | CZ03 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ03 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ03 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXOH | Fans | 1434668.9 | 0
Existing | CZ03 | cDXOH | Pumps | 117255.19 | 0
Existing | CZ03 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ03 | cDXOH | Humidification | 0 | 0
Existing | CZ03 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ03 | cDXOH | Water Systems | 0 | 936322.61
Existing | CZ03 | cDXOH | Refrigeration | 0 | 0
Existing | CZ03 | cDXOH | Generators | 0 | 0
Existing | CZ03 | cDXOH | Total End Uses | 9734811.23 | 1660386.52
Existing | CZ04 | cDXOH | Heating | 0 | 572825.82
Existing | CZ04 | cDXOH | Cooling | 2158961.78 | 0
Existing | CZ04 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ04 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ04 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXOH | Fans | 1644137.29 | 0
Existing | CZ04 | cDXOH | Pumps | 129497.9 | 0
Existing | CZ04 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ04 | cDXOH | Humidification | 0 | 0
Existing | CZ04 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ04 | cDXOH | Water Systems | 0 | 904247.23
Existing | CZ04 | cDXOH | Refrigeration | 0 | 0
Existing | CZ04 | cDXOH | Generators | 0 | 0
Existing | CZ04 | cDXOH | Total End Uses | 10758578.49 | 1626411.27
Existing | CZ05 | cDXOH | Heating | 0 | 597026.86
Existing | CZ05 | cDXOH | Cooling | 1588746.4 | 0
Existing | CZ05 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ05 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ05 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXOH | Fans | 1496806.99 | 0
Existing | CZ05 | cDXOH | Pumps | 113253.14 | 0
Existing | CZ05 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ05 | cDXOH | Humidification | 0 | 0
Existing | CZ05 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ05 | cDXOH | Water Systems | 0 | 936437.8
Existing | CZ05 | cDXOH | Refrigeration | 0 | 0
Existing | CZ05 | cDXOH | Generators | 0 | 0
Existing | CZ05 | cDXOH | Total End Uses | 10024788.05 | 1682802.88
Existing | CZ06 | cDXOH | Heating | 0 | 179506.64
Existing | CZ06 | cDXOH | Cooling | 2531253.45 | 0
Existing | CZ06 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ06 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ06 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXOH | Fans | 1584914.93 | 0
Existing | CZ06 | cDXOH | Pumps | 123732 | 0
Existing | CZ06 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ06 | cDXOH | Humidification | 0 | 0
Existing | CZ06 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ06 | cDXOH | Water Systems | 0 | 862428.95
Existing | CZ06 | cDXOH | Refrigeration | 0 | 0
Existing | CZ06 | cDXOH | Generators | 0 | 0
Existing | CZ06 | cDXOH | Total End Uses | 11065881.91 | 1191273.81
Existing | CZ07 | cDXOH | Heating | 0 | 192396.64
Existing | CZ07 | cDXOH | Cooling | 2774907.9 | 0
Existing | CZ07 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ07 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ07 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXOH | Fans | 1608326.52 | 0
Existing | CZ07 | cDXOH | Pumps | 130061.93 | 0
Existing | CZ07 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ07 | cDXOH | Humidification | 0 | 0
Existing | CZ07 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ07 | cDXOH | Water Systems | 0 | 851430.77
Existing | CZ07 | cDXOH | Refrigeration | 0 | 0
Existing | CZ07 | cDXOH | Generators | 0 | 0
Existing | CZ07 | cDXOH | Total End Uses | 11339277.87 | 1193165.63
Existing | CZ08 | cDXOH | Heating | 0 | 297890.89
Existing | CZ08 | cDXOH | Cooling | 3062744.61 | 0
Existing | CZ08 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ08 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ08 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXOH | Fans | 1740325.27 | 0
Existing | CZ08 | cDXOH | Pumps | 137608.63 | 0
Existing | CZ08 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ08 | cDXOH | Humidification | 0 | 0
Existing | CZ08 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ08 | cDXOH | Water Systems | 0 | 850259.39
Existing | CZ08 | cDXOH | Refrigeration | 0 | 0
Existing | CZ08 | cDXOH | Generators | 0 | 0
Existing | CZ08 | cDXOH | Total End Uses | 11766660.02 | 1297488.49
Existing | CZ09 | cDXOH | Heating | 0 | 303436.95
Existing | CZ09 | cDXOH | Cooling | 3367040.27 | 0
Existing | CZ09 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ09 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ09 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXOH | Fans | 1874998.61 | 0
Existing | CZ09 | cDXOH | Pumps | 140324.97 | 0
Existing | CZ09 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ09 | cDXOH | Humidification | 0 | 0
Existing | CZ09 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ09 | cDXOH | Water Systems | 0 | 838490.84
Existing | CZ09 | cDXOH | Refrigeration | 0 | 0
Existing | CZ09 | cDXOH | Generators | 0 | 0
Existing | CZ09 | cDXOH | Total End Uses | 12208345.37 | 1291266.01
Existing | CZ10 | cDXOH | Heating | 0 | 664110.99
Existing | CZ10 | cDXOH | Cooling | 3900756.97 | 0
Existing | CZ10 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ10 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ10 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXOH | Fans | 2070743.9 | 0
Existing | CZ10 | cDXOH | Pumps | 153348.84 | 0
Existing | CZ10 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ10 | cDXOH | Humidification | 0 | 0
Existing | CZ10 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ10 | cDXOH | Water Systems | 0 | 831702.06
Existing | CZ10 | cDXOH | Refrigeration | 0 | 0
Existing | CZ10 | cDXOH | Generators | 0 | 0
Existing | CZ10 | cDXOH | Total End Uses | 12950831.23 | 1645151.26
Existing | CZ11 | cDXOH | Heating | 0 | 1047675.46
Existing | CZ11 | cDXOH | Cooling | 3771511.77 | 0
Existing | CZ11 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ11 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ11 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXOH | Fans | 2006483.38 | 0
Existing | CZ11 | cDXOH | Pumps | 152500.91 | 0
Existing | CZ11 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ11 | cDXOH | Humidification | 0 | 0
Existing | CZ11 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ11 | cDXOH | Water Systems | 0 | 850275.79
Existing | CZ11 | cDXOH | Refrigeration | 0 | 0
Existing | CZ11 | cDXOH | Generators | 0 | 0
Existing | CZ11 | cDXOH | Total End Uses | 12756477.58 | 2047289.47
Existing | CZ12 | cDXOH | Heating | 0 | 949100.6
Existing | CZ12 | cDXOH | Cooling | 3308060.37 | 0
Existing | CZ12 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ12 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ12 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXOH | Fans | 1853695.69 | 0
Existing | CZ12 | cDXOH | Pumps | 149199.69 | 0
Existing | CZ12 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ12 | cDXOH | Humidification | 0 | 0
Existing | CZ12 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ12 | cDXOH | Water Systems | 0 | 874265.58
Existing | CZ12 | cDXOH | Refrigeration | 0 | 0
Existing | CZ12 | cDXOH | Generators | 0 | 0
Existing | CZ12 | cDXOH | Total End Uses | 12136937.27 | 1972704.39
Existing | CZ13 | cDXOH | Heating | 0 | 809100.63
Existing | CZ13 | cDXOH | Cooling | 4112392.81 | 0
Existing | CZ13 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ13 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ13 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXOH | Fans | 2023731.95 | 0
Existing | CZ13 | cDXOH | Pumps | 157626.02 | 0
Existing | CZ13 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ13 | cDXOH | Humidification | 0 | 0
Existing | CZ13 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ13 | cDXOH | Water Systems | 0 | 825484.99
Existing | CZ13 | cDXOH | Refrigeration | 0 | 0
Existing | CZ13 | cDXOH | Generators | 0 | 0
Existing | CZ13 | cDXOH | Total End Uses | 13119732.29 | 1783923.83
Existing | CZ14 | cDXOH | Heating | 0 | 623387.91
Existing | CZ14 | cDXOH | Cooling | 4785699.29 | 0
Existing | CZ14 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ14 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ14 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXOH | Fans | 2281466.96 | 0
Existing | CZ14 | cDXOH | Pumps | 158500.55 | 0
Existing | CZ14 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ14 | cDXOH | Humidification | 0 | 0
Existing | CZ14 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ14 | cDXOH | Water Systems | 0 | 783551.49
Existing | CZ14 | cDXOH | Refrigeration | 0 | 0
Existing | CZ14 | cDXOH | Generators | 0 | 0
Existing | CZ14 | cDXOH | Total End Uses | 14051648.32 | 1556277.62
Existing | CZ15 | cDXOH | Heating | 0 | 504407.47
Existing | CZ15 | cDXOH | Cooling | 6212500.72 | 0
Existing | CZ15 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ15 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ15 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXOH | Fans | 2318958.31 | 0
Existing | CZ15 | cDXOH | Pumps | 167059.35 | 0
Existing | CZ15 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ15 | cDXOH | Humidification | 0 | 0
Existing | CZ15 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ15 | cDXOH | Water Systems | 0 | 695461.44
Existing | CZ15 | cDXOH | Refrigeration | 0 | 0
Existing | CZ15 | cDXOH | Generators | 0 | 0
Existing | CZ15 | cDXOH | Total End Uses | 15524499.9 | 1349207.12
Existing | CZ16 | cDXOH | Heating | 0 | 1342950.42
Existing | CZ16 | cDXOH | Cooling | 3823553.08 | 0
Existing | CZ16 | cDXOH | Interior Lighting | 2929105.9 | 0
Existing | CZ16 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ16 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXOH | Fans | 2307389.76 | 0
Existing | CZ16 | cDXOH | Pumps | 144401.25 | 0
Existing | CZ16 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ16 | cDXOH | Humidification | 0 | 0
Existing | CZ16 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ16 | cDXOH | Water Systems | 0 | 924528.54
Existing | CZ16 | cDXOH | Refrigeration | 0 | 0
Existing | CZ16 | cDXOH | Generators | 0 | 0
Existing | CZ16 | cDXOH | Total End Uses | 13101325.6 | 2416817.18
New Construction | CZ01 | cDXOH | Heating | 0 | 784589.86
New Construction | CZ01 | cDXOH | Cooling | 319965.71 | 0
New Construction | CZ01 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ01 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ01 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXOH | Fans | 1094999.83 | 0
New Construction | CZ01 | cDXOH | Pumps | 77366.17 | 0
New Construction | CZ01 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXOH | Humidification | 0 | 0
New Construction | CZ01 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXOH | Water Systems | 0 | 1022586.11
New Construction | CZ01 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ01 | cDXOH | Generators | 0 | 0
New Construction | CZ01 | cDXOH | Total End Uses | 7529853.06 | 1956514.19
New Construction | CZ02 | cDXOH | Heating | 0 | 1214479.41
New Construction | CZ02 | cDXOH | Cooling | 1654994.54 | 0
New Construction | CZ02 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ02 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ02 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXOH | Fans | 1411256.87 | 0
New Construction | CZ02 | cDXOH | Pumps | 108092.01 | 0
New Construction | CZ02 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXOH | Humidification | 0 | 0
New Construction | CZ02 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXOH | Water Systems | 0 | 939771.81
New Construction | CZ02 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ02 | cDXOH | Generators | 0 | 0
New Construction | CZ02 | cDXOH | Total End Uses | 9211864.77 | 2303589.44
New Construction | CZ03 | cDXOH | Heating | 0 | 842945
New Construction | CZ03 | cDXOH | Cooling | 1161713.92 | 0
New Construction | CZ03 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ03 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ03 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXOH | Fans | 1265966.56 | 0
New Construction | CZ03 | cDXOH | Pumps | 101942.55 | 0
New Construction | CZ03 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXOH | Humidification | 0 | 0
New Construction | CZ03 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXOH | Water Systems | 0 | 936110.22
New Construction | CZ03 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ03 | cDXOH | Generators | 0 | 0
New Construction | CZ03 | cDXOH | Total End Uses | 8567144.39 | 1928393.44
New Construction | CZ04 | cDXOH | Heating | 0 | 802844.77
New Construction | CZ04 | cDXOH | Cooling | 1887846.58 | 0
New Construction | CZ04 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ04 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ04 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXOH | Fans | 1450467.43 | 0
New Construction | CZ04 | cDXOH | Pumps | 114694.45 | 0
New Construction | CZ04 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXOH | Humidification | 0 | 0
New Construction | CZ04 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXOH | Water Systems | 0 | 903934.68
New Construction | CZ04 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ04 | cDXOH | Generators | 0 | 0
New Construction | CZ04 | cDXOH | Total End Uses | 9490529.8 | 1856117.68
New Construction | CZ05 | cDXOH | Heating | 0 | 877009.32
New Construction | CZ05 | cDXOH | Cooling | 1351363.35 | 0
New Construction | CZ05 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ05 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ05 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXOH | Fans | 1309715.43 | 0
New Construction | CZ05 | cDXOH | Pumps | 98122.72 | 0
New Construction | CZ05 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXOH | Humidification | 0 | 0
New Construction | CZ05 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXOH | Water Systems | 0 | 936166.37
New Construction | CZ05 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ05 | cDXOH | Generators | 0 | 0
New Construction | CZ05 | cDXOH | Total End Uses | 8796722.85 | 1962513.9
New Construction | CZ06 | cDXOH | Heating | 0 | 321394.63
New Construction | CZ06 | cDXOH | Cooling | 2152994.18 | 0
New Construction | CZ06 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ06 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ06 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXOH | Fans | 1379958.72 | 0
New Construction | CZ06 | cDXOH | Pumps | 109937.11 | 0
New Construction | CZ06 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXOH | Humidification | 0 | 0
New Construction | CZ06 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXOH | Water Systems | 0 | 862281.89
New Construction | CZ06 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ06 | cDXOH | Generators | 0 | 0
New Construction | CZ06 | cDXOH | Total End Uses | 9680411.37 | 1333014.74
New Construction | CZ07 | cDXOH | Heating | 0 | 306221.36
New Construction | CZ07 | cDXOH | Cooling | 2356995.24 | 0
New Construction | CZ07 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ07 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ07 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXOH | Fans | 1383642.35 | 0
New Construction | CZ07 | cDXOH | Pumps | 114728.94 | 0
New Construction | CZ07 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXOH | Humidification | 0 | 0
New Construction | CZ07 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXOH | Water Systems | 0 | 851233.17
New Construction | CZ07 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ07 | cDXOH | Generators | 0 | 0
New Construction | CZ07 | cDXOH | Total End Uses | 9892887.87 | 1306792.75
New Construction | CZ08 | cDXOH | Heating | 0 | 448130.25
New Construction | CZ08 | cDXOH | Cooling | 2660565.55 | 0
New Construction | CZ08 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ08 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ08 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXOH | Fans | 1520999.78 | 0
New Construction | CZ08 | cDXOH | Pumps | 123842.52 | 0
New Construction | CZ08 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXOH | Humidification | 0 | 0
New Construction | CZ08 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXOH | Water Systems | 0 | 850076.34
New Construction | CZ08 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ08 | cDXOH | Generators | 0 | 0
New Construction | CZ08 | cDXOH | Total End Uses | 10342929.2 | 1447544.81
New Construction | CZ09 | cDXOH | Heating | 0 | 432742.72
New Construction | CZ09 | cDXOH | Cooling | 2940414.15 | 0
New Construction | CZ09 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ09 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ09 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXOH | Fans | 1645179.25 | 0
New Construction | CZ09 | cDXOH | Pumps | 127096.07 | 0
New Construction | CZ09 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXOH | Humidification | 0 | 0
New Construction | CZ09 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXOH | Water Systems | 0 | 838298.33
New Construction | CZ09 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ09 | cDXOH | Generators | 0 | 0
New Construction | CZ09 | cDXOH | Total End Uses | 10750210.82 | 1420379.27
New Construction | CZ10 | cDXOH | Heating | 0 | 717291.5
New Construction | CZ10 | cDXOH | Cooling | 3397371.55 | 0
New Construction | CZ10 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ10 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ10 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXOH | Fans | 1793412.23 | 0
New Construction | CZ10 | cDXOH | Pumps | 136009.77 | 0
New Construction | CZ10 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXOH | Humidification | 0 | 0
New Construction | CZ10 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXOH | Water Systems | 0 | 831584.7
New Construction | CZ10 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ10 | cDXOH | Generators | 0 | 0
New Construction | CZ10 | cDXOH | Total End Uses | 11364314.9 | 1698214.42
New Construction | CZ11 | cDXOH | Heating | 0 | 627454.18
New Construction | CZ11 | cDXOH | Cooling | 2988946.71 | 0
New Construction | CZ11 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ11 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ11 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXOH | Fans | 1526617.38 | 0
New Construction | CZ11 | cDXOH | Pumps | 125798.99 | 0
New Construction | CZ11 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXOH | Humidification | 0 | 0
New Construction | CZ11 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXOH | Water Systems | 0 | 849815.58
New Construction | CZ11 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ11 | cDXOH | Generators | 0 | 0
New Construction | CZ11 | cDXOH | Total End Uses | 10678884.42 | 1626607.98
New Construction | CZ12 | cDXOH | Heating | 0 | 646448.91
New Construction | CZ12 | cDXOH | Cooling | 2661360.5 | 0
New Construction | CZ12 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ12 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ12 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXOH | Fans | 1456385.61 | 0
New Construction | CZ12 | cDXOH | Pumps | 125375.3 | 0
New Construction | CZ12 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXOH | Humidification | 0 | 0
New Construction | CZ12 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXOH | Water Systems | 0 | 873872.27
New Construction | CZ12 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ12 | cDXOH | Generators | 0 | 0
New Construction | CZ12 | cDXOH | Total End Uses | 10280642.76 | 1669659.4
New Construction | CZ13 | cDXOH | Heating | 0 | 528046.15
New Construction | CZ13 | cDXOH | Cooling | 3279774.71 | 0
New Construction | CZ13 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ13 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ13 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXOH | Fans | 1566208.85 | 0
New Construction | CZ13 | cDXOH | Pumps | 131264.38 | 0
New Construction | CZ13 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXOH | Humidification | 0 | 0
New Construction | CZ13 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXOH | Water Systems | 0 | 825080.91
New Construction | CZ13 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ13 | cDXOH | Generators | 0 | 0
New Construction | CZ13 | cDXOH | Total End Uses | 11014769.3 | 1502465.28
New Construction | CZ14 | cDXOH | Heating | 0 | 447400.52
New Construction | CZ14 | cDXOH | Cooling | 3841503.53 | 0
New Construction | CZ14 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ14 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ14 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXOH | Fans | 1758954.17 | 0
New Construction | CZ14 | cDXOH | Pumps | 131412.94 | 0
New Construction | CZ14 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXOH | Humidification | 0 | 0
New Construction | CZ14 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXOH | Water Systems | 0 | 783119.59
New Construction | CZ14 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ14 | cDXOH | Generators | 0 | 0
New Construction | CZ14 | cDXOH | Total End Uses | 11769392 | 1379858.33
New Construction | CZ15 | cDXOH | Heating | 0 | 413764.84
New Construction | CZ15 | cDXOH | Cooling | 5034410.11 | 0
New Construction | CZ15 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ15 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ15 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXOH | Fans | 1773508.2 | 0
New Construction | CZ15 | cDXOH | Pumps | 138832.57 | 0
New Construction | CZ15 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXOH | Humidification | 0 | 0
New Construction | CZ15 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXOH | Water Systems | 0 | 694879.98
New Construction | CZ15 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ15 | cDXOH | Generators | 0 | 0
New Construction | CZ15 | cDXOH | Total End Uses | 12984272.22 | 1257983.04
New Construction | CZ16 | cDXOH | Heating | 0 | 849675.67
New Construction | CZ16 | cDXOH | Cooling | 3022727.13 | 0
New Construction | CZ16 | cDXOH | Interior Lighting | 2140645.73 | 0
New Construction | CZ16 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXOH | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ16 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXOH | Fans | 1792967.77 | 0
New Construction | CZ16 | cDXOH | Pumps | 119195.57 | 0
New Construction | CZ16 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXOH | Humidification | 0 | 0
New Construction | CZ16 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXOH | Water Systems | 0 | 924182.62
New Construction | CZ16 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ16 | cDXOH | Generators | 0 | 0
New Construction | CZ16 | cDXOH | Total End Uses | 10972411.82 | 1923196.51
Existing | CZ01 | cPVVG | Heating | 0 | 1188855.86
Existing | CZ01 | cPVVG | Cooling | 426975.58 | 0
Existing | CZ01 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ01 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ01 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ01 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ01 | cPVVG | Fans | 782406.58 | 0
Existing | CZ01 | cPVVG | Pumps | 92559.39 | 0
Existing | CZ01 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ01 | cPVVG | Humidification | 0 | 0
Existing | CZ01 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ01 | cPVVG | Water Systems | 0 | 1023195.88
Existing | CZ01 | cPVVG | Refrigeration | 0 | 0
Existing | CZ01 | cPVVG | Generators | 0 | 0
Existing | CZ01 | cPVVG | Total End Uses | 8127923.07 | 2361389.96
Existing | CZ02 | cPVVG | Heating | 0 | 1137341.79
Existing | CZ02 | cPVVG | Cooling | 1937432.87 | 0
Existing | CZ02 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ02 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ02 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ02 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ02 | cPVVG | Fans | 1072362.61 | 0
Existing | CZ02 | cPVVG | Pumps | 126928.58 | 0
Existing | CZ02 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ02 | cPVVG | Humidification | 0 | 0
Existing | CZ02 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ02 | cPVVG | Water Systems | 0 | 940113.09
Existing | CZ02 | cPVVG | Refrigeration | 0 | 0
Existing | CZ02 | cPVVG | Generators | 0 | 0
Existing | CZ02 | cPVVG | Total End Uses | 9962705.57 | 2226793.1
Existing | CZ03 | cPVVG | Heating | 0 | 687968.06
Existing | CZ03 | cPVVG | Cooling | 1366874.36 | 0
Existing | CZ03 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ03 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ03 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ03 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ03 | cPVVG | Fans | 915038.87 | 0
Existing | CZ03 | cPVVG | Pumps | 117380.47 | 0
Existing | CZ03 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ03 | cPVVG | Humidification | 0 | 0
Existing | CZ03 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ03 | cPVVG | Water Systems | 0 | 936344.07
Existing | CZ03 | cPVVG | Refrigeration | 0 | 0
Existing | CZ03 | cPVVG | Generators | 0 | 0
Existing | CZ03 | cPVVG | Total End Uses | 9225275.21 | 1773650.35
Existing | CZ04 | cPVVG | Heating | 0 | 679518.82
Existing | CZ04 | cPVVG | Cooling | 2150996.68 | 0
Existing | CZ04 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ04 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ04 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ04 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ04 | cPVVG | Fans | 1124881.71 | 0
Existing | CZ04 | cPVVG | Pumps | 129628.75 | 0
Existing | CZ04 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ04 | cPVVG | Humidification | 0 | 0
Existing | CZ04 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ04 | cPVVG | Water Systems | 0 | 904236.77
Existing | CZ04 | cPVVG | Refrigeration | 0 | 0
Existing | CZ04 | cPVVG | Generators | 0 | 0
Existing | CZ04 | cPVVG | Total End Uses | 10231488.66 | 1733093.81
Existing | CZ05 | cPVVG | Heating | 0 | 707539.56
Existing | CZ05 | cPVVG | Cooling | 1591608.13 | 0
Existing | CZ05 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ05 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ05 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ05 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ05 | cPVVG | Fans | 988191.58 | 0
Existing | CZ05 | cPVVG | Pumps | 113325.89 | 0
Existing | CZ05 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ05 | cPVVG | Humidification | 0 | 0
Existing | CZ05 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ05 | cPVVG | Water Systems | 0 | 936399.95
Existing | CZ05 | cPVVG | Refrigeration | 0 | 0
Existing | CZ05 | cPVVG | Generators | 0 | 0
Existing | CZ05 | cPVVG | Total End Uses | 9519107.12 | 1793277.73
Existing | CZ06 | cPVVG | Heating | 0 | 206264.77
Existing | CZ06 | cPVVG | Cooling | 2537014.93 | 0
Existing | CZ06 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ06 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ06 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ06 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ06 | cPVVG | Fans | 1095017.1 | 0
Existing | CZ06 | cPVVG | Pumps | 123732.54 | 0
Existing | CZ06 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ06 | cPVVG | Humidification | 0 | 0
Existing | CZ06 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ06 | cPVVG | Water Systems | 0 | 862421.15
Existing | CZ06 | cPVVG | Refrigeration | 0 | 0
Existing | CZ06 | cPVVG | Generators | 0 | 0
Existing | CZ06 | cPVVG | Total End Uses | 10581746.08 | 1218024.14
Existing | CZ07 | cPVVG | Heating | 0 | 217587.22
Existing | CZ07 | cPVVG | Cooling | 2764758.17 | 0
Existing | CZ07 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ07 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ07 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ07 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ07 | cPVVG | Fans | 1125315.25 | 0
Existing | CZ07 | cPVVG | Pumps | 130049.92 | 0
Existing | CZ07 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ07 | cPVVG | Humidification | 0 | 0
Existing | CZ07 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ07 | cPVVG | Water Systems | 0 | 851471.89
Existing | CZ07 | cPVVG | Refrigeration | 0 | 0
Existing | CZ07 | cPVVG | Generators | 0 | 0
Existing | CZ07 | cPVVG | Total End Uses | 10846104.85 | 1218397.33
Existing | CZ08 | cPVVG | Heating | 0 | 334850.62
Existing | CZ08 | cPVVG | Cooling | 3049711.41 | 0
Existing | CZ08 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ08 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ08 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ08 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ08 | cPVVG | Fans | 1244787.81 | 0
Existing | CZ08 | cPVVG | Pumps | 137631.36 | 0
Existing | CZ08 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ08 | cPVVG | Humidification | 0 | 0
Existing | CZ08 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ08 | cPVVG | Water Systems | 0 | 850252.19
Existing | CZ08 | cPVVG | Refrigeration | 0 | 0
Existing | CZ08 | cPVVG | Generators | 0 | 0
Existing | CZ08 | cPVVG | Total End Uses | 11258112.1 | 1334441.02
Existing | CZ09 | cPVVG | Heating | 0 | 333854.77
Existing | CZ09 | cPVVG | Cooling | 3346958.35 | 0
Existing | CZ09 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ09 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ09 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ09 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ09 | cPVVG | Fans | 1372380.46 | 0
Existing | CZ09 | cPVVG | Pumps | 140328.82 | 0
Existing | CZ09 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ09 | cPVVG | Humidification | 0 | 0
Existing | CZ09 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ09 | cPVVG | Water Systems | 0 | 838490.04
Existing | CZ09 | cPVVG | Refrigeration | 0 | 0
Existing | CZ09 | cPVVG | Generators | 0 | 0
Existing | CZ09 | cPVVG | Total End Uses | 11685649.14 | 1321683.03
Existing | CZ10 | cPVVG | Heating | 0 | 751906.47
Existing | CZ10 | cPVVG | Cooling | 3864727.89 | 0
Existing | CZ10 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ10 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ10 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ10 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ10 | cPVVG | Fans | 1543098.92 | 0
Existing | CZ10 | cPVVG | Pumps | 153466.95 | 0
Existing | CZ10 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ10 | cPVVG | Humidification | 0 | 0
Existing | CZ10 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ10 | cPVVG | Water Systems | 0 | 831717.2
Existing | CZ10 | cPVVG | Refrigeration | 0 | 0
Existing | CZ10 | cPVVG | Generators | 0 | 0
Existing | CZ10 | cPVVG | Total End Uses | 12387275.27 | 1732961.89
Existing | CZ11 | cPVVG | Heating | 0 | 1224404.87
Existing | CZ11 | cPVVG | Cooling | 3740520.5 | 0
Existing | CZ11 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ11 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ11 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ11 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ11 | cPVVG | Fans | 1501822.84 | 0
Existing | CZ11 | cPVVG | Pumps | 152925.65 | 0
Existing | CZ11 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ11 | cPVVG | Humidification | 0 | 0
Existing | CZ11 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ11 | cPVVG | Water Systems | 0 | 850270
Existing | CZ11 | cPVVG | Refrigeration | 0 | 0
Existing | CZ11 | cPVVG | Generators | 0 | 0
Existing | CZ11 | cPVVG | Total End Uses | 12221250.5 | 2224013.09
Existing | CZ12 | cPVVG | Heating | 0 | 1118393.1
Existing | CZ12 | cPVVG | Cooling | 3283523.05 | 0
Existing | CZ12 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ12 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ12 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ12 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ12 | cPVVG | Fans | 1359849.88 | 0
Existing | CZ12 | cPVVG | Pumps | 149535.06 | 0
Existing | CZ12 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ12 | cPVVG | Humidification | 0 | 0
Existing | CZ12 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ12 | cPVVG | Water Systems | 0 | 874266.43
Existing | CZ12 | cPVVG | Refrigeration | 0 | 0
Existing | CZ12 | cPVVG | Generators | 0 | 0
Existing | CZ12 | cPVVG | Total End Uses | 11618889.5 | 2141997.74
Existing | CZ13 | cPVVG | Heating | 0 | 939631.62
Existing | CZ13 | cPVVG | Cooling | 4077762.68 | 0
Existing | CZ13 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ13 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ13 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ13 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ13 | cPVVG | Fans | 1533976.86 | 0
Existing | CZ13 | cPVVG | Pumps | 157745.41 | 0
Existing | CZ13 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ13 | cPVVG | Humidification | 0 | 0
Existing | CZ13 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ13 | cPVVG | Water Systems | 0 | 825490.68
Existing | CZ13 | cPVVG | Refrigeration | 0 | 0
Existing | CZ13 | cPVVG | Generators | 0 | 0
Existing | CZ13 | cPVVG | Total End Uses | 12595466.46 | 1914460.52
Existing | CZ14 | cPVVG | Heating | 0 | 705751.17
Existing | CZ14 | cPVVG | Cooling | 4740232.05 | 0
Existing | CZ14 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ14 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ14 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ14 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ14 | cPVVG | Fans | 1791964.72 | 0
Existing | CZ14 | cPVVG | Pumps | 158503.63 | 0
Existing | CZ14 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ14 | cPVVG | Humidification | 0 | 0
Existing | CZ14 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ14 | cPVVG | Water Systems | 0 | 783591.35
Existing | CZ14 | cPVVG | Refrigeration | 0 | 0
Existing | CZ14 | cPVVG | Generators | 0 | 0
Existing | CZ14 | cPVVG | Total End Uses | 13516681.92 | 1638680.74
Existing | CZ15 | cPVVG | Heating | 0 | 530793.57
Existing | CZ15 | cPVVG | Cooling | 6153567.98 | 0
Existing | CZ15 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ15 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ15 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ15 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ15 | cPVVG | Fans | 1887867.01 | 0
Existing | CZ15 | cPVVG | Pumps | 167048.56 | 0
Existing | CZ15 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ15 | cPVVG | Humidification | 0 | 0
Existing | CZ15 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ15 | cPVVG | Water Systems | 0 | 695501.76
Existing | CZ15 | cPVVG | Refrigeration | 0 | 0
Existing | CZ15 | cPVVG | Generators | 0 | 0
Existing | CZ15 | cPVVG | Total End Uses | 15034465.07 | 1375633.55
Existing | CZ16 | cPVVG | Heating | 0 | 1606429.18
Existing | CZ16 | cPVVG | Cooling | 3793868.87 | 0
Existing | CZ16 | cPVVG | Interior Lighting | 2929105.9 | 0
Existing | CZ16 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ16 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
Existing | CZ16 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ16 | cPVVG | Fans | 1766485.93 | 0
Existing | CZ16 | cPVVG | Pumps | 144810.54 | 0
Existing | CZ16 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ16 | cPVVG | Humidification | 0 | 0
Existing | CZ16 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ16 | cPVVG | Water Systems | 0 | 924517.83
Existing | CZ16 | cPVVG | Refrigeration | 0 | 0
Existing | CZ16 | cPVVG | Generators | 0 | 0
Existing | CZ16 | cPVVG | Total End Uses | 12531146.86 | 2680285.23
New Construction | CZ01 | cPVVG | Heating | 0 | 1029451.79
New Construction | CZ01 | cPVVG | Cooling | 324617.32 | 0
New Construction | CZ01 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ01 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ01 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ01 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ01 | cPVVG | Fans | 680197.21 | 0
New Construction | CZ01 | cPVVG | Pumps | 77961.2 | 0
New Construction | CZ01 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ01 | cPVVG | Humidification | 0 | 0
New Construction | CZ01 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ01 | cPVVG | Water Systems | 0 | 1022540.32
New Construction | CZ01 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ01 | cPVVG | Generators | 0 | 0
New Construction | CZ01 | cPVVG | Total End Uses | 7120297.08 | 2201330.33
New Construction | CZ02 | cPVVG | Heating | 0 | 1529076.46
New Construction | CZ02 | cPVVG | Cooling | 1644901.23 | 0
New Construction | CZ02 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ02 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ02 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ02 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ02 | cPVVG | Fans | 918097.49 | 0
New Construction | CZ02 | cPVVG | Pumps | 108678.16 | 0
New Construction | CZ02 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ02 | cPVVG | Humidification | 0 | 0
New Construction | CZ02 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ02 | cPVVG | Water Systems | 0 | 939757.26
New Construction | CZ02 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ02 | cPVVG | Generators | 0 | 0
New Construction | CZ02 | cPVVG | Total End Uses | 8709198.22 | 2618171.94
New Construction | CZ03 | cPVVG | Heating | 0 | 1046256.71
New Construction | CZ03 | cPVVG | Cooling | 1164874.96 | 0
New Construction | CZ03 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ03 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ03 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ03 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ03 | cPVVG | Fans | 785067.2 | 0
New Construction | CZ03 | cPVVG | Pumps | 102264.58 | 0
New Construction | CZ03 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ03 | cPVVG | Humidification | 0 | 0
New Construction | CZ03 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ03 | cPVVG | Water Systems | 0 | 936080.29
New Construction | CZ03 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ03 | cPVVG | Generators | 0 | 0
New Construction | CZ03 | cPVVG | Total End Uses | 8089728.08 | 2131675.22
New Construction | CZ04 | cPVVG | Heating | 0 | 983107.4
New Construction | CZ04 | cPVVG | Cooling | 1875279.45 | 0
New Construction | CZ04 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ04 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ04 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ04 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ04 | cPVVG | Fans | 963766.57 | 0
New Construction | CZ04 | cPVVG | Pumps | 115056.57 | 0
New Construction | CZ04 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ04 | cPVVG | Humidification | 0 | 0
New Construction | CZ04 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ04 | cPVVG | Water Systems | 0 | 903918.59
New Construction | CZ04 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ04 | cPVVG | Generators | 0 | 0
New Construction | CZ04 | cPVVG | Total End Uses | 8991623.95 | 2036364.2
New Construction | CZ05 | cPVVG | Heating | 0 | 1080997.67
New Construction | CZ05 | cPVVG | Cooling | 1349885.63 | 0
New Construction | CZ05 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ05 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ05 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ05 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ05 | cPVVG | Fans | 842577.73 | 0
New Construction | CZ05 | cPVVG | Pumps | 98332.8 | 0
New Construction | CZ05 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ05 | cPVVG | Humidification | 0 | 0
New Construction | CZ05 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ05 | cPVVG | Water Systems | 0 | 936183.81
New Construction | CZ05 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ05 | cPVVG | Generators | 0 | 0
New Construction | CZ05 | cPVVG | Total End Uses | 8328317.5 | 2166519.7
New Construction | CZ06 | cPVVG | Heating | 0 | 374243.38
New Construction | CZ06 | cPVVG | Cooling | 2151927.39 | 0
New Construction | CZ06 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ06 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ06 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ06 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ06 | cPVVG | Fans | 923617.11 | 0
New Construction | CZ06 | cPVVG | Pumps | 109979.58 | 0
New Construction | CZ06 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ06 | cPVVG | Humidification | 0 | 0
New Construction | CZ06 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ06 | cPVVG | Water Systems | 0 | 862252.29
New Construction | CZ06 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ06 | cPVVG | Generators | 0 | 0
New Construction | CZ06 | cPVVG | Total End Uses | 9223045.42 | 1385833.88
New Construction | CZ07 | cPVVG | Heating | 0 | 352249.96
New Construction | CZ07 | cPVVG | Cooling | 2342123.8 | 0
New Construction | CZ07 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ07 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ07 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ07 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ07 | cPVVG | Fans | 940749.2 | 0
New Construction | CZ07 | cPVVG | Pumps | 114792.58 | 0
New Construction | CZ07 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ07 | cPVVG | Humidification | 0 | 0
New Construction | CZ07 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ07 | cPVVG | Water Systems | 0 | 851229.58
New Construction | CZ07 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ07 | cPVVG | Generators | 0 | 0
New Construction | CZ07 | cPVVG | Total End Uses | 9435186.93 | 1352817.76
New Construction | CZ08 | cPVVG | Heating | 0 | 518015.37
New Construction | CZ08 | cPVVG | Cooling | 2641299.27 | 0
New Construction | CZ08 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ08 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ08 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ08 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ08 | cPVVG | Fans | 1053236.55 | 0
New Construction | CZ08 | cPVVG | Pumps | 123850.98 | 0
New Construction | CZ08 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ08 | cPVVG | Humidification | 0 | 0
New Construction | CZ08 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ08 | cPVVG | Water Systems | 0 | 850000.61
New Construction | CZ08 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ08 | cPVVG | Generators | 0 | 0
New Construction | CZ08 | cPVVG | Total End Uses | 9855908.15 | 1517354.2
New Construction | CZ09 | cPVVG | Heating | 0 | 489649.95
New Construction | CZ09 | cPVVG | Cooling | 2915588.75 | 0
New Construction | CZ09 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ09 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ09 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ09 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ09 | cPVVG | Fans | 1166462.98 | 0
New Construction | CZ09 | cPVVG | Pumps | 127150.9 | 0
New Construction | CZ09 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ09 | cPVVG | Humidification | 0 | 0
New Construction | CZ09 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ09 | cPVVG | Water Systems | 0 | 838328.99
New Construction | CZ09 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ09 | cPVVG | Generators | 0 | 0
New Construction | CZ09 | cPVVG | Total End Uses | 10246723.97 | 1477317.15
New Construction | CZ10 | cPVVG | Heating | 0 | 847122.28
New Construction | CZ10 | cPVVG | Cooling | 3361606.02 | 0
New Construction | CZ10 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ10 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ10 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ10 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ10 | cPVVG | Fans | 1307107.32 | 0
New Construction | CZ10 | cPVVG | Pumps | 136253.5 | 0
New Construction | CZ10 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ10 | cPVVG | Humidification | 0 | 0
New Construction | CZ10 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ10 | cPVVG | Water Systems | 0 | 831494.21
New Construction | CZ10 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ10 | cPVVG | Generators | 0 | 0
New Construction | CZ10 | cPVVG | Total End Uses | 10842488.19 | 1827954.7
New Construction | CZ11 | cPVVG | Heating | 0 | 773099.77
New Construction | CZ11 | cPVVG | Cooling | 2965167.6 | 0
New Construction | CZ11 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ11 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ11 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ11 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ11 | cPVVG | Fans | 1144983.18 | 0
New Construction | CZ11 | cPVVG | Pumps | 126172.78 | 0
New Construction | CZ11 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ11 | cPVVG | Humidification | 0 | 0
New Construction | CZ11 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ11 | cPVVG | Water Systems | 0 | 849867.49
New Construction | CZ11 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ11 | cPVVG | Generators | 0 | 0
New Construction | CZ11 | cPVVG | Total End Uses | 10273844.91 | 1772305.48
New Construction | CZ12 | cPVVG | Heating | 0 | 803704.83
New Construction | CZ12 | cPVVG | Cooling | 2641419.46 | 0
New Construction | CZ12 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ12 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ12 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ12 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ12 | cPVVG | Fans | 1065201.4 | 0
New Construction | CZ12 | cPVVG | Pumps | 125740.05 | 0
New Construction | CZ12 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ12 | cPVVG | Humidification | 0 | 0
New Construction | CZ12 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ12 | cPVVG | Water Systems | 0 | 873854.35
New Construction | CZ12 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ12 | cPVVG | Generators | 0 | 0
New Construction | CZ12 | cPVVG | Total End Uses | 9869882.26 | 1826897.4
New Construction | CZ13 | cPVVG | Heating | 0 | 646187.03
New Construction | CZ13 | cPVVG | Cooling | 3252370.47 | 0
New Construction | CZ13 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ13 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ13 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ13 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ13 | cPVVG | Fans | 1185812.05 | 0
New Construction | CZ13 | cPVVG | Pumps | 131455.64 | 0
New Construction | CZ13 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ13 | cPVVG | Humidification | 0 | 0
New Construction | CZ13 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ13 | cPVVG | Water Systems | 0 | 825070.88
New Construction | CZ13 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ13 | cPVVG | Generators | 0 | 0
New Construction | CZ13 | cPVVG | Total End Uses | 10607159.5 | 1620596.12
New Construction | CZ14 | cPVVG | Heating | 0 | 529026.59
New Construction | CZ14 | cPVVG | Cooling | 3805842.74 | 0
New Construction | CZ14 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ14 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ14 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ14 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ14 | cPVVG | Fans | 1376475.59 | 0
New Construction | CZ14 | cPVVG | Pumps | 131337.71 | 0
New Construction | CZ14 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ14 | cPVVG | Humidification | 0 | 0
New Construction | CZ14 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ14 | cPVVG | Water Systems | 0 | 783046.43
New Construction | CZ14 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ14 | cPVVG | Generators | 0 | 0
New Construction | CZ14 | cPVVG | Total End Uses | 11351177.38 | 1461411.23
New Construction | CZ15 | cPVVG | Heating | 0 | 441814.58
New Construction | CZ15 | cPVVG | Cooling | 4989187.38 | 0
New Construction | CZ15 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ15 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ15 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ15 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ15 | cPVVG | Fans | 1441291.67 | 0
New Construction | CZ15 | cPVVG | Pumps | 138771.58 | 0
New Construction | CZ15 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ15 | cPVVG | Humidification | 0 | 0
New Construction | CZ15 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ15 | cPVVG | Water Systems | 0 | 694964.45
New Construction | CZ15 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ15 | cPVVG | Generators | 0 | 0
New Construction | CZ15 | cPVVG | Total End Uses | 12606771.97 | 1286117.25
New Construction | CZ16 | cPVVG | Heating | 0 | 1101646.03
New Construction | CZ16 | cPVVG | Cooling | 2998857.23 | 0
New Construction | CZ16 | cPVVG | Interior Lighting | 2140645.73 | 0
New Construction | CZ16 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ16 | cPVVG | Interior Equipment | 3896875.61 | 149338.22
New Construction | CZ16 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ16 | cPVVG | Fans | 1366757.71 | 0
New Construction | CZ16 | cPVVG | Pumps | 119139.22 | 0
New Construction | CZ16 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ16 | cPVVG | Humidification | 0 | 0
New Construction | CZ16 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ16 | cPVVG | Water Systems | 0 | 924152.07
New Construction | CZ16 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ16 | cPVVG | Generators | 0 | 0
New Construction | CZ16 | cPVVG | Total End Uses | 10522275.51 | 2175136.32

## PV
PV - Health/Medical - Hospital (NA)

## EV Charger
EV Charger - Health/Medical - Hospital (NA)

## Raw_building (hidden)
Building Type | Building Category | Roof Type | Window Wall Ratio (%)
Health/Medical - Hospital | Nonresidential | Flat Roof | 10.02

## Raw_windowdimensionsillheight (hidden)
Window Name | Width [ft] | Height [ft] | Sill Height [ft]
B7340A | 6.89 | 5.25 | 2.99
D15667 | 26.12 | 5.22 | 2.99
7EB99B | 6.86 | 5.22 | 2.99
1CD46F | 19.59 | 5.22 | 2.99
69F01B | 19.59 | 5.22 | 2.99
819053 | 64.5 | 5.25 | 2.99
833CE1 | 6.86 | 5.22 | 2.99
FC8CF2 | 6.89 | 5.25 | 2.99
B69C36 | 65.81 | 5.25 | 2.99
10D7F1 | 65.81 | 5.22 | 2.99
4E79CD | 26.05 | 5.25 | 2.99
8B3482 | 26.05 | 5.25 | 2.99
6D2F92 | 6.89 | 5.25 | 2.99
60D3FB | 64.57 | 5.25 | 2.99
49A8C1 | 6.86 | 5.25 | 2.99
393249 | 64.5 | 5.25 | 2.99
15FB16 | 6.89 | 5.25 | 2.99
6800FE | 6.86 | 5.25 | 2.99
3E09AC | 57.09 | 5.25 | 2.99
C9D167 | 57.09 | 5.25 | 2.99
D8047F | 39.6 | 5.25 | 2.99
6B8CF6 | 39.6 | 5.25 | 2.99
E8E45C | 64.57 | 5.25 | 2.99
B49C08 | 6.86 | 5.25 | 2.99
28A73C | 6.89 | 5.25 | 2.99
2A6292 | 16.96 | 5.25 | 2.99
D512F8 | 17.85 | 5.22 | 2.99
B51BE0 | 6.89 | 5.25 | 2.99
7E0A49 | 64.5 | 5.25 | 2.99
74E10E | 6.86 | 5.25 | 2.99
9A0AE0 | 43.5 | 5.25 | 2.99
3F51A9 | 43.5 | 5.25 | 2.99

## Raw_shadinggeometry (hidden)
Shading Name | Width [ft] | Length [ft]
No Shading

## Raw_zonesummary (hidden)
Vintage | Space | Zone Name | Conditioned | Area (Excluding Plenums and CrawlSpace) (ft2) | Area (Including Plenums and CrawlSpace) (ft2) | Width (ft) | Length (ft) | Volume (ft3) | Multipliers | People (Persons/1000 ft2) | Lighting (Btu/h-ft2) | Plug Loads (Btu/h-ft2) | Outdoor Air Flow per Person (cfm/person) | Outdoor Air Flow per Zone Floor Area (cfm/ft2) | Zone Type | HVAC System Identifier | Schedule Identifier | Height (ft)
Existing | DINING EL1 NORTH PERIM (G.N1) | DINING EL1 NORTH PERIM (G.N1) | Yes | 2362.68 | 2362.68 | 25.1 | 94.13 | 30697.7 | 1 | 33.33 | 4.1409 | 2.5588 | 0.0 | 0.5 | Dining_fast | Main | Office | 12.9927
Existing | DINING EL1 SOUTH PERIM (G.S2) | DINING EL1 SOUTH PERIM (G.S2) | Yes | 1759.04 | 1759.04 | 25.1 | 70.08 | 22854.75 | 1 | 33.33 | 4.1409 | 2.5588 | 0.0 | 0.5 | Dining_fast | Main | Office | 12.9927
Existing | EL2 CORE PLNM ZN (G.C14) | EL2 CORE PLNM ZN (G.C14) | No | 0 | 44658.95 | 240.39 | 185.76 | 133338.68 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL2 EAST PERIM PLNM ZN (G.E8) | EL2 EAST PERIM PLNM ZN (G.E8) | No | 0 | 5916.16 | 25.1 | 235.7 | 17663.95 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL2 NNW PERIM PLNM ZN (G.NNW10) | EL2 NNW PERIM PLNM ZN (G.NNW10) | No | 0 | 1572.07 | 62.96 | 24.97 | 4693.75 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL2 NORTH PERIM PLNM ZN (G.N13) | EL2 NORTH PERIM PLNM ZN (G.N13) | No | 0 | 6002.38 | 240.39 | 24.97 | 17921.36 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL2 SSW PERIM PLNM ZN (G.SSW9) | EL2 SSW PERIM PLNM ZN (G.SSW9) | No | 0 | 1572.07 | 62.96 | 24.97 | 4693.75 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL2 SOUTH PERIM PLNM ZN (G.S12) | EL2 SOUTH PERIM PLNM ZN (G.S12) | No | 0 | 6002.38 | 240.39 | 24.97 | 17921.36 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL2 WEST PERIM PLNM ZN (G.W11) | EL2 WEST PERIM PLNM ZN (G.W11) | No | 0 | 11696.54 | 62.96 | 185.76 | 34922.47 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL3 CORE PLNM ZN (G.C16) | EL3 CORE PLNM ZN (G.C16) | No | 0 | 17669.76 | 95.11 | 185.76 | 52756.77 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL3 CORE PLNM ZN (G.C16) ZN | EL3 CORE PLNM ZN (G.C16) ZN | No | 0 | 38685.73 | 208.23 | 185.76 | 115504.38 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL3 EAST PERIM PLNM ZN (G.E9) | EL3 EAST PERIM PLNM ZN (G.E9) | No | 0 | 5916.16 | 25.1 | 235.7 | 17663.95 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL3 NORTH PERIM PLNM ZN (G.N11) | EL3 NORTH PERIM PLNM ZN (G.N11) | No | 0 | 2374.9 | 95.11 | 24.97 | 7090.76 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL3 NORTH PERIM PLNM ZN (G.N14) | EL3 NORTH PERIM PLNM ZN (G.N14) | No | 0 | 5199.55 | 208.23 | 24.97 | 15524.34 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL3 SOUTH PERIM PLNM ZN (G.S12) | EL3 SOUTH PERIM PLNM ZN (G.S12) | No | 0 | 2374.9 | 95.11 | 24.97 | 7090.76 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL3 SOUTH PERIM PLNM ZN (G.S15) | EL3 SOUTH PERIM PLNM ZN (G.S15) | No | 0 | 5199.55 | 208.23 | 24.97 | 15524.34 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL3 WEST PERIM PLNM ZN (G.W10) | EL3 WEST PERIM PLNM ZN (G.W10) | No | 0 | 5916.16 | 25.1 | 235.7 | 17663.95 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL4 CORE PLNM ZN (G.C13) | EL4 CORE PLNM ZN (G.C13) | No | 0 | 26861.2 | 144.59 | 185.76 | 80199.75 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL4 CORE PLNM ZN (G.C16) | EL4 CORE PLNM ZN (G.C16) | No | 0 | 29494.29 | 158.76 | 185.76 | 88061.4 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL4 EAST PERIM PLNM ZN (G.E9) | EL4 EAST PERIM PLNM ZN (G.E9) | No | 0 | 5916.16 | 25.1 | 235.7 | 17663.95 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL4 NORTH PERIM PLNM ZN (G.N11) | EL4 NORTH PERIM PLNM ZN (G.N11) | No | 0 | 3610.27 | 144.59 | 24.97 | 10779.23 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL4 NORTH PERIM PLNM ZN (G.N14) | EL4 NORTH PERIM PLNM ZN (G.N14) | No | 0 | 3964.17 | 158.76 | 24.97 | 11835.87 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL4 SOUTH PERIM PLNM ZN (G.S12) | EL4 SOUTH PERIM PLNM ZN (G.S12) | No | 0 | 3610.27 | 144.59 | 24.97 | 10779.23 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL4 SOUTH PERIM PLNM ZN (G.S15) | EL4 SOUTH PERIM PLNM ZN (G.S15) | No | 0 | 3964.17 | 158.76 | 24.97 | 11835.87 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | EL4 WEST PERIM PLNM ZN (G.W10) | EL4 WEST PERIM PLNM ZN (G.W10) | No | 0 | 5916.16 | 25.1 | 235.7 | 17663.95 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
Existing | KITCHEN EL1 WEST PERIM (G.W3) | KITCHEN EL1 WEST PERIM (G.W3) | Yes | 1794.45 | 1794.45 | 25.1 | 71.49 | 23314.85 | 1 | 2.5 | 5.6273 | 26.4716 | 0.0 | 0.15 | Kitchen | Customized | Kitchen | 12.9928
Existing | OFFICE EL2 CORE (G.C7) | OFFICE EL2 CORE (G.C7) | Yes | 44658.95 | 44658.95 | 240.39 | 185.76 | 446904.36 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 10.0071
Existing | OFFICE EL2 EAST PERIM (G.E1) | OFFICE EL2 EAST PERIM (G.E1) | Yes | 5916.16 | 5916.16 | 25.1 | 235.7 | 59203.35 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 10.0071
Existing | OFFICE EL2 NORTH PERIM (G.N6) | OFFICE EL2 NORTH PERIM (G.N6) | Yes | 6002.38 | 6002.38 | 240.39 | 24.97 | 60066.09 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 10.007
Existing | OFFICE EL2 SOUTH PERIM (G.S5) | OFFICE EL2 SOUTH PERIM (G.S5) | Yes | 6002.38 | 6002.38 | 240.39 | 24.97 | 60066.09 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 10.007
Existing | OFFICE EL3 CORE (G.C5) | OFFICE EL3 CORE (G.C5) | Yes | 17669.76 | 17669.76 | 95.11 | 185.76 | 176822.13 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Alternative | Health | 10.007
Existing | OFFICE EL3 NORTH PERIM (G.N3) | OFFICE EL3 NORTH PERIM (G.N3) | Yes | 2374.9 | 2374.9 | 95.11 | 24.97 | 23765.74 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Alternative | Health | 10.007
Existing | OFFICE EL3 SOUTH PERIM (G.S4) | OFFICE EL3 SOUTH PERIM (G.S4) | Yes | 2374.9 | 2374.9 | 95.11 | 24.97 | 23765.74 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Alternative | Health | 10.007
Existing | OFFICE EL3 WEST PERIM (G.W2) | OFFICE EL3 WEST PERIM (G.W2) | Yes | 5916.16 | 5916.16 | 25.1 | 235.7 | 59203.35 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Alternative | Health | 10.0071
Existing | PATIENTROOM EL3 CORE (G.C8) | PATIENTROOM EL3 CORE (G.C8) | Yes | 38685.73 | 38685.73 | 208.23 | 185.76 | 387130.06 | 1 | 5 | 4.4427 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.0071
Existing | PATIENTROOM EL3 EAST PERIM (G.E1) | PATIENTROOM EL3 EAST PERIM (G.E1) | Yes | 5916.16 | 5916.16 | 25.1 | 235.7 | 59203.35 | 1 | 5 | 4.4427 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.0071
Existing | PATIENTROOM EL3 NORTH PERIM (G.N6) | PATIENTROOM EL3 NORTH PERIM (G.N6) | Yes | 5199.55 | 5199.55 | 208.23 | 24.97 | 52032.14 | 1 | 5 | 4.4427 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.007
Existing | PATIENTROOM EL3 SOUTH PERIM (G.S7) | PATIENTROOM EL3 SOUTH PERIM (G.S7) | Yes | 5199.55 | 5199.55 | 208.23 | 24.97 | 52032.14 | 1 | 5 | 4.4427 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.007
Existing | PATIENTROOM EL4 CORE (G.C5) | PATIENTROOM EL4 CORE (G.C5) | Yes | 26861.2 | 26861.2 | 144.59 | 185.76 | 268801.35 | 1 | 5 | 4.4427 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.007
Existing | PATIENTROOM EL4 NORTH PERIM (G.N3) | PATIENTROOM EL4 NORTH PERIM (G.N3) | Yes | 3610.27 | 3610.27 | 144.59 | 24.97 | 36128.19 | 1 | 5 | 4.4427 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.0071
Existing | PATIENTROOM EL4 SOUTH PERIM (G.S4) | PATIENTROOM EL4 SOUTH PERIM (G.S4) | Yes | 3610.27 | 3610.27 | 144.59 | 24.97 | 36128.19 | 1 | 5 | 4.4427 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.0071
Existing | PATIENTROOM EL4 WEST PERIM (G.W2) | PATIENTROOM EL4 WEST PERIM (G.W2) | Yes | 5916.16 | 5916.16 | 25.1 | 235.7 | 59203.35 | 1 | 5 | 4.4427 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.0071
Existing | SURGERY EL2 NNW PERIM (G.NNW3) | SURGERY EL2 NNW PERIM (G.NNW3) | Yes | 1572.07 | 1572.07 | 62.96 | 24.97 | 15731.79 | 1 | 5 | 4.5778 | 5.1175 | 0.0 | 0.15 | Health_operating | Main | Office | 10.0071
Existing | SURGERY EL2 SSW PERIM (G.SSW2) | SURGERY EL2 SSW PERIM (G.SSW2) | Yes | 1572.07 | 1572.07 | 62.96 | 24.97 | 15731.79 | 1 | 5 | 4.5778 | 5.1175 | 0.0 | 0.15 | Health_operating | Main | Office | 10.0071
Existing | SURGERY EL2 WEST PERIM (G.W4) | SURGERY EL2 WEST PERIM (G.W4) | Yes | 11696.54 | 11696.54 | 62.96 | 185.76 | 117047.83 | 1 | 5 | 4.5778 | 5.1175 | 0.0 | 0.15 | Health_operating | Main | Office | 10.007
Existing | SURGERY EL4 CORE (G.C8) | SURGERY EL4 CORE (G.C8) | Yes | 29494.29 | 29494.29 | 158.76 | 185.76 | 295150.84 | 1 | 5 | 4.5778 | 5.1175 | 0.0 | 0.15 | Health_operating | Alternative | Health | 10.0071
Existing | SURGERY EL4 EAST PERIM (G.E1) | SURGERY EL4 EAST PERIM (G.E1) | Yes | 5916.16 | 5916.16 | 25.1 | 235.7 | 59203.35 | 1 | 5 | 4.5778 | 5.1175 | 0.0 | 0.15 | Health_operating | Alternative | Health | 10.0071
Existing | SURGERY EL4 NORTH PERIM (G.N6) | SURGERY EL4 NORTH PERIM (G.N6) | Yes | 3964.17 | 3964.17 | 158.76 | 24.97 | 39669.69 | 1 | 5 | 4.5778 | 5.1175 | 0.0 | 0.15 | Health_operating | Alternative | Health | 10.0071
Existing | SURGERY EL4 SOUTH PERIM (G.S7) | SURGERY EL4 SOUTH PERIM (G.S7) | Yes | 3964.17 | 3964.17 | 158.76 | 24.97 | 39669.69 | 1 | 5 | 4.5778 | 5.1175 | 0.0 | 0.15 | Health_operating | Alternative | Health | 10.0071
New Construction | DINING EL1 NORTH PERIM (G.N1) | DINING EL1 NORTH PERIM (G.N1) | Yes | 2362.68 | 2362.68 | 25.1 | 94.13 | 30697.7 | 1 | 33.33 | 1.5353 | 2.5588 | 0.0 | 0.5 | Dining_fast | Main | Office | 12.9927
New Construction | DINING EL1 SOUTH PERIM (G.S2) | DINING EL1 SOUTH PERIM (G.S2) | Yes | 1759.04 | 1759.04 | 25.1 | 70.08 | 22854.75 | 1 | 33.33 | 1.5353 | 2.5588 | 0.0 | 0.5 | Dining_fast | Main | Office | 12.9927
New Construction | EL2 CORE PLNM ZN (G.C14) | EL2 CORE PLNM ZN (G.C14) | No | 0 | 44658.95 | 240.39 | 185.76 | 133338.68 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL2 EAST PERIM PLNM ZN (G.E8) | EL2 EAST PERIM PLNM ZN (G.E8) | No | 0 | 5916.16 | 25.1 | 235.7 | 17663.95 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL2 NNW PERIM PLNM ZN (G.NNW10) | EL2 NNW PERIM PLNM ZN (G.NNW10) | No | 0 | 1572.07 | 62.96 | 24.97 | 4693.75 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL2 NORTH PERIM PLNM ZN (G.N13) | EL2 NORTH PERIM PLNM ZN (G.N13) | No | 0 | 6002.38 | 240.39 | 24.97 | 17921.36 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL2 SSW PERIM PLNM ZN (G.SSW9) | EL2 SSW PERIM PLNM ZN (G.SSW9) | No | 0 | 1572.07 | 62.96 | 24.97 | 4693.75 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL2 SOUTH PERIM PLNM ZN (G.S12) | EL2 SOUTH PERIM PLNM ZN (G.S12) | No | 0 | 6002.38 | 240.39 | 24.97 | 17921.36 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL2 WEST PERIM PLNM ZN (G.W11) | EL2 WEST PERIM PLNM ZN (G.W11) | No | 0 | 11696.54 | 62.96 | 185.76 | 34922.47 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL3 CORE PLNM ZN (G.C16) | EL3 CORE PLNM ZN (G.C16) | No | 0 | 17669.76 | 95.11 | 185.76 | 52756.77 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL3 CORE PLNM ZN (G.C16) ZN | EL3 CORE PLNM ZN (G.C16) ZN | No | 0 | 38685.73 | 208.23 | 185.76 | 115504.38 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL3 EAST PERIM PLNM ZN (G.E9) | EL3 EAST PERIM PLNM ZN (G.E9) | No | 0 | 5916.16 | 25.1 | 235.7 | 17663.95 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL3 NORTH PERIM PLNM ZN (G.N11) | EL3 NORTH PERIM PLNM ZN (G.N11) | No | 0 | 2374.9 | 95.11 | 24.97 | 7090.76 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL3 NORTH PERIM PLNM ZN (G.N14) | EL3 NORTH PERIM PLNM ZN (G.N14) | No | 0 | 5199.55 | 208.23 | 24.97 | 15524.34 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL3 SOUTH PERIM PLNM ZN (G.S12) | EL3 SOUTH PERIM PLNM ZN (G.S12) | No | 0 | 2374.9 | 95.11 | 24.97 | 7090.76 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL3 SOUTH PERIM PLNM ZN (G.S15) | EL3 SOUTH PERIM PLNM ZN (G.S15) | No | 0 | 5199.55 | 208.23 | 24.97 | 15524.34 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL3 WEST PERIM PLNM ZN (G.W10) | EL3 WEST PERIM PLNM ZN (G.W10) | No | 0 | 5916.16 | 25.1 | 235.7 | 17663.95 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL4 CORE PLNM ZN (G.C13) | EL4 CORE PLNM ZN (G.C13) | No | 0 | 26861.2 | 144.59 | 185.76 | 80199.75 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL4 CORE PLNM ZN (G.C16) | EL4 CORE PLNM ZN (G.C16) | No | 0 | 29494.29 | 158.76 | 185.76 | 88061.4 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL4 EAST PERIM PLNM ZN (G.E9) | EL4 EAST PERIM PLNM ZN (G.E9) | No | 0 | 5916.16 | 25.1 | 235.7 | 17663.95 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL4 NORTH PERIM PLNM ZN (G.N11) | EL4 NORTH PERIM PLNM ZN (G.N11) | No | 0 | 3610.27 | 144.59 | 24.97 | 10779.23 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL4 NORTH PERIM PLNM ZN (G.N14) | EL4 NORTH PERIM PLNM ZN (G.N14) | No | 0 | 3964.17 | 158.76 | 24.97 | 11835.87 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL4 SOUTH PERIM PLNM ZN (G.S12) | EL4 SOUTH PERIM PLNM ZN (G.S12) | No | 0 | 3610.27 | 144.59 | 24.97 | 10779.23 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL4 SOUTH PERIM PLNM ZN (G.S15) | EL4 SOUTH PERIM PLNM ZN (G.S15) | No | 0 | 3964.17 | 158.76 | 24.97 | 11835.87 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | EL4 WEST PERIM PLNM ZN (G.W10) | EL4 WEST PERIM PLNM ZN (G.W10) | No | 0 | 5916.16 | 25.1 | 235.7 | 17663.95 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 2.9857
New Construction | KITCHEN EL1 WEST PERIM (G.W3) | KITCHEN EL1 WEST PERIM (G.W3) | Yes | 1794.45 | 1794.45 | 25.1 | 71.49 | 23314.85 | 1 | 2.5 | 3.2411 | 26.4716 | 0.0 | 0.15 | Kitchen | Customized | Kitchen | 12.9928
New Construction | OFFICE EL2 CORE (G.C7) | OFFICE EL2 CORE (G.C7) | Yes | 44658.95 | 44658.95 | 240.39 | 185.76 | 446904.36 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 10.0071
New Construction | OFFICE EL2 EAST PERIM (G.E1) | OFFICE EL2 EAST PERIM (G.E1) | Yes | 5916.16 | 5916.16 | 25.1 | 235.7 | 59203.35 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 10.0071
New Construction | OFFICE EL2 NORTH PERIM (G.N6) | OFFICE EL2 NORTH PERIM (G.N6) | Yes | 6002.38 | 6002.38 | 240.39 | 24.97 | 60066.09 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 10.007
New Construction | OFFICE EL2 SOUTH PERIM (G.S5) | OFFICE EL2 SOUTH PERIM (G.S5) | Yes | 6002.38 | 6002.38 | 240.39 | 24.97 | 60066.09 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 10.007
New Construction | OFFICE EL3 CORE (G.C5) | OFFICE EL3 CORE (G.C5) | Yes | 17669.76 | 17669.76 | 95.11 | 185.76 | 176822.13 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Alternative | Health | 10.007
New Construction | OFFICE EL3 NORTH PERIM (G.N3) | OFFICE EL3 NORTH PERIM (G.N3) | Yes | 2374.9 | 2374.9 | 95.11 | 24.97 | 23765.74 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Alternative | Health | 10.007
New Construction | OFFICE EL3 SOUTH PERIM (G.S4) | OFFICE EL3 SOUTH PERIM (G.S4) | Yes | 2374.9 | 2374.9 | 95.11 | 24.97 | 23765.74 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Alternative | Health | 10.007
New Construction | OFFICE EL3 WEST PERIM (G.W2) | OFFICE EL3 WEST PERIM (G.W2) | Yes | 5916.16 | 5916.16 | 25.1 | 235.7 | 59203.35 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Alternative | Health | 10.0071
New Construction | PATIENTROOM EL3 CORE (G.C8) | PATIENTROOM EL3 CORE (G.C8) | Yes | 38685.73 | 38685.73 | 208.23 | 185.76 | 387130.06 | 1 | 5 | 2.3882 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.0071
New Construction | PATIENTROOM EL3 EAST PERIM (G.E1) | PATIENTROOM EL3 EAST PERIM (G.E1) | Yes | 5916.16 | 5916.16 | 25.1 | 235.7 | 59203.35 | 1 | 5 | 2.3882 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.0071
New Construction | PATIENTROOM EL3 NORTH PERIM (G.N6) | PATIENTROOM EL3 NORTH PERIM (G.N6) | Yes | 5199.55 | 5199.55 | 208.23 | 24.97 | 52032.14 | 1 | 5 | 2.3882 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.007
New Construction | PATIENTROOM EL3 SOUTH PERIM (G.S7) | PATIENTROOM EL3 SOUTH PERIM (G.S7) | Yes | 5199.55 | 5199.55 | 208.23 | 24.97 | 52032.14 | 1 | 5 | 2.3882 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.007
New Construction | PATIENTROOM EL4 CORE (G.C5) | PATIENTROOM EL4 CORE (G.C5) | Yes | 26861.2 | 26861.2 | 144.59 | 185.76 | 268801.35 | 1 | 5 | 2.3882 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.007
New Construction | PATIENTROOM EL4 NORTH PERIM (G.N3) | PATIENTROOM EL4 NORTH PERIM (G.N3) | Yes | 3610.27 | 3610.27 | 144.59 | 24.97 | 36128.19 | 1 | 5 | 2.3882 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.0071
New Construction | PATIENTROOM EL4 SOUTH PERIM (G.S4) | PATIENTROOM EL4 SOUTH PERIM (G.S4) | Yes | 3610.27 | 3610.27 | 144.59 | 24.97 | 36128.19 | 1 | 5 | 2.3882 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.0071
New Construction | PATIENTROOM EL4 WEST PERIM (G.W2) | PATIENTROOM EL4 WEST PERIM (G.W2) | Yes | 5916.16 | 5916.16 | 25.1 | 235.7 | 59203.35 | 1 | 5 | 2.3882 | 5.1175 | 0.0 | 0.15 | Health_patient | Alternative | Health | 10.0071
New Construction | SURGERY EL2 NNW PERIM (G.NNW3) | SURGERY EL2 NNW PERIM (G.NNW3) | Yes | 1572.07 | 1572.07 | 62.96 | 24.97 | 15731.79 | 1 | 5 | 6.4822 | 5.1175 | 0.0 | 0.15 | Health_operating | Main | Office | 10.0071
New Construction | SURGERY EL2 SSW PERIM (G.SSW2) | SURGERY EL2 SSW PERIM (G.SSW2) | Yes | 1572.07 | 1572.07 | 62.96 | 24.97 | 15731.79 | 1 | 5 | 6.4822 | 5.1175 | 0.0 | 0.15 | Health_operating | Main | Office | 10.0071
New Construction | SURGERY EL2 WEST PERIM (G.W4) | SURGERY EL2 WEST PERIM (G.W4) | Yes | 11696.54 | 11696.54 | 62.96 | 185.76 | 117047.83 | 1 | 5 | 6.4822 | 5.1175 | 0.0 | 0.15 | Health_operating | Main | Office | 10.007
New Construction | SURGERY EL4 CORE (G.C8) | SURGERY EL4 CORE (G.C8) | Yes | 29494.29 | 29494.29 | 158.76 | 185.76 | 295150.84 | 1 | 5 | 6.4822 | 5.1175 | 0.0 | 0.15 | Health_operating | Alternative | Health | 10.0071
New Construction | SURGERY EL4 EAST PERIM (G.E1) | SURGERY EL4 EAST PERIM (G.E1) | Yes | 5916.16 | 5916.16 | 25.1 | 235.7 | 59203.35 | 1 | 5 | 6.4822 | 5.1175 | 0.0 | 0.15 | Health_operating | Alternative | Health | 10.0071
New Construction | SURGERY EL4 NORTH PERIM (G.N6) | SURGERY EL4 NORTH PERIM (G.N6) | Yes | 3964.17 | 3964.17 | 158.76 | 24.97 | 39669.69 | 1 | 5 | 6.4822 | 5.1175 | 0.0 | 0.15 | Health_operating | Alternative | Health | 10.0071
New Construction | SURGERY EL4 SOUTH PERIM (G.S7) | SURGERY EL4 SOUTH PERIM (G.S7) | Yes | 3964.17 | 3964.17 | 158.76 | 24.97 | 39669.69 | 1 | 5 | 6.4822 | 5.1175 | 0.0 | 0.15 | Health_operating | Alternative | Health | 10.0071