## Geometry Summary (hidden)
Abbreviation | Building Type | Shape | Number of Floors | Aspect Ratio | Zone Height_1 | Zone Height_2 | Zone Height_3 | Plenum Height | Floor to Floor Height (feet) | Floor to Ceiling Height (feet)
Asm | Assembly | #VALUE! | 1 | 1 | 12.0006 | na | na | 3.0001 | 12.0006 | 15.0007
ECC | Education - Community College | #VALUE! | 3 | 5.7 | 9.0004 | 13.0006 | na | 4.0002 | 9 / 13 | 13 / 17
EPr | Education - Primary School | #VALUE! | 1 | 2 | 9.0004 | 12.0006 | na | 3.0001 | 9 / 12 | 12 / 15
ERC | Education - Relocatable Classroom | #VALUE! | 1 | 1.7 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
ESe | Education - Secondary School | #VALUE! | 2 | 2.5/1.0 | 9.0004 | 13.0006 | na | 4.0002 | 9 / 13 | 13 / 17
EUn | Education - University | #VALUE! | 4 | 2.0/15.0 | 10.0005 | 9.0004 | 14.0007 | 4.0002 | 9 / 10 / 14 | 13 / 14 / 18
Fin | Financial buildings, incl. banks | #VALUE! | 1 | 1 | 11.0005 | na | na | na | 11.0005 | 11.0005
Gro | Grocery | #VALUE! | 1 | 1 | 25.0012 | na | na | na | 25.0012 | 25.0012
Hsp | Health/Medical - Hospital | #VALUE! | 3 | 1 | 10.007 | 12.9927 | na | 2.9857 | 10 / 13 | 13 / 16
Htl | Lodging - Hotel | #VALUE! | 4 | 6.6 | 8.0004 | 10.5005 | na | 1.5001 | 8 / 11 | 10 / 12
Lib | Libraries | #VALUE! | 1 | 1 | 13.0006 | na | na | na | 13.0006 | 13.0006
MBT | Manufacturing Biotech | #VALUE! | 1 | 6 | 9.0004 | na | na | 6.0003 | 9.0004 | 15.0008
MLI | Manufacturing Light Industrial | #VALUE! | 1 | 1 | 35.0017 | na | na | na | 35.0017 | 35.0017
Mtl | Lodging - Motel | #VALUE! | 2 | 5.1 | 9.0004 | na | na | na | 9.0004 | 9.0004
Nrs | Health/Medical - Nursing Home | #VALUE! | 2 | 10.3 | 12.9986 | 9.0005 | na | 4.0055 | 9 / 13 | 13 / 17
OfL | Office - Large | #VALUE! | 3 | 1.5 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
OfS | Office - Small | #VALUE! | 2 | 1.5 | 9.0004 | na | na | 3.0001 | 9.0004 | 12.0006
Rel | Religious assembly buildings | #VALUE! | 1 | 2.5 | 37.5018 | 15.0007 | na | na | 38 / 15 | 38 / 15
RFF | Restaurant - Fast-Food | #VALUE! | 1 | 1 | 10.0005 | na | na | 3.0002 | 10.0005 | 13.0007
RSD | Restaurant - Sit-Down | #VALUE! | 1 | 1 | 10.0005 | na | na | 3.0001 | 10.0005 | 13.0006
Rt3 | Retail - Multistory Large | #VALUE! | 3 | 1 | 15.0007 | na | na | 5.8002 | 15.0007 | 20.8009
RtL | Retail - Single-Story Large | #VALUE! | 1 | 1 | 20.501 | na | na | na | 20.501 | 20.501
RtS | Retail - Small | #VALUE! | 1 | 1 | 10.0005 | na | na | 2.0001 | 10.0005 | 12.0006
SCn | Storage - Conditioned | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023
SUn | Storage - Unconditioned | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023
WRf | Warehouse - Refrigerated | #VALUE! | 1 | 1 | 48.0023 | na | na | na | 48.0023 | 48.0023

## Prototype
TRC, Updated Febuary 2026
Manufacturing Biotech
Characteristic | Value
Building Type | Manufacturing Biotech
Building Category | Nonresidential
Vintages | Two vintages: Existing and New Construction
Shape | #VALUE!
Total Floor Area (ft²) | 199994.23
Aspect Ratio | 6
Number of Floors | 1
Roof Type | Flat Roof
Gross Window to Wall Ratio (%) | 12
Shading Geometry | No Shading
Floor to Floor Height (feet) | 9.0004
Floor to Ceiling Height (feet) | 15.0008
Glazing Sill Height (feet) | 4.5

## Notes
Prototype Overview
Name | Description
Asm | Assembly
ECC | Education - Community College
EPr | Education - Primary School
ERC | Education - Relocatable Classroom
ESe | Education - Secondary School
EUn | Education - University
Fin | Financial buildings, incl. banks
Gro | Grocery
Hsp | Health/Medical - Hospital
Htl | Lodging - Hotel
Lib | Libraries
MBT | Manufacturing Biotech
MLI | Manufacturing Light Industrial
Mtl | Lodging - Motel
Nrs | Health/Medical - Nursing Home
OfL | Office - Large
OfS | Office - Small
Rel | Religious assembly buildings
RFF | Restaurant - Fast-Food
RSD | Restaurant - Sit-Down
Rt3 | Retail - Multistory Large
RtL | Retail - Single-Story Large
RtS | Retail - Small
SCn | Storage - Conditioned
SUn | Storage - Unconditioned
WRf | Warehouse - Refrigerated
Vintages
Existing | Weighted average of Title 24 requirements based on vintages from 1975 to 2022
New Construction | Title 24 2025
Run Begin Day
Begin Month | Begin Day of Month | Day of Week for Start Day
1 | 1 | Sunday
Special Days
Name | Start Date | Duration (days) | Special Day Type
New Years Day | January 1 | 1 | Holiday
Veterans Day | November 11 | 1 | Holiday
Christmas | December 25 | 1 | Holiday
Independence Day | July 4 | 1 | Holiday
MLK Day | 3rd Monday in January | 1 | Holiday
Presidents Day | 3rd Monday in February | 1 | Holiday
Memorial Day | Last Monday in May | 1 | Holiday
Labor Day | 1st Monday in September | 1 | Holiday
Columbus Day | 2nd Monday in October | 1 | Holiday
Thanksgiving | 4th Thursday in November | 1 | Holiday

## Raw_runbeginday (hidden)
Begin Month | Begin Day of Month | Day of Week for Start Day
1 | 1 | Sunday

## Raw_specialdays (hidden)
Name | Start Day | Duration | Special Day Type
New Years Day | January 1 | 1 | Holiday
Veterans Day | November 11 | 1 | Holiday
Christmas | December 25 | 1 | Holiday
Independence Day | July 4 | 1 | Holiday
MLK Day | 3rd Monday in January | 1 | Holiday
Presidents Day | 3rd Monday in February | 1 | Holiday
Memorial Day | Last Monday in May | 1 | Holiday
Labor Day | 1st Monday in September | 1 | Holiday
Columbus Day | 2nd Monday in October | 1 | Holiday
Thanksgiving | 4th Thursday in November | 1 | Holiday

## Climate Zone
Climate Zones - All Prototypes
Climate Zone | Representative City | Weather File Name
CZ01 | Eureka | CA_EUREKA_725940S_CZ2022.epw
CZ02 | Napa | CA_NAPA-CO_724955S_CZ2022.epw
CZ03 | Oakland | CA_OAKLAND-METRO-AP_724930S_CZ2022.epw
CZ04 | San Jose | CA_SAN-JOSE-IAP_724945S_CZ2022.epw
CZ05 | Santa Maria | CA_SANTA-MARIA-PUBLIC-AP_723940S_CZ2022.epw
CZ06 | Los Angeles | CA_LOS-ANGELES-IAP_722950S_CZ2022.epw
CZ07 | San Diego-Lindbergh | CA_SAN-DIEGO-LINDBERGH-FLD_722900S_CZ2022.epw
CZ08 | Long Beach-Daugherty | CA_LONG-BEACH-DAUGHERTY-FLD_722970S_CZ2022.epw
CZ09 | Los Angeles | CA_LOS-ANGELES-DOWNTOWN-USC_722874S_CZ2022.epw
CZ10 | Riverside | CA_RIVERSIDE-MUNI_722869S_CZ2022.epw
CZ11 | Red Bluff | CA_RED-BLUFF-MUNI-AP_725910S_CZ2022.epw
CZ12 | Stockton | CA_STOCKTON-METRO-AP_724920S_CZ2022.epw
CZ13 | Fresno Yosemite | CA_FRESNO-YOSEMITE-IAP_723890S_CZ2022.epw
CZ14 | Daggett Barstow | CA_DAGGETT-BARSTOW-AP_723815S_CZ2022.epw
CZ15 | El Centro | CA_EL-CENTRO-NAF_722810S_CZ2022.epw
CZ16 | Bishop | CA_BISHOP-AP_724800S_CZ2022.epw
Source: California Energy Commission, https://cecgis-caenergy.opendata.arcgis.com/datasets/CAEnergy::california-building-climate-zones/about

## Zones
Zone Summary - Manufacturing Biotech
Space | Zone Name | Conditioned [Y/N] | Zone Type | HVAC System Identifier (Main/Alternative/Customized) | Schedule Identifier | Area Fraction | Area (Excluding Plenums and Crawl Space) (ft²) | Volume (ft³) | Multipliers | People (Persons/1,000 ft²) | Note
COMPUTER EL1 CORE SPC (G.C8) | COMPUTER EL1 CORE SPC (G.C8) | Yes | Computer | Customized | Computer room | 1.999% | 3997.96 | 35983.42 | 1 | 1.5
CONFERENCE EL1 CORE SPC (G.C7) | CONFERENCE EL1 CORE SPC (G.C7) | Yes | Conference | Main | Office | 2% | 3999.03 | 35993.03 | 1 | 33.33
CORRIDOR EL1 CORE SPC (G.C6) | CORRIDOR EL1 CORE SPC (G.C6) | Yes | Corridor | Main | Office | 20% | 40004.04 | 360051.18 | 1 | 5
DINING EL1 CORE SPC (G.C9) | DINING EL1 CORE SPC (G.C9) | Yes | Dining_fast | Main | Office | 3% | 5998.85 | 53987.72 | 1 | 33.33
EL1 CORE PLNM (G.C16) | EL1 CORE PLNM (G.C16) | No | Plenum | - | Plenum | 0% | 0 | 544051.58 | 1 | 0
EL1 CORE PLNM (G.C17) | EL1 CORE PLNM (G.C17) | No | Plenum | - | Plenum | 0% | 0 | 240035.65 | 1 | 0
EL1 CORE PLNM (G.C18) | EL1 CORE PLNM (G.C18) | No | Plenum | - | Plenum | 0% | 0 | 23995.36 | 1 | 0
EL1 CORE PLNM (G.C19) | EL1 CORE PLNM (G.C19) | No | Plenum | - | Plenum | 0% | 0 | 23990.47 | 1 | 0
EL1 CORE PLNM (G.C20) | EL1 CORE PLNM (G.C20) | No | Plenum | - | Plenum | 0% | 0 | 35991.81 | 1 | 0
EL1 CORE PLNM (G.C21) | EL1 CORE PLNM (G.C21) | No | Plenum | - | Plenum | 0% | 0 | 11996.76 | 1 | 0
EL1 CORE PLNM (G.C22) | EL1 CORE PLNM (G.C22) | No | Plenum | - | Plenum | 0% | 0 | 95284.47 | 1 | 0
EL1 EAST PERIM PLNM (G.E13) | EL1 EAST PERIM PLNM (G.E13) | No | Plenum | - | Plenum | 0% | 0 | 15081.71 | 1 | 0
EL1 NORTH PERIM PLNM (G.N14) | EL1 NORTH PERIM PLNM (G.N14) | No | Plenum | - | Plenum | 0% | 0 | 97256.41 | 1 | 0
EL1 SOUTH PERIM PLNM (G.S12) | EL1 SOUTH PERIM PLNM (G.S12) | No | Plenum | - | Plenum | 0% | 0 | 97254.59 | 1 | 0
EL1 WEST PERIM PLNM (G.W15) | EL1 WEST PERIM PLNM (G.W15) | No | Plenum | - | Plenum | 0% | 0 | 15081.71 | 1 | 0
KITCHEN EL1 CORE SPC (G.C10) | KITCHEN EL1 CORE SPC (G.C10) | Yes | Kitchen | Customized | Kitchen | 1% | 2000.13 | 17995.14 | 1 | 2.5
LAB EL1 CORE SPC (G.C5) | LAB EL1 CORE SPC (G.C5) | Yes | Lab | Customized | lab | 45.34% | 90670.84 | 816077.38 | 1 | 5
OFFICE EL1 CORE SPC (G.C11) | OFFICE EL1 CORE SPC (G.C11) | Yes | Office | Main | Office | 7.94% | 15879.72 | 142926.71 | 1 | 5
OFFICE EL1 EAST PERIM SPC (G.E2) | OFFICE EL1 EAST PERIM SPC (G.E2) | Yes | Office | Main | Office | 1.257% | 2513.5 | 22622.56 | 1 | 5
OFFICE EL1 NORTH PERIM SPC (G.N3) | OFFICE EL1 NORTH PERIM SPC (G.N3) | Yes | Office | Main | Office | 8.104% | 16208.33 | 145887.13 | 1 | 5
OFFICE EL1 SOUTH PERIM SPC (G.S1) | OFFICE EL1 SOUTH PERIM SPC (G.S1) | Yes | Office | Main | Office | 8.104% | 16208.33 | 145881.65 | 1 | 5
OFFICE EL1 WEST PERIM SPC (G.W4) | OFFICE EL1 WEST PERIM SPC (G.W4) | Yes | Office | Main | Office | 1.257% | 2513.5 | 22622.56 | 1 | 5
Total (22 Space) | Total (22 Space) | Total (11 Conditioned zones, 11 Unconditioned Zones) |  |  |  |  | 199994.23

## Envelope
Envelope - Manufacturing Biotech
Element | Prototype | Assembly Type | Construction | Unit | Vintage | Selected T24 | Note | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
External Wall | Manufacturing Biotech | - | Stucco+Wall Continuous Insulation+Gypsum 5/8in | U-value IP | Existing | Weighted average |  | 0.185 | 0.179 | 0.185 | 0.178 | 0.178 | 0.18 | 0.174 | 0.176 | 0.176 | 0.15 | 0.171 | 0.171 | 0.168 | 0.161 | 0.153 | 0.162
External Wall | Manufacturing Biotech | - | Stucco+Wall Continuous Insulation+Gypsum 5/8in | U-value IP | New Construction | 2025 |  | 0.063 | 0.058 | 0.076 | 0.058 | 0.058 | 0.063 | 0.063 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058 | 0.058
Roof | Manufacturing Biotech | - | Roof Membrane+Roof Continuous Insulation+Metal Decking | U-value IP | Existing | Weighted average |  | 0.062 | 0.061 | 0.062 | 0.061 | 0.061 | 0.065 | 0.065 | 0.065 | 0.065 | 0.062 | 0.061 | 0.061 | 0.06 | 0.06 | 0.059 | 0.06
Roof | Manufacturing Biotech | - | Roof Membrane+Roof Continuous Insulation+Metal Decking | U-value IP | New Construction | 2025 |  | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039 | 0.039
Windows | Manufacturing Biotech | - | Theoretical Glazing | U-value IP | Existing | Weighted average |  | 1.024 | 1.078 | 1.131 | 1.108 | 1.109 | 1.115 | 1.075 | 1.114 | 1.112 | 0.875 | 0.942 | 0.94 | 0.929 | 0.886 | 0.831 | 0.885
Windows | Manufacturing Biotech | - | Theoretical Glazing | U-value IP | New Construction | 2025 |  | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.34 | 0.36 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.36
Windows | Manufacturing Biotech | - | Theoretical Glazing | SHGC | Existing | Weighted average |  | 0.70708 | 0.70715 | 0.73753 | 0.71836 | 0.75308 | 0.7254 | 0.72673 | 0.7241 | 0.72365 | 0.5734 | 0.64366 | 0.64394 | 0.6358 | 0.60724 | 0.57129 | 0.62767
Windows | Manufacturing Biotech | - | Theoretical Glazing | SHGC | New Construction | 2025 |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.22 | 0.25 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.25
Windows | Manufacturing Biotech | - | Theoretical Glazing | Visible Transmittance | Existing | Weighted average |  | 0.26089 | 0.26141 | 0.26004 | 0.26231 | 0.26223 | 0.26197 | 0.26576 | 0.26213 | 0.26228 | 0.27816 | 0.26665 | 0.26607 | 0.26793 | 0.27125 | 0.27583 | 0.27139
Windows | Manufacturing Biotech | - | Theoretical Glazing | Visible Transmittance | New Construction | 2025 |  | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42 | 0.42
Infiltration - Manufacturing Biotech
|  |  |  | Element | Unit | Vintage | Note | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
|  |  |  | Infiltration Rate | CFM/ft2 | Existing | Infiltration rate is flow rate per exterior surface area at 10 mph wind speed, modeled proportionally to wind speed. | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801
[6 empty] | New Construction |  | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801

## Raw_envelope (hidden)
Climate Zone | Vintage | Exterior Roof Layers | Roof U-Value [Btu/h-ft2-F] | Exterior Wall Layers | Wall U-Value [Btu/h-ft2-F] | Exterior Window Layers | Window U-Value [Btu/h-ft2-F] | Window SHGC | Window VT
CZ01 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.062 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.185 | Theoretical Glazing | 1.024 | 0.70708 | 0.26089
CZ02 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.179 | Theoretical Glazing | 1.078 | 0.70715 | 0.26141
CZ03 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.062 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.185 | Theoretical Glazing | 1.131 | 0.73753 | 0.26004
CZ04 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.178 | Theoretical Glazing | 1.108 | 0.71836 | 0.26231
CZ05 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.178 | Theoretical Glazing | 1.109 | 0.75308 | 0.26223
CZ06 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.18 | Theoretical Glazing | 1.115 | 0.7254 | 0.26197
CZ07 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.174 | Theoretical Glazing | 1.075 | 0.72673 | 0.26576
CZ08 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.176 | Theoretical Glazing | 1.114 | 0.7241 | 0.26213
CZ09 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.065 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.176 | Theoretical Glazing | 1.112 | 0.72365 | 0.26228
CZ10 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.062 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.15 | Theoretical Glazing | 0.875 | 0.5734 | 0.27816
CZ11 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.171 | Theoretical Glazing | 0.942 | 0.64366 | 0.26665
CZ12 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.061 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.171 | Theoretical Glazing | 0.94 | 0.64394 | 0.26607
CZ13 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.06 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.168 | Theoretical Glazing | 0.929 | 0.6358 | 0.26793
CZ14 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.06 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.161 | Theoretical Glazing | 0.886 | 0.60724 | 0.27125
CZ15 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.059 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.153 | Theoretical Glazing | 0.831 | 0.57129 | 0.27583
CZ16 | Existing | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.06 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.162 | Theoretical Glazing | 0.885 | 0.62767 | 0.27139
CZ01 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.063 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ02 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ03 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.076 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ04 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ05 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ06 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.063 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ07 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.063 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ08 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ09 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ10 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.36 | 0.25 | 0.42
CZ11 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ12 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ13 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ14 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ15 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.34 | 0.22 | 0.42
CZ16 | New Construction | Roof Membrane+Roof Continuous Insulation+Metal Decking | 0.039 | Stucco+Wall Continuous Insulation+Gypsum 5/8in | 0.058 | Theoretical Glazing | 0.36 | 0.25 | 0.42

## Raw_infiltrationcfmft (hidden)
Vintage | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
Existing | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801
New Construction | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801 | 0.044801

## Thermostat
Thermostat Setpoints - Manufacturing Biotech | [18 empty] | Zone Type
Schedule Identifier | Setpoint | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Notes | Computer room
Computer room | Heating Setpoint (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | Kitchen
Computer room | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | lab
Computer room | Cooling Setpoint (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | Office
Computer room | Cooling Setback (F) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
Kitchen | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Kitchen | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Kitchen | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Kitchen | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
lab | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
lab | Heating Setback (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
lab | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
lab | Cooling Setback (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Office | Heating Setpoint (F) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Office | Heating Setback (F) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Office | Cooling Setpoint (F) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Office | Cooling Setback (F) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85

## Raw_thermostatsetpoints (hidden)
Climate Zone | Schedule Identifier | Heating Setpoint (F) | Heating Setback (F) | Cooling Setpoint (F) | Cooling Setback (F)
CZ01 | Computer room | 60 | 60 | 80 | 80
CZ01 | Kitchen | 70 | 60 | 75 | 85
CZ01 | Office | 70 | 60 | 75 | 85
CZ01 | lab | 70 | 70 | 75 | 75
CZ02 | Computer room | 60 | 60 | 80 | 80
CZ02 | Kitchen | 70 | 60 | 75 | 85
CZ02 | Office | 70 | 60 | 75 | 85
CZ02 | lab | 70 | 70 | 75 | 75
CZ03 | Computer room | 60 | 60 | 80 | 80
CZ03 | Kitchen | 70 | 60 | 75 | 85
CZ03 | Office | 70 | 60 | 75 | 85
CZ03 | lab | 70 | 70 | 75 | 75
CZ04 | Computer room | 60 | 60 | 80 | 80
CZ04 | Kitchen | 70 | 60 | 75 | 85
CZ04 | Office | 70 | 60 | 75 | 85
CZ04 | lab | 70 | 70 | 75 | 75
CZ05 | Computer room | 60 | 60 | 80 | 80
CZ05 | Kitchen | 70 | 60 | 75 | 85
CZ05 | Office | 70 | 60 | 75 | 85
CZ05 | lab | 70 | 70 | 75 | 75
CZ06 | Computer room | 60 | 60 | 80 | 80
CZ06 | Kitchen | 70 | 60 | 75 | 85
CZ06 | Office | 70 | 60 | 75 | 85
CZ06 | lab | 70 | 70 | 75 | 75
CZ07 | Computer room | 60 | 60 | 80 | 80
CZ07 | Kitchen | 70 | 60 | 75 | 85
CZ07 | Office | 70 | 60 | 75 | 85
CZ07 | lab | 70 | 70 | 75 | 75
CZ08 | Computer room | 60 | 60 | 80 | 80
CZ08 | Kitchen | 70 | 60 | 75 | 85
CZ08 | Office | 70 | 60 | 75 | 85
CZ08 | lab | 70 | 70 | 75 | 75
CZ09 | Computer room | 60 | 60 | 80 | 80
CZ09 | Kitchen | 70 | 60 | 75 | 85
CZ09 | Office | 70 | 60 | 75 | 85
CZ09 | lab | 70 | 70 | 75 | 75
CZ10 | Computer room | 60 | 60 | 80 | 80
CZ10 | Kitchen | 70 | 60 | 75 | 85
CZ10 | Office | 70 | 60 | 75 | 85
CZ10 | lab | 70 | 70 | 75 | 75
CZ11 | Computer room | 60 | 60 | 80 | 80
CZ11 | Kitchen | 70 | 60 | 75 | 85
CZ11 | Office | 70 | 60 | 75 | 85
CZ11 | lab | 70 | 70 | 75 | 75
CZ12 | Computer room | 60 | 60 | 80 | 80
CZ12 | Kitchen | 70 | 60 | 75 | 85
CZ12 | Office | 70 | 60 | 75 | 85
CZ12 | lab | 70 | 70 | 75 | 75
CZ13 | Computer room | 60 | 60 | 80 | 80
CZ13 | Kitchen | 70 | 60 | 75 | 85
CZ13 | Office | 70 | 60 | 75 | 85
CZ13 | lab | 70 | 70 | 75 | 75
CZ14 | Computer room | 60 | 60 | 80 | 80
CZ14 | Kitchen | 70 | 60 | 75 | 85
CZ14 | Office | 70 | 60 | 75 | 85
CZ14 | lab | 70 | 70 | 75 | 75
CZ15 | Computer room | 60 | 60 | 80 | 80
CZ15 | Kitchen | 70 | 60 | 75 | 85
CZ15 | Office | 70 | 60 | 75 | 85
CZ15 | lab | 70 | 70 | 75 | 75
CZ16 | Computer room | 60 | 60 | 80 | 80
CZ16 | Kitchen | 70 | 60 | 75 | 85
CZ16 | Office | 70 | 60 | 75 | 85
CZ16 | lab | 70 | 70 | 75 | 75

## HVAC System
HVAC system - Manufacturing Biotech
Vintage | System Name | Category | Heating Type* | Cooling Type* | Air Distribution | Heating Efficiency | Cooling Efficiency | Note
Existing | cDXGF | Main | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.65
Existing | cDXGF | Alternative | - | - | - | - | -
Existing | cDXGF | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
New Construction | cDXGF | Main | Furnace (gas) | DX-AIR | SZ-CAV | 0.8 | 3.65
New Construction | cDXGF | Alternative | - | - | - | - | -
New Construction | cDXGF | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
Existing | cDXHP | Main | DX-AIR | DX-AIR | SZ-CAV | 3.738 | 3.65
Existing | cDXHP | Alternative | - | - | - | - | -
Existing | cDXHP | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
New Construction | cDXHP | Main | DX-AIR | DX-AIR | SZ-CAV | 3.738 | 3.65
New Construction | cDXHP | Alternative | - | - | - | - | -
New Construction | cDXHP | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
Existing | cAVVG | Main | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Alternative | - | - | - | - | -
Existing | cAVVG | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.805 | 3.05
New Construction | cAVVG | Main | Boiler (gas) | Chiller system | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Alternative | - | - | - | - | -
New Construction | cAVVG | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.805 | 3.05
Existing | cDXOH | Main | None | DX-AIR | SZ-CAV | - | 3.65
Existing | cDXOH | Alternative | - | - | - | - | -
Existing | cDXOH | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
New Construction | cDXOH | Main | None | DX-AIR | SZ-CAV | - | 3.65
New Construction | cDXOH | Alternative | - | - | - | - | -
New Construction | cDXOH | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
Existing | cPVVG | Main | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.65
Existing | cPVVG | Alternative | - | - | - | - | -
Existing | cPVVG | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
New Construction | cPVVG | Main | Furnace (gas) | DX-AIR | SZ-VAV | 0.8 | 3.65
New Construction | cPVVG | Alternative | - | - | - | - | -
New Construction | cPVVG | Customized | Boiler (gas) | Chiller system | SZ-CAV | 0.8 | 2.87
*DX Heating and cooling COPs are calculated based on coil-only input power and exclude fan power
Fan Power - Manufacturing Biotech
Vintage | System Name | HVAC System Identifier | Fan System | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm | Note
Existing | cAVVG | Main | MZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
Existing | cAVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cAVVG | Customized | SZ-CRAC | 5.362 | 0.65 | 0.85 | 0.97
Existing | cAVVG | Customized | SZ-VAV | 2.25 | 0.75 | 0.85 | 0.35
Existing | cAVVG | Customized | SZ-VAV | 3 | 0.75 | 0.85 | 0.47
New Construction | cAVVG | Main | MZ-VAV | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cAVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cAVVG | Customized | SZ-CRAC | 5.362 | 0.65 | 0.85 | 0.97
New Construction | cAVVG | Customized | SZ-VAV | 2.25 | 0.75 | 0.85 | 0.35
New Construction | cAVVG | Customized | SZ-VAV | 3 | 0.75 | 0.85 | 0.47
Existing | cDXGF | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXGF | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXGF | Customized | SZ-CRAC | 5.362 | 0.65 | 0.85 | 0.97
Existing | cDXGF | Customized | SZ-VAV | 2.25 | 0.75 | 0.85 | 0.35
Existing | cDXGF | Customized | SZ-VAV | 3 | 0.75 | 0.85 | 0.47
New Construction | cDXGF | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXGF | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXGF | Customized | SZ-CRAC | 5.362 | 0.65 | 0.85 | 0.97
New Construction | cDXGF | Customized | SZ-VAV | 2.25 | 0.75 | 0.85 | 0.35
New Construction | cDXGF | Customized | SZ-VAV | 3 | 0.75 | 0.85 | 0.47
Existing | cDXHP | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXHP | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXHP | Customized | SZ-CRAC | 5.362 | 0.65 | 0.85 | 0.97
Existing | cDXHP | Customized | SZ-VAV | 2.25 | 0.75 | 0.85 | 0.35
Existing | cDXHP | Customized | SZ-VAV | 3 | 0.75 | 0.85 | 0.47
New Construction | cDXHP | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXHP | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXHP | Customized | SZ-CRAC | 5.362 | 0.65 | 0.85 | 0.97
New Construction | cDXHP | Customized | SZ-VAV | 2.25 | 0.75 | 0.85 | 0.35
New Construction | cDXHP | Customized | SZ-VAV | 3 | 0.75 | 0.85 | 0.47
Existing | cDXOH | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXOH | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXOH | Customized | SZ-CRAC | 5.362 | 0.65 | 0.85 | 0.97
Existing | cDXOH | Customized | SZ-VAV | 2.25 | 0.75 | 0.85 | 0.35
Existing | cDXOH | Customized | SZ-VAV | 3 | 0.75 | 0.85 | 0.47
New Construction | cDXOH | Main | SZ-CAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXOH | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXOH | Customized | SZ-CRAC | 5.362 | 0.65 | 0.85 | 0.97
New Construction | cDXOH | Customized | SZ-VAV | 2.25 | 0.75 | 0.85 | 0.35
New Construction | cDXOH | Customized | SZ-VAV | 3 | 0.75 | 0.85 | 0.47
Existing | cPVVG | Main | SZ-VAV | 3.877 | 0.55 | 0.87 | 0.83
Existing | cPVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
Existing | cPVVG | Customized | SZ-CRAC | 5.362 | 0.65 | 0.85 | 0.97
Existing | cPVVG | Customized | SZ-VAV | 2.25 | 0.75 | 0.85 | 0.35
Existing | cPVVG | Customized | SZ-VAV | 3 | 0.75 | 0.85 | 0.47
New Construction | cPVVG | Main | SZ-VAV | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cPVVG | Customized | SZ-CAV | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cPVVG | Customized | SZ-CRAC | 5.362 | 0.65 | 0.85 | 0.97
New Construction | cPVVG | Customized | SZ-VAV | 2.25 | 0.75 | 0.85 | 0.35
New Construction | cPVVG | Customized | SZ-VAV | 3 | 0.75 | 0.85 | 0.47

## Raw_fanoverview (hidden)
Vintage | HVAC name | System type | HVAC System Identifier | Total Static Pressure (TSP) (in w.c.) | Fan Efficiency | Fan Motor and Drive Efficiency | W/cfm
Existing | cAVVG | MZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
Existing | cAVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cAVVG | SZ-CRAC Fans | Customized | 5.362 | 0.65 | 0.85 | 0.97
Existing | cAVVG | SZ-VAV Fans | Customized | 2.25 | 0.75 | 0.85 | 0.35
Existing | cAVVG | SZ-VAV Fans | Customized | 3 | 0.75 | 0.85 | 0.47
New Construction | cAVVG | MZ-VAV Fans | Main | 5.362 | 0.55 | 0.9 | 1.15
New Construction | cAVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cAVVG | SZ-CRAC Fans | Customized | 5.362 | 0.65 | 0.85 | 0.97
New Construction | cAVVG | SZ-VAV Fans | Customized | 2.25 | 0.75 | 0.85 | 0.35
New Construction | cAVVG | SZ-VAV Fans | Customized | 3 | 0.75 | 0.85 | 0.47
Existing | cDXGF | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXGF | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXGF | SZ-CRAC Fans | Customized | 5.362 | 0.65 | 0.85 | 0.97
Existing | cDXGF | SZ-VAV Fans | Customized | 2.25 | 0.75 | 0.85 | 0.35
Existing | cDXGF | SZ-VAV Fans | Customized | 3 | 0.75 | 0.85 | 0.47
New Construction | cDXGF | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXGF | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXGF | SZ-CRAC Fans | Customized | 5.362 | 0.65 | 0.85 | 0.97
New Construction | cDXGF | SZ-VAV Fans | Customized | 2.25 | 0.75 | 0.85 | 0.35
New Construction | cDXGF | SZ-VAV Fans | Customized | 3 | 0.75 | 0.85 | 0.47
Existing | cDXHP | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXHP | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXHP | SZ-CRAC Fans | Customized | 5.362 | 0.65 | 0.85 | 0.97
Existing | cDXHP | SZ-VAV Fans | Customized | 2.25 | 0.75 | 0.85 | 0.35
Existing | cDXHP | SZ-VAV Fans | Customized | 3 | 0.75 | 0.85 | 0.47
New Construction | cDXHP | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXHP | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXHP | SZ-CRAC Fans | Customized | 5.362 | 0.65 | 0.85 | 0.97
New Construction | cDXHP | SZ-VAV Fans | Customized | 2.25 | 0.75 | 0.85 | 0.35
New Construction | cDXHP | SZ-VAV Fans | Customized | 3 | 0.75 | 0.85 | 0.47
Existing | cDXOH | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cDXOH | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cDXOH | SZ-CRAC Fans | Customized | 5.362 | 0.65 | 0.85 | 0.97
Existing | cDXOH | SZ-VAV Fans | Customized | 2.25 | 0.75 | 0.85 | 0.35
Existing | cDXOH | SZ-VAV Fans | Customized | 3 | 0.75 | 0.85 | 0.47
New Construction | cDXOH | SZ-CAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cDXOH | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cDXOH | SZ-CRAC Fans | Customized | 5.362 | 0.65 | 0.85 | 0.97
New Construction | cDXOH | SZ-VAV Fans | Customized | 2.25 | 0.75 | 0.85 | 0.35
New Construction | cDXOH | SZ-VAV Fans | Customized | 3 | 0.75 | 0.85 | 0.47
Existing | cPVVG | SZ-VAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
Existing | cPVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
Existing | cPVVG | SZ-CRAC Fans | Customized | 5.362 | 0.65 | 0.85 | 0.97
Existing | cPVVG | SZ-VAV Fans | Customized | 2.25 | 0.75 | 0.85 | 0.35
Existing | cPVVG | SZ-VAV Fans | Customized | 3 | 0.75 | 0.85 | 0.47
New Construction | cPVVG | SZ-VAV Fans | Main | 3.877 | 0.55 | 0.87 | 0.83
New Construction | cPVVG | SZ-CAV Fans | Customized | 3.877 | 0.65 | 0.85 | 0.7
New Construction | cPVVG | SZ-CRAC Fans | Customized | 5.362 | 0.65 | 0.85 | 0.97
New Construction | cPVVG | SZ-VAV Fans | Customized | 2.25 | 0.75 | 0.85 | 0.35
New Construction | cPVVG | SZ-VAV Fans | Customized | 3 | 0.75 | 0.85 | 0.47

## Raw_hvac (hidden)
Vintage | System Name | HVAC System Identifier | Air Distribution | Heating Efficiency | Cooling Efficiency | Cooling Coil Type | Heating Coil Type
Existing | cAVVG | Main | MZ-VAV | 0.805 | 3.05
Existing | cAVVG | Customized | SZ-CAV | 0.805 | 3.05 | WATER | WATER
Existing | cAVVG | Customized | SZ-CRAC | 0.805 | 3.4223 | DX-AIR | NONE
Existing | cAVVG | Customized | SZ-VAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cAVVG | Main | MZ-VAV | 0.805 | 3.05
New Construction | cAVVG | Customized | SZ-CAV | 0.805 | 3.05 | WATER | WATER
New Construction | cAVVG | Customized | SZ-CRAC | 0.805 | 3.4223 | DX-AIR | NONE
New Construction | cAVVG | Customized | SZ-VAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cDXGF | Main | SZ-CAV | 0.8 | 3.65
Existing | cDXGF | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
Existing | cDXGF | Customized | SZ-CRAC | 0.8 | 3.4223 | DX-AIR | NONE
Existing | cDXGF | Customized | SZ-VAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cDXGF | Main | SZ-CAV | 0.8 | 3.65
New Construction | cDXGF | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
New Construction | cDXGF | Customized | SZ-CRAC | 0.8 | 3.4223 | DX-AIR | NONE
New Construction | cDXGF | Customized | SZ-VAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cDXHP | Main | SZ-CAV | 3.738 | 3.65
Existing | cDXHP | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
Existing | cDXHP | Customized | SZ-CRAC | 3.23 | 3.4223 | DX-AIR | NONE
Existing | cDXHP | Customized | SZ-VAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cDXHP | Main | SZ-CAV | 3.738 | 3.65
New Construction | cDXHP | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
New Construction | cDXHP | Customized | SZ-CRAC | 3.23 | 3.4223 | DX-AIR | NONE
New Construction | cDXHP | Customized | SZ-VAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cDXOH | Main | SZ-CAV | - | 3.65
Existing | cDXOH | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
Existing | cDXOH | Customized | SZ-CRAC |  | 3.4223 | DX-AIR | NONE
Existing | cDXOH | Customized | SZ-VAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cDXOH | Main | SZ-CAV | - | 3.65
New Construction | cDXOH | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
New Construction | cDXOH | Customized | SZ-CRAC |  | 3.4223 | DX-AIR | NONE
New Construction | cDXOH | Customized | SZ-VAV | 0.8 | 3 | DX-AIR | COMBUSTION
Existing | cPVVG | Main | SZ-VAV | 0.8 | 3.65
Existing | cPVVG | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
Existing | cPVVG | Customized | SZ-CRAC | 0.8 | 3.4223 | DX-AIR | NONE
Existing | cPVVG | Customized | SZ-VAV | 0.8 | 3 | DX-AIR | COMBUSTION
New Construction | cPVVG | Main | SZ-VAV | 0.8 | 3.65
New Construction | cPVVG | Customized | SZ-CAV | 0.8 | 2.87 | WATER | WATER
New Construction | cPVVG | Customized | SZ-CRAC | 0.8 | 3.4223 | DX-AIR | NONE
New Construction | cPVVG | Customized | SZ-VAV | 0.8 | 3 | DX-AIR | COMBUSTION

## Ventilation
Outdoor Airflow Rate - Manufacturing Biotech | [19 empty] | Zone Type
Zone Type | Floor area (ft²) | cfm/person | cfm/ft² | cfm | Notes | [14 empty] | Computer
Computer | 3997.96 | 0 | 0.15 | 599.694 | [15 empty] | Conference
Conference | 3999.03 | 0 | 0.5 | 1999.515 | [15 empty] | Corridor
Corridor | 40004.04 | 0 | 0.15 | 6000.606 | [15 empty] | Dining_fast
Dining_fast | 5998.85 | 0 | 0.5 | 2999.425 | [15 empty] | Kitchen
Kitchen | 2000.13 | 0 | 0.15 | 300.0195 | [15 empty] | Lab
Lab | 90670.84 | 0 | 1 | 90670.84 | [15 empty] | Office
Office | 53323.38 | 0 | 0.15 | 7998.507
OA Controller - Manufacturing Biotech
Element | Vintage | Unit | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16 | Notes
Economizer Maximum Limit Dry-Bulb Temperature | Existing | °F | 75 | 73 | 75 | 73 | 75 | 71 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 75 | 75 | 75
| New Construction | °F | 75 | 73 | 75 | 73 | 75 | 71 | 69 | 71 | 71 | 73 | 75 | 75 | 75 | 75 | 75 | 75
Exhaust hood - Manufacturing Biotech
Type of Hood | Max Exhaust Flow Rate (cfm/ft) | Hood Length (ft) | Hood Exhaust Rate (cfm) | Note
- | - | - | -

## Raw_outdoorairflowrate (hidden)
Zone Type | Floor Area (ft2) | cfm/person | cfm/ft2
Computer | 3997.96 | 0 | 0.15
Conference | 3999.03 | 0 | 0.5
Corridor | 40004.04 | 0 | 0.15
Dining_fast | 5998.85 | 0 | 0.5
Kitchen | 2000.13 | 0 | 0.15
Lab | 90670.84 | 0 | 1
Office | 53323.38 | 0 | 0.15

## Raw_oacontroller (hidden)
Climate Zone | Vintage | Economizer Maximum Limit Dry-Bulb Temperature (F)
CZ01 | Existing | 75
CZ02 | Existing | 73
CZ03 | Existing | 75
CZ04 | Existing | 73
CZ05 | Existing | 75
CZ06 | Existing | 71
CZ07 | Existing | 69
CZ08 | Existing | 71
CZ09 | Existing | 71
CZ10 | Existing | 73
CZ11 | Existing | 75
CZ12 | Existing | 75
CZ13 | Existing | 75
CZ14 | Existing | 75
CZ15 | Existing | 75
CZ16 | Existing | 75
CZ01 | New Construction | 75
CZ02 | New Construction | 73
CZ03 | New Construction | 75
CZ04 | New Construction | 73
CZ05 | New Construction | 75
CZ06 | New Construction | 71
CZ07 | New Construction | 69
CZ08 | New Construction | 71
CZ09 | New Construction | 71
CZ10 | New Construction | 73
CZ11 | New Construction | 75
CZ12 | New Construction | 75
CZ13 | New Construction | 75
CZ14 | New Construction | 75
CZ15 | New Construction | 75
CZ16 | New Construction | 75

## Water Heater
Water Heater - Manufacturing Biotech
Vintage | Fuel type | Burner Efficiency | Maximum Heater Capacity (Btu/hr) | Tank Volume (gallon) | Tank Loss |  | Notes
[5 empty] | Off Cycle (W/K) | On Cycle (W/K)
Existing | Gas | 0.8 | 665924.45 | 139.66 | 1.6282 | 1.6282
New Construction | Gas | 0.8 | 665924.45 | 139.66 | 1.6282 | 1.6282
Peak Hot Water Consumption - Manufacturing Biotech
Space | Floor Area (ft²) | Number of People | Hot Water Usage Specification (gal/hr per person) | Peak Hot Water Usage (gal/hr) | Peak Hot Water Usage (gal/min) | Notes
COMPUTER EL1 CORE SPC (G.C8) | 3997.96 | 1.5 | 1.4393 | 2.1589 | 0.035982
CONFERENCE EL1 CORE SPC (G.C7) | 3999.03 | 33.33 | 0.7199 | 23.9942 | 0.3999
CORRIDOR EL1 CORE SPC (G.C6) | 40004.04 | 5 | 0 | 0 | 0
DINING EL1 CORE SPC (G.C9) | 5998.85 | 33.33 | 6.9354 | 231.1557 | 3.8526
EL1 CORE PLNM (G.C16) | 0 | 0 | 0 | 0 | 0
EL1 CORE PLNM (G.C17) | 0 | 0 | 0 | 0 | 0
EL1 CORE PLNM (G.C18) | 0 | 0 | 0 | 0 | 0
EL1 CORE PLNM (G.C19) | 0 | 0 | 0 | 0 | 0
EL1 CORE PLNM (G.C20) | 0 | 0 | 0 | 0 | 0
EL1 CORE PLNM (G.C21) | 0 | 0 | 0 | 0 | 0
EL1 CORE PLNM (G.C22) | 0 | 0 | 0 | 0 | 0
EL1 EAST PERIM PLNM (G.E13) | 0 | 0 | 0 | 0 | 0
EL1 NORTH PERIM PLNM (G.N14) | 0 | 0 | 0 | 0 | 0
EL1 SOUTH PERIM PLNM (G.S12) | 0 | 0 | 0 | 0 | 0
EL1 WEST PERIM PLNM (G.W15) | 0 | 0 | 0 | 0 | 0
KITCHEN EL1 CORE SPC (G.C10) | 2000.13 | 2.5 | 2.3122 | 5.7804 | 0.09634
LAB EL1 CORE SPC (G.C5) | 90670.84 | 5 | 32.6415 | 163.2075 | 2.7201
OFFICE EL1 CORE SPC (G.C11) | 15879.72 | 5 | 5.7167 | 28.5835 | 0.47639
OFFICE EL1 EAST PERIM SPC (G.E2) | 2513.5 | 5 | 0.90486 | 4.5243 | 0.075405
OFFICE EL1 NORTH PERIM SPC (G.N3) | 16208.33 | 5 | 5.835 | 29.175 | 0.48625
OFFICE EL1 SOUTH PERIM SPC (G.S1) | 16208.33 | 5 | 5.835 | 29.175 | 0.48625
OFFICE EL1 WEST PERIM SPC (G.W4) | 2513.5 | 5 | 0.90486 | 4.5243 | 0.075405
Total (22 Space)

## Raw_waterheater (hidden)
Vintage | Burner Efficiency | Maximum Heater Capacity (Btu/h) | Tank Volume (ft3) | Tank Loss_Off Cycle (W/K) | Tank Loss_On Cycle (W/K)
Existing | 0.8 | 665924.45 | 139.66 | 1.6282 | 1.6282
New Construction | 0.8 | 665924.45 | 139.66 | 1.6282 | 1.6282

## Raw_dhwpeakflowbyzone (hidden)
Space | Peak hot water usage (gal/hr) | Zone Name
Computer EL1 Core Spc (G.C8) | 2.1589 | COMPUTER EL1 CORE SPC (G.C8)
Conference EL1 Core Spc (G.C7) | 23.9942 | CONFERENCE EL1 CORE SPC (G.C7)
Dining EL1 Core Spc (G.C9) | 231.1557 | DINING EL1 CORE SPC (G.C9)
Kitchen EL1 Core Spc (G.C10) | 5.7804 | KITCHEN EL1 CORE SPC (G.C10)
Lab EL1 Core Spc (G.C5) | 163.2075 | LAB EL1 CORE SPC (G.C5)
Office EL1 Core Spc (G.C11) | 28.5835 | OFFICE EL1 CORE SPC (G.C11)
Office EL1 East Perim Spc (G.E2) | 4.5243 | OFFICE EL1 EAST PERIM SPC (G.E2)
Office EL1 North Perim Spc (G.N3) | 29.175 | OFFICE EL1 NORTH PERIM SPC (G.N3)
Office EL1 South Perim Spc (G.S1) | 29.175 | OFFICE EL1 SOUTH PERIM SPC (G.S1)
Office EL1 West Perim Spc (G.W4) | 4.5243 | OFFICE EL1 WEST PERIM SPC (G.W4)

## Interior Lights
Interior Lighting - Manufacturing Biotech
Vintage | Method | Zone type | Floor area (ft²) | Lighting Power Density (Watts/ft²) | Additional Lighting Power for Portable Lighting (Watts/ft²) | Technology | Notes
Existing | Space by space | Computer | 3997.96 | 1.1054 | NA | NA
Existing | Space by space | Conference | 3999.03 | 1.4161 | NA | NA
Existing | Space by space | Corridor | 40004.04 | 0.62242 | NA | NA
Existing | Space by space | Dining_fast | 5998.85 | 1.2136 | NA | NA
Existing | Space by space | Kitchen | 2000.13 | 1.6492 | NA | NA
Existing | Space by space | Lab | 90670.84 | 1.3239 | NA | NA
Existing | Space by space | Office | 53323.38 | 1.2504 | NA | NA
New Construction | Space by space | Computer | 3997.96 | 0.49992 | NA | NA
New Construction | Space by space | Conference | 3999.03 | 0.74991 | NA | NA
New Construction | Space by space | Corridor | 40004.04 | 0.39995 | NA | NA
New Construction | Space by space | Dining_fast | 5998.85 | 0.44995 | NA | NA
New Construction | Space by space | Kitchen | 2000.13 | 0.94987 | NA | NA
New Construction | Space by space | Lab | 90670.84 | 0.89987 | NA | NA
New Construction | Space by space | Office | 53323.38 | 0.59992 | NA | NA

## Ext Lighting
Exterior Lighting - Manufacturing Biotech
Vintage | Non-Motion Controlled Luminaires (W) | Motion-Controlled Luminaires (W) | Total (W) | Notes
Existing | NA | NA | NA
New Consturction | NA | NA | NA

## Raw_interiorlights (hidden)
Vintage | Zone Type | Floor Area (ft2) | Lighting Power Density(W/ft2)
Existing | Computer | 3997.96 | 1.1054
Existing | Conference | 3999.03 | 1.4161
Existing | Corridor | 40004.04 | 0.62242
Existing | Dining_fast | 5998.85 | 1.2136
Existing | Kitchen | 2000.13 | 1.6492
Existing | Lab | 90670.84 | 1.3239
Existing | Office | 53323.38 | 1.2504
New Construction | Computer | 3997.96 | 0.49992
New Construction | Conference | 3999.03 | 0.74991
New Construction | Corridor | 40004.04 | 0.39995
New Construction | Dining_fast | 5998.85 | 0.44995
New Construction | Kitchen | 2000.13 | 0.94987
New Construction | Lab | 90670.84 | 0.89987
New Construction | Office | 53323.38 | 0.59992

## Equipment
Equipment - Manufacturing Biotech
Zone Type | Floor Area (ft²) | Plug Load Intensity (W/ft²) | Gas Power Density (Btu/hr-ft²)
Computer | 3997.96 | 19.9972 | 0
Conference | 3999.03 | 0.99987 | 0
Corridor | 40004.04 | 0 | 0
Dining_fast | 5998.85 | 0.74991 | 0
Kitchen | 2000.13 | 7.7581 | 17.5354
Lab | 90670.84 | 5.999 | 12.6925
Office | 53323.38 | 1.4998 | 0
Refrigeration - Manufacturing Biotech
Refrigeration System Name | Condenser Fan Power | Refrigeration System Working Fluid | Condenser Type
Elevator - Manufacturing Biotech
Vintage | No. of Elevators | Cab Lighting Power Limit | Lighting Shutoff | Cab Fan Control | Fan Power Limit | Regenerative Drive Threshold | Design load (W) | Note
Existing | - | - | - | - | - | - | -
New Construction | - | - | - | - | - | - | -

## Raw_equipment (hidden)
Vintage | Zone Type | Floor Area (ft2) | Plug Load Intensity (W/ft2)
Existing | Computer | 3997.96 | 19.9972
Existing | Conference | 3999.03 | 0.99987
Existing | Corridor | 40004.04 | 0
Existing | Dining_fast | 5998.85 | 0.74991
Existing | Kitchen | 2000.13 | 7.7581
Existing | Lab | 90670.84 | 5.999
Existing | Office | 53323.38 | 1.4998
New Construction | Computer | 3997.96 | 19.9972
New Construction | Conference | 3999.03 | 0.99987
New Construction | Corridor | 40004.04 | 0
New Construction | Dining_fast | 5998.85 | 0.74991
New Construction | Kitchen | 2000.13 | 7.7581
New Construction | Lab | 90670.84 | 5.999
New Construction | Office | 53323.38 | 1.4998

## Raw_gasequipment (hidden)
Vintage | Zone Name | Gas Loads (Btu/h-ft2) | Zone Type
Existing | Kitchen EL1 Core Spc (G.C10) | 17.5354 | Kitchen
Existing | Lab EL1 Core Spc (G.C5) | 12.6925 | Lab
New Construction | Kitchen EL1 Core Spc (G.C10) | 17.5354 | Kitchen
New Construction | Lab EL1 Core Spc (G.C5) | 12.6925 | Lab

## Raw_refrigerationsystem (hidden)
Vintage | Refrigeration System Name | Condenser Fan Power | Working fluid | Condenser Type
No refrigeration system was found

## Schedules
Schedule by Hour - Manufacturing Biotech
Schedule Identifier | Space type | Type | Notes | Hour
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Cooling Setpoint Schedule | Computer room | AllDays | Cooling/Heating setpoints are in °F; others are intensity (0–100%) | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
DHW Sch | Computer room | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DHW Sch | Computer room | Weekdays |  | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.5 | 0.5 | 0.7 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0
Elec Equip Sch | Computer room | AllOtherDays (Through 1/31) |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Elec Equip Sch | Computer room | AllOtherDays (Through 2/28) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Elec Equip Sch | Computer room | AllOtherDays (Through 3/31) |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Elec Equip Sch | Computer room | AllOtherDays (Through 4/30) | bar: Hour 1 to Hour 24
Elec Equip Sch | Computer room | AllOtherDays (Through 5/31) |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Elec Equip Sch | Computer room | AllOtherDays (Through 6/30) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Elec Equip Sch | Computer room | AllOtherDays (Through 7/31) |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Elec Equip Sch | Computer room | AllOtherDays (Through 8/31) | bar: Hour 1 to Hour 24
Elec Equip Sch | Computer room | AllOtherDays (Through 9/30) |  | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Elec Equip Sch | Computer room | AllOtherDays (Through 10/31) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Elec Equip Sch | Computer room | AllOtherDays (Through 11/30) |  | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Elec Equip Sch | Computer room | AllOtherDays (Through 12/31) | bar: Hour 1 to Hour 24
Heating Setpoint Schedule | Computer room | AllDays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Infiltration Schedule | Computer room | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Computer room | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Computer room | Saturdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.15 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.2 | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Lighting Schedule | Computer room | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.7 | 0.8 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
OA Schedule | Computer room | AllDays | bar: Hour 1 to Hour 24
Occupant Sch | Computer room | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Occupant Sch | Computer room | Saturdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Occupant Sch | Computer room | Weekdays |  | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.25 | 0.65 | 0.65 | 0.65 | 0.65 | 0.6 | 0.6 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.25 | 0.1 | 0.05 | 0.05 | 0.05 | 0
Cooling Setpoint Schedule | Kitchen | AllOtherDays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Cooling Setpoint Schedule | Kitchen | Saturdays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Cooling Setpoint Schedule | Kitchen | Weekdays |  | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | Kitchen | AllOtherDays |  | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
DHW Sch | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
DHW Sch | Kitchen | Weekdays |  | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
Elec Equip Sch | Kitchen | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | Kitchen | AllOtherDays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Elec Equip Sch | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Elec Equip Sch | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Heating Setpoint Schedule | Kitchen | AllOtherDays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Heating Setpoint Schedule | Kitchen | Saturdays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Heating Setpoint Schedule | Kitchen | Weekdays |  | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | Kitchen | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Kitchen | AllOtherDays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
Lighting Schedule | Kitchen | Saturdays |  | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Lighting Schedule | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
OA Schedule | Kitchen | AllOtherDays |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OA Schedule | Kitchen | Saturdays |  | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OA Schedule | Kitchen | Weekdays |  | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Occupant Sch | Kitchen | AllOtherDays |  | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Occupant Sch | Kitchen | Saturdays |  | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
Occupant Sch | Kitchen | Weekdays |  | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Cooling Setpoint Schedule | Office | AllOtherDays |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | Office | Saturday |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Cooling Setpoint Schedule | Office | Weekdays |  | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | Office | AllOtherDays |  | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
DHW Sch | Office | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
DHW Sch | Office | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
Elec Equip Sch | Office | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | Office | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | Office | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Elec Equip Sch | Office | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Heating Setpoint Schedule | Office | AllOtherDays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | Office | Saturday |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Heating Setpoint Schedule | Office | Weekdays |  | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | Office | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | Office | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Office | Saturday |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Lighting Schedule | Office | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OA Schedule | Office | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OA Schedule | Office | Saturday |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OA Schedule | Office | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Occupant Sch | Office | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Office | Saturday |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
Occupant Sch | Office | Weekdays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
Infiltration Schedule | Plenum | AllDays | bar: Hour 1 to Hour 24
Cooling Setpoint Schedule | lab | AllDays |  | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
DHW Sch | lab | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
DHW Sch | lab | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
Elec Equip Sch | lab | AllDays | bar: Hour 1 to Hour 24
Elec Equip Sch | lab | AllOtherDays |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elec Equip Sch | lab | Weekdays |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.5 | 0.7 | 0.8 | 0.5 | 0.6 | 0.7 | 0.9 | 0.8 | 0.5 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Heating Setpoint Schedule | lab | AllDays |  | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Infiltration Schedule | lab | AllDays | bar: Hour 1 to Hour 24
Lighting Schedule | lab | AllOtherDays |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Lighting Schedule | lab | Saturdays |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Lighting Schedule | lab | Weekdays |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2
OA Schedule | lab | AllDays | bar: Hour 1 to Hour 24
Occupant Sch | lab | AllOtherDays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Occupant Sch | lab | Weekdays |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.9 | 0.9 | 0.45 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05

## Schedule_Figures
Schedule Figures (linked to Schedules tab)

## Raw_schedule (hidden)
Schedule Identifier | Schedule Name | Type | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Computer room | Cooling Setpoint Schedule | AllDays | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06 | 80.06
Computer room | DHW Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Computer room | DHW Sch | Weekdays | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.9 | 0.9 | 0.5 | 0.5 | 0.7 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0
Computer room | Elec Equip Sch | AllOtherDays (Through 1/31) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Computer room | Elec Equip Sch | AllOtherDays (Through 2/28) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Computer room | Elec Equip Sch | AllOtherDays (Through 3/31) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Computer room | Elec Equip Sch | AllOtherDays (Through 4/30) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Computer room | Elec Equip Sch | AllOtherDays (Through 5/31) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Computer room | Elec Equip Sch | AllOtherDays (Through 6/30) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Computer room | Elec Equip Sch | AllOtherDays (Through 7/31) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Computer room | Elec Equip Sch | AllOtherDays (Through 8/31) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Computer room | Elec Equip Sch | AllOtherDays (Through 9/30) | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Computer room | Elec Equip Sch | AllOtherDays (Through 10/31) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Computer room | Elec Equip Sch | AllOtherDays (Through 11/30) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Computer room | Elec Equip Sch | AllOtherDays (Through 12/31) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Computer room | Heating Setpoint Schedule | AllDays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Computer room | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Computer room | Lighting Schedule | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05
Computer room | Lighting Schedule | Saturdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.15 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.2 | 0.2 | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Computer room | Lighting Schedule | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.7 | 0.8 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.35 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Computer room | OA Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Computer room | Occupant Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Computer room | Occupant Sch | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0
Computer room | Occupant Sch | Weekdays | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.25 | 0.65 | 0.65 | 0.65 | 0.65 | 0.6 | 0.6 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.25 | 0.1 | 0.05 | 0.05 | 0.05 | 0
Kitchen | Cooling Setpoint Schedule | AllOtherDays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | Cooling Setpoint Schedule | Saturdays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | Cooling Setpoint Schedule | Weekdays | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Kitchen | DHW Sch | AllOtherDays | 0.25 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
Kitchen | DHW Sch | Saturdays | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
Kitchen | DHW Sch | Weekdays | 0.2 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
Kitchen | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Elec Equip Sch | AllOtherDays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
Kitchen | Elec Equip Sch | Saturdays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Kitchen | Elec Equip Sch | Weekdays | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
Kitchen | Heating Setpoint Schedule | AllOtherDays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Heating Setpoint Schedule | Saturdays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Heating Setpoint Schedule | Weekdays | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Kitchen | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Lighting Schedule | AllOtherDays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.45 | 0.45 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.45 | 0.3
Kitchen | Lighting Schedule | Saturdays | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.55 | 0.55 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Kitchen | Lighting Schedule | Weekdays | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.35 | 0.55 | 0.55 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3
Kitchen | OA Schedule | AllOtherDays | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | OA Schedule | Saturdays | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | OA Schedule | Weekdays | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kitchen | Occupant Sch | AllOtherDays | 0.2 | 0.2 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.25 | 0.25 | 0.15 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
Kitchen | Occupant Sch | Saturdays | 0.3 | 0.25 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
Kitchen | Occupant Sch | Weekdays | 0.15 | 0.15 | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
Office | Cooling Setpoint Schedule | AllOtherDays | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Office | Cooling Setpoint Schedule | Saturday | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 84.92 | 84.92 | 84.92 | 84.92 | 84.92
Office | Cooling Setpoint Schedule | Weekdays | 84.92 | 84.92 | 84.92 | 84.92 | 84.92 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
Office | DHW Sch | AllOtherDays | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
Office | DHW Sch | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
Office | DHW Sch | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
Office | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Elec Equip Sch | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Elec Equip Sch | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Elec Equip Sch | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Office | Heating Setpoint Schedule | AllOtherDays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Office | Heating Setpoint Schedule | Saturday | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 60.08 | 60.08 | 60.08 | 60.08 | 60.08
Office | Heating Setpoint Schedule | Weekdays | 60.08 | 60.08 | 60.08 | 60.08 | 60.08 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
Office | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Lighting Schedule | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Lighting Schedule | Saturday | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Office | Lighting Schedule | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.35 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
Office | OA Schedule | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Office | OA Schedule | Saturday | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Office | OA Schedule | Weekdays | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Office | Occupant Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Office | Occupant Sch | Saturday | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
Office | Occupant Sch | Weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
Plenum | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
lab | Cooling Setpoint Schedule | AllDays | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02 | 75.02
lab | DHW Sch | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.12 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
lab | DHW Sch | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
lab | Elec Equip Sch | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
lab | Elec Equip Sch | AllOtherDays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
lab | Elec Equip Sch | Weekdays | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.5 | 0.7 | 0.8 | 0.5 | 0.6 | 0.7 | 0.9 | 0.8 | 0.5 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
lab | Heating Setpoint Schedule | AllDays | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98 | 69.98
lab | Infiltration Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
lab | Lighting Schedule | AllOtherDays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
lab | Lighting Schedule | Saturdays | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
lab | Lighting Schedule | Weekdays | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2
lab | OA Schedule | AllDays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
lab | Occupant Sch | AllOtherDays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
lab | Occupant Sch | Weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.9 | 0.9 | 0.45 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05

## Energy Usage
Energy Consumption - Manufacturing Biotech
Climate Zone | HVAC Type | Vintage | Total Floorspace (Excluding Plenums and Crawl Space) (ft²) | Annual Electricity Intensity (kBtu/ft²) | Annual Gas Intensity (kBtu/ft²) | Notes
CZ01 | cAVVG | Existing | 199994.23 | 49.3474 | 90.5661
CZ01 | cAVVG | New Construction | 199994.23 | 44.4755 | 92.6847
CZ01 | cDXGF | Existing | 199994.23 | 52.3403 | 87.3487
CZ01 | cDXGF | New Construction | 199994.23 | 46.5286 | 89.165
CZ01 | cDXHP | Existing | 199994.23 | 53.1377 | 84.0382
CZ01 | cDXHP | New Construction | 199994.23 | 47.3251 | 85.8189
CZ01 | cDXOH | Existing | 199994.23 | 52.3406 | 84.3358
CZ01 | cDXOH | New Construction | 199994.23 | 46.5209 | 86.2059
CZ01 | cPVVG | Existing | 199994.23 | 49.7416 | 88.6486
CZ01 | cPVVG | New Construction | 199994.23 | 44.808 | 90.0829
CZ02 | cAVVG | Existing | 199994.23 | 52.9215 | 65.4949
CZ02 | cAVVG | New Construction | 199994.23 | 47.5226 | 67.1889
CZ02 | cDXGF | Existing | 199994.23 | 56.1175 | 63.2483
CZ02 | cDXGF | New Construction | 199994.23 | 49.558 | 64.9515
CZ02 | cDXHP | Existing | 199994.23 | 56.6212 | 61.3441
CZ02 | cDXHP | New Construction | 199994.23 | 50.0551 | 63.0293
CZ02 | cDXOH | Existing | 199994.23 | 56.111 | 61.4984
CZ02 | cDXOH | New Construction | 199994.23 | 49.5351 | 63.2261
CZ02 | cPVVG | Existing | 199994.23 | 53.166 | 64.169
CZ02 | cPVVG | New Construction | 199994.23 | 47.5888 | 65.6027
CZ03 | cAVVG | Existing | 199994.23 | 51.0697 | 56.0929
CZ03 | cAVVG | New Construction | 199994.23 | 45.9096 | 58.2473
CZ03 | cDXGF | Existing | 199994.23 | 54.1676 | 54.5726
CZ03 | cDXGF | New Construction | 199994.23 | 47.8998 | 56.5653
CZ03 | cDXHP | Existing | 199994.23 | 54.4473 | 53.4002
CZ03 | cDXHP | New Construction | 199994.23 | 48.1916 | 55.319
CZ03 | cDXOH | Existing | 199994.23 | 54.1643 | 53.4976
CZ03 | cDXOH | New Construction | 199994.23 | 47.8912 | 55.4506
CZ03 | cPVVG | Existing | 199994.23 | 51.3089 | 55.2528
CZ03 | cPVVG | New Construction | 199994.23 | 45.9794 | 57.0705
CZ04 | cAVVG | Existing | 199994.23 | 53.8444 | 51.4022
CZ04 | cAVVG | New Construction | 199994.23 | 48.2485 | 53.0967
CZ04 | cDXGF | Existing | 199994.23 | 56.9699 | 49.8822
CZ04 | cDXGF | New Construction | 199994.23 | 50.2468 | 51.5598
CZ04 | cDXHP | Existing | 199994.23 | 57.2166 | 48.8792
CZ04 | cDXHP | New Construction | 199994.23 | 50.5015 | 50.5066
CZ04 | cDXOH | Existing | 199994.23 | 56.9657 | 48.9578
CZ04 | cDXOH | New Construction | 199994.23 | 50.2361 | 50.6099
CZ04 | cPVVG | Existing | 199994.23 | 54.044 | 50.5156
CZ04 | cPVVG | New Construction | 199994.23 | 48.2798 | 52.0303
CZ05 | cAVVG | Existing | 199994.23 | 51.484 | 57.5457
CZ05 | cAVVG | New Construction | 199994.23 | 46.2642 | 59.9219
CZ05 | cDXGF | Existing | 199994.23 | 54.5317 | 56.0144
CZ05 | cDXGF | New Construction | 199994.23 | 48.2174 | 58.1347
CZ05 | cDXHP | Existing | 199994.23 | 54.7893 | 54.9802
CZ05 | cDXHP | New Construction | 199994.23 | 48.4946 | 56.9946
CZ05 | cDXOH | Existing | 199994.23 | 54.5228 | 55.0602
CZ05 | cDXOH | New Construction | 199994.23 | 48.1964 | 57.1055
CZ05 | cPVVG | Existing | 199994.23 | 51.7314 | 56.6397
CZ05 | cPVVG | New Construction | 199994.23 | 46.3272 | 58.5777
CZ06 | cAVVG | Existing | 199994.23 | 53.642 | 31.4901
CZ06 | cAVVG | New Construction | 199994.23 | 47.8646 | 32.7565
CZ06 | cDXGF | Existing | 199994.23 | 56.0169 | 30.9078
CZ06 | cDXGF | New Construction | 199994.23 | 49.3221 | 32.1602
CZ06 | cDXHP | Existing | 199994.23 | 55.9964 | 30.7192
CZ06 | cDXHP | New Construction | 199994.23 | 49.3144 | 31.9217
CZ06 | cDXOH | Existing | 199994.23 | 56.0147 | 30.7324
CZ06 | cDXOH | New Construction | 199994.23 | 49.3194 | 31.9434
CZ06 | cPVVG | Existing | 199994.23 | 53.3385 | 31.1471
CZ06 | cPVVG | New Construction | 199994.23 | 47.4932 | 32.3311
CZ07 | cAVVG | Existing | 199994.23 | 54.7433 | 30.471
CZ07 | cAVVG | New Construction | 199994.23 | 48.4954 | 31.5813
CZ07 | cDXGF | Existing | 199994.23 | 56.946 | 29.887
CZ07 | cDXGF | New Construction | 199994.23 | 50.1623 | 30.985
CZ07 | cDXHP | Existing | 199994.23 | 56.9416 | 29.7071
CZ07 | cDXHP | New Construction | 199994.23 | 50.1695 | 30.7544
CZ07 | cDXOH | Existing | 199994.23 | 56.9442 | 29.7195
CZ07 | cDXOH | New Construction | 199994.23 | 50.1596 | 30.7759
CZ07 | cPVVG | Existing | 199994.23 | 54.2536 | 30.1072
CZ07 | cPVVG | New Construction | 199994.23 | 48.3168 | 31.1444
CZ08 | cAVVG | Existing | 199994.23 | 55.8434 | 34.288
CZ08 | cAVVG | New Construction | 199994.23 | 49.8203 | 35.4377
CZ08 | cDXGF | Existing | 199994.23 | 58.5245 | 33.4775
CZ08 | cDXGF | New Construction | 199994.23 | 51.5206 | 34.6664
CZ08 | cDXHP | Existing | 199994.23 | 58.5653 | 33.174
CZ08 | cDXHP | New Construction | 199994.23 | 51.5729 | 34.3145
CZ08 | cDXOH | Existing | 199994.23 | 58.5205 | 33.1941
CZ08 | cDXOH | New Construction | 199994.23 | 51.5143 | 34.3444
CZ08 | cPVVG | Existing | 199994.23 | 55.6876 | 33.7687
CZ08 | cPVVG | New Construction | 199994.23 | 49.6043 | 34.8837
CZ09 | cAVVG | Existing | 199994.23 | 57.2503 | 32.2209
CZ09 | cAVVG | New Construction | 199994.23 | 50.5211 | 33.1539
CZ09 | cDXGF | Existing | 199994.23 | 59.611 | 31.4318
CZ09 | cDXGF | New Construction | 199994.23 | 52.2691 | 32.4645
CZ09 | cDXHP | Existing | 199994.23 | 59.6334 | 31.1939
CZ09 | cDXHP | New Construction | 199994.23 | 52.3039 | 32.1912
CZ09 | cDXOH | Existing | 199994.23 | 59.6068 | 31.2086
CZ09 | cDXOH | New Construction | 199994.23 | 52.2632 | 32.2135
CZ09 | cPVVG | Existing | 199994.23 | 56.6522 | 31.6976
CZ09 | cPVVG | New Construction | 199994.23 | 50.2708 | 32.6686
CZ10 | cAVVG | Existing | 199994.23 | 60.1046 | 40.2532
CZ10 | cAVVG | New Construction | 199994.23 | 53.7418 | 41.3416
CZ10 | cDXGF | Existing | 199994.23 | 62.7435 | 39.1015
CZ10 | cDXGF | New Construction | 199994.23 | 55.438 | 40.2124
CZ10 | cDXHP | Existing | 199994.23 | 62.9268 | 38.4452
CZ10 | cDXHP | New Construction | 199994.23 | 55.6427 | 39.5137
CZ10 | cDXOH | Existing | 199994.23 | 62.7331 | 38.4888
CZ10 | cDXOH | New Construction | 199994.23 | 55.42 | 39.57
CZ10 | cPVVG | Existing | 199994.23 | 59.8061 | 39.5172
CZ10 | cPVVG | New Construction | 199994.23 | 53.3952 | 40.5198
CZ11 | cAVVG | Existing | 199994.23 | 62.6516 | 56.2308
CZ11 | cAVVG | New Construction | 199994.23 | 56.0647 | 56.8285
CZ11 | cDXGF | Existing | 199994.23 | 65.5534 | 53.9364
CZ11 | cDXGF | New Construction | 199994.23 | 57.8356 | 54.879
CZ11 | cDXHP | Existing | 199994.23 | 66.0722 | 52.1358
CZ11 | cDXHP | New Construction | 199994.23 | 58.3579 | 53.0739
CZ11 | cDXOH | Existing | 199994.23 | 65.5503 | 52.2818
CZ11 | cDXOH | New Construction | 199994.23 | 57.822 | 53.2542
CZ11 | cPVVG | Existing | 199994.23 | 62.433 | 54.9049
CZ11 | cPVVG | New Construction | 199994.23 | 55.7365 | 55.587
CZ12 | cAVVG | Existing | 199994.23 | 59.355 | 56.5728
CZ12 | cAVVG | New Construction | 199994.23 | 53.1641 | 57.645
CZ12 | cDXGF | Existing | 199994.23 | 62.125 | 54.5851
CZ12 | cDXGF | New Construction | 199994.23 | 54.8992 | 55.8161
CZ12 | cDXHP | Existing | 199994.23 | 62.6203 | 52.8511
CZ12 | cDXHP | New Construction | 199994.23 | 55.4031 | 54.0635
CZ12 | cDXOH | Existing | 199994.23 | 62.1241 | 52.9941
CZ12 | cDXOH | New Construction | 199994.23 | 54.8838 | 54.2474
CZ12 | cPVVG | Existing | 199994.23 | 59.209 | 55.4358
CZ12 | cPVVG | New Construction | 199994.23 | 52.9321 | 56.4407
CZ13 | cAVVG | Existing | 199994.23 | 64.4229 | 49.614
CZ13 | cAVVG | New Construction | 199994.23 | 57.5541 | 50.4154
CZ13 | cDXGF | Existing | 199994.23 | 66.9735 | 47.9132
CZ13 | cDXGF | New Construction | 199994.23 | 59.1141 | 48.867
CZ13 | cDXHP | Existing | 199994.23 | 67.366 | 46.5273
CZ13 | cDXHP | New Construction | 199994.23 | 59.5213 | 47.4406
CZ13 | cDXOH | Existing | 199994.23 | 66.9741 | 46.6407
CZ13 | cDXOH | New Construction | 199994.23 | 59.1038 | 47.5895
CZ13 | cPVVG | Existing | 199994.23 | 63.9755 | 48.6614
CZ13 | cPVVG | New Construction | 199994.23 | 57.0762 | 49.4445
CZ14 | cAVVG | Existing | 199994.23 | 68.9745 | 42.2782
CZ14 | cAVVG | New Construction | 199994.23 | 61.227 | 42.9555
CZ14 | cDXGF | Existing | 199994.23 | 71.2748 | 40.8135
CZ14 | cDXGF | New Construction | 199994.23 | 62.8893 | 41.6683
CZ14 | cDXHP | Existing | 199994.23 | 71.5654 | 39.9073
CZ14 | cDXHP | New Construction | 199994.23 | 63.2104 | 40.7178
CZ14 | cDXOH | Existing | 199994.23 | 71.2683 | 39.9743
CZ14 | cDXOH | New Construction | 199994.23 | 62.8756 | 40.8063
CZ14 | cPVVG | Existing | 199994.23 | 68.081 | 41.4047
CZ14 | cPVVG | New Construction | 199994.23 | 60.7395 | 42.1706
CZ15 | cAVVG | Existing | 199994.23 | 78.2657 | 29.6455
CZ15 | cAVVG | New Construction | 199994.23 | 70.3364 | 30.389
CZ15 | cDXGF | Existing | 199994.23 | 79.9592 | 28.8331
CZ15 | cDXGF | New Construction | 199994.23 | 71.0455 | 29.6634
CZ15 | cDXHP | Existing | 199994.23 | 80.0186 | 28.639
CZ15 | cDXHP | New Construction | 199994.23 | 71.1302 | 29.4038
CZ15 | cDXOH | Existing | 199994.23 | 79.9533 | 28.6488
CZ15 | cDXOH | New Construction | 199994.23 | 71.0316 | 29.4186
CZ15 | cPVVG | Existing | 199994.23 | 76.9808 | 29.0335
CZ15 | cPVVG | New Construction | 199994.23 | 69.0815 | 29.8389
CZ16 | cAVVG | Existing | 199994.23 | 58.0795 | 65.7874
CZ16 | cAVVG | New Construction | 199994.23 | 51.8148 | 66.3009
CZ16 | cDXGF | Existing | 199994.23 | 61.4225 | 62.967
CZ16 | cDXGF | New Construction | 199994.23 | 54.0555 | 63.8315
CZ16 | cDXHP | Existing | 199994.23 | 62.4421 | 60.0195
CZ16 | cDXHP | New Construction | 199994.23 | 55.0444 | 60.919
CZ16 | cDXOH | Existing | 199994.23 | 61.5041 | 60.2669
CZ16 | cDXOH | New Construction | 199994.23 | 54.0537 | 61.2358
CZ16 | cPVVG | Existing | 199994.23 | 58.0944 | 64.1949
CZ16 | cPVVG | New Construction | 199994.23 | 51.7176 | 64.8228

## Energy Usage_Figures
Energy Figures (from 'Energy Usage' Tab)
cAVVG ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cAVVG ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 49.3474 | 44.4755 | CZ01 | 90.5661 | 92.6847
CZ02 | 52.9215 | 47.5226 | CZ02 | 65.4949 | 67.1889
CZ03 | 51.0697 | 45.9096 | CZ03 | 56.0929 | 58.2473
CZ04 | 53.8444 | 48.2485 | CZ04 | 51.4022 | 53.0967
CZ05 | 51.484 | 46.2642 | CZ05 | 57.5457 | 59.9219
CZ06 | 53.642 | 47.8646 | CZ06 | 31.4901 | 32.7565
CZ07 | 54.7433 | 48.4954 | CZ07 | 30.471 | 31.5813
CZ08 | 55.8434 | 49.8203 | CZ08 | 34.288 | 35.4377
CZ09 | 57.2503 | 50.5211 | CZ09 | 32.2209 | 33.1539
CZ10 | 60.1046 | 53.7418 | CZ10 | 40.2532 | 41.3416
CZ11 | 62.6516 | 56.0647 | CZ11 | 56.2308 | 56.8285
CZ12 | 59.355 | 53.1641 | CZ12 | 56.5728 | 57.645
CZ13 | 64.4229 | 57.5541 | CZ13 | 49.614 | 50.4154
CZ14 | 68.9745 | 61.227 | CZ14 | 42.2782 | 42.9555
CZ15 | 78.2657 | 70.3364 | CZ15 | 29.6455 | 30.389
CZ16 | 58.0795 | 51.8148 | CZ16 | 65.7874 | 66.3009
cDXGF ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXGF ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 52.3403 | 46.5286 | CZ01 | 87.3487 | 89.165
CZ02 | 56.1175 | 49.558 | CZ02 | 63.2483 | 64.9515
CZ03 | 54.1676 | 47.8998 | CZ03 | 54.5726 | 56.5653
CZ04 | 56.9699 | 50.2468 | CZ04 | 49.8822 | 51.5598
CZ05 | 54.5317 | 48.2174 | CZ05 | 56.0144 | 58.1347
CZ06 | 56.0169 | 49.3221 | CZ06 | 30.9078 | 32.1602
CZ07 | 56.946 | 50.1623 | CZ07 | 29.887 | 30.985
CZ08 | 58.5245 | 51.5206 | CZ08 | 33.4775 | 34.6664
CZ09 | 59.611 | 52.2691 | CZ09 | 31.4318 | 32.4645
CZ10 | 62.7435 | 55.438 | CZ10 | 39.1015 | 40.2124
CZ11 | 65.5534 | 57.8356 | CZ11 | 53.9364 | 54.879
CZ12 | 62.125 | 54.8992 | CZ12 | 54.5851 | 55.8161
CZ13 | 66.9735 | 59.1141 | CZ13 | 47.9132 | 48.867
CZ14 | 71.2748 | 62.8893 | CZ14 | 40.8135 | 41.6683
CZ15 | 79.9592 | 71.0455 | CZ15 | 28.8331 | 29.6634
CZ16 | 61.4225 | 54.0555 | CZ16 | 62.967 | 63.8315
cDXHP ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXHP ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 53.1377 | 47.3251 | CZ01 | 84.0382 | 85.8189
CZ02 | 56.6212 | 50.0551 | CZ02 | 61.3441 | 63.0293
CZ03 | 54.4473 | 48.1916 | CZ03 | 53.4002 | 55.319
CZ04 | 57.2166 | 50.5015 | CZ04 | 48.8792 | 50.5066
CZ05 | 54.7893 | 48.4946 | CZ05 | 54.9802 | 56.9946
CZ06 | 55.9964 | 49.3144 | CZ06 | 30.7192 | 31.9217
CZ07 | 56.9416 | 50.1695 | CZ07 | 29.7071 | 30.7544
CZ08 | 58.5653 | 51.5729 | CZ08 | 33.174 | 34.3145
CZ09 | 59.6334 | 52.3039 | CZ09 | 31.1939 | 32.1912
CZ10 | 62.9268 | 55.6427 | CZ10 | 38.4452 | 39.5137
CZ11 | 66.0722 | 58.3579 | CZ11 | 52.1358 | 53.0739
CZ12 | 62.6203 | 55.4031 | CZ12 | 52.8511 | 54.0635
CZ13 | 67.366 | 59.5213 | CZ13 | 46.5273 | 47.4406
CZ14 | 71.5654 | 63.2104 | CZ14 | 39.9073 | 40.7178
CZ15 | 80.0186 | 71.1302 | CZ15 | 28.639 | 29.4038
CZ16 | 62.4421 | 55.0444 | CZ16 | 60.0195 | 60.919
cDXOH ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cDXOH ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 52.3406 | 46.5209 | CZ01 | 84.3358 | 86.2059
CZ02 | 56.111 | 49.5351 | CZ02 | 61.4984 | 63.2261
CZ03 | 54.1643 | 47.8912 | CZ03 | 53.4976 | 55.4506
CZ04 | 56.9657 | 50.2361 | CZ04 | 48.9578 | 50.6099
CZ05 | 54.5228 | 48.1964 | CZ05 | 55.0602 | 57.1055
CZ06 | 56.0147 | 49.3194 | CZ06 | 30.7324 | 31.9434
CZ07 | 56.9442 | 50.1596 | CZ07 | 29.7195 | 30.7759
CZ08 | 58.5205 | 51.5143 | CZ08 | 33.1941 | 34.3444
CZ09 | 59.6068 | 52.2632 | CZ09 | 31.2086 | 32.2135
CZ10 | 62.7331 | 55.42 | CZ10 | 38.4888 | 39.57
CZ11 | 65.5503 | 57.822 | CZ11 | 52.2818 | 53.2542
CZ12 | 62.1241 | 54.8838 | CZ12 | 52.9941 | 54.2474
CZ13 | 66.9741 | 59.1038 | CZ13 | 46.6407 | 47.5895
CZ14 | 71.2683 | 62.8756 | CZ14 | 39.9743 | 40.8063
CZ15 | 79.9533 | 71.0316 | CZ15 | 28.6488 | 29.4186
CZ16 | 61.5041 | 54.0537 | CZ16 | 60.2669 | 61.2358
cPVVG ¦ Annual Electricity Intensity (kBtu/ft²) |  |  | cPVVG ¦ Annual Gas Intensity (kBtu/ft²)
Climate Zone | Existing | New Construction | Climate Zone | Existing | New Construction
CZ01 | 49.7416 | 44.808 | CZ01 | 88.6486 | 90.0829
CZ02 | 53.166 | 47.5888 | CZ02 | 64.169 | 65.6027
CZ03 | 51.3089 | 45.9794 | CZ03 | 55.2528 | 57.0705
CZ04 | 54.044 | 48.2798 | CZ04 | 50.5156 | 52.0303
CZ05 | 51.7314 | 46.3272 | CZ05 | 56.6397 | 58.5777
CZ06 | 53.3385 | 47.4932 | CZ06 | 31.1471 | 32.3311
CZ07 | 54.2536 | 48.3168 | CZ07 | 30.1072 | 31.1444
CZ08 | 55.6876 | 49.6043 | CZ08 | 33.7687 | 34.8837
CZ09 | 56.6522 | 50.2708 | CZ09 | 31.6976 | 32.6686
CZ10 | 59.8061 | 53.3952 | CZ10 | 39.5172 | 40.5198
CZ11 | 62.433 | 55.7365 | CZ11 | 54.9049 | 55.587
CZ12 | 59.209 | 52.9321 | CZ12 | 55.4358 | 56.4407
CZ13 | 63.9755 | 57.0762 | CZ13 | 48.6614 | 49.4445
CZ14 | 68.081 | 60.7395 | CZ14 | 41.4047 | 42.1706
CZ15 | 76.9808 | 69.0815 | CZ15 | 29.0335 | 29.8389
CZ16 | 58.0944 | 51.7176 | CZ16 | 64.1949 | 64.8228

## Raw_totalendusesannual (hidden)
Vintage | Climate Zone | HVAC System | Electricity (kBtu) | Natural Gas (kBtu)
Existing | CZ01 | cAVVG | 9869190.45 | 18112690.25
Existing | CZ02 | cAVVG | 10584002.24 | 13098595.67
Existing | CZ03 | cAVVG | 10213636.44 | 11218254.26
Existing | CZ04 | cAVVG | 10768570.01 | 10280146.08
Existing | CZ05 | cAVVG | 10296504.37 | 11508817.08
Existing | CZ06 | cAVVG | 10728091.51 | 6297829.92
Existing | CZ07 | cAVVG | 10948336.81 | 6094024.53
Existing | CZ08 | cAVVG | 11168366.65 | 6857409.58
Existing | CZ09 | cAVVG | 11449721.72 | 6443995.22
Existing | CZ10 | cAVVG | 12020563.6 | 8050412.8
Existing | CZ11 | cAVVG | 12529952.32 | 11245841.46
Existing | CZ12 | cAVVG | 11870664.66 | 11314235.24
Existing | CZ13 | cAVVG | 12884210.97 | 9922520.57
Existing | CZ14 | cAVVG | 13794504.39 | 8455390.34
Existing | CZ15 | cAVVG | 15652689.04 | 5928933.2
Existing | CZ16 | cAVVG | 11615570.22 | 13157095.78
New Construction | CZ01 | cAVVG | 8894848.2 | 18536398.23
New Construction | CZ02 | cAVVG | 9504245.54 | 13437401.87
New Construction | CZ03 | cAVVG | 9181646.05 | 11649129.23
New Construction | CZ04 | cAVVG | 9649411.94 | 10619041.58
New Construction | CZ05 | cAVVG | 9252569.59 | 11984032.08
New Construction | CZ06 | cAVVG | 9572645.55 | 6551108.77
New Construction | CZ07 | cAVVG | 9698809.79 | 6316082.92
New Construction | CZ08 | cAVVG | 9963782.49 | 7087329.94
New Construction | CZ09 | cAVVG | 10103934.65 | 6630583.78
New Construction | CZ10 | cAVVG | 10748051.99 | 8268085.2
New Construction | CZ11 | cAVVG | 11212620.49 | 11365378.97
New Construction | CZ12 | cAVVG | 10632508.19 | 11528675.88
New Construction | CZ13 | cAVVG | 11510493.43 | 10082779.67
New Construction | CZ14 | cAVVG | 12245056.51 | 8590859.15
New Construction | CZ15 | cAVVG | 14066866.65 | 6077631.9
New Construction | CZ16 | cAVVG | 10362660.57 | 13259801.77
Existing | CZ01 | cDXGF | 10467752.63 | 17469243.66
Existing | CZ02 | cDXGF | 11223172.83 | 12649286.42
Existing | CZ03 | cDXGF | 10833207.64 | 10914205.26
Existing | CZ04 | cDXGF | 11393658.17 | 9976152.22
Existing | CZ05 | cDXGF | 10906032.26 | 11202555.39
Existing | CZ06 | cDXGF | 11203052.2 | 6181380.64
Existing | CZ07 | cDXGF | 11388875.07 | 5977224.68
Existing | CZ08 | cDXGF | 11704558.45 | 6695303.82
Existing | CZ09 | cDXGF | 11921857.81 | 6286173.99
Existing | CZ10 | cDXGF | 12548334.5 | 7820067.16
Existing | CZ11 | cDXGF | 13110309.37 | 10786963.96
Existing | CZ12 | cDXGF | 12424639.29 | 10916709.64
Existing | CZ13 | cDXGF | 13394316.75 | 9582366.92
Existing | CZ14 | cDXGF | 14254558.17 | 8162459.96
Existing | CZ15 | cDXGF | 15991370.53 | 5766450.32
Existing | CZ16 | cDXGF | 12284141.24 | 12593028.35
New Construction | CZ01 | cDXGF | 9305451.62 | 17832477.27
New Construction | CZ02 | cDXGF | 9911305.84 | 12989931.88
New Construction | CZ03 | cDXGF | 9579690.09 | 11312725.38
New Construction | CZ04 | cDXGF | 10049065.46 | 10311657.1
New Construction | CZ05 | cDXGF | 9643201.92 | 11626602.04
New Construction | CZ06 | cDXGF | 9864142.78 | 6431845.94
New Construction | CZ07 | cDXGF | 10032174.56 | 6196820.78
New Construction | CZ08 | cDXGF | 10303816.71 | 6933072.88
New Construction | CZ09 | cDXGF | 10453522.98 | 6492707.66
New Construction | CZ10 | cDXGF | 11087276.44 | 8042252.27
New Construction | CZ11 | cDXGF | 11566795.02 | 10975483.35
New Construction | CZ12 | cDXGF | 10979522.4 | 11162897.73
New Construction | CZ13 | cDXGF | 11822487.25 | 9773112.62
New Construction | CZ14 | cDXGF | 12577487.44 | 8333421.19
New Construction | CZ15 | cDXGF | 14208697.29 | 5932515.47
New Construction | CZ16 | cDXGF | 10810784.59 | 12765934.02
Existing | CZ01 | cDXHP | 10627241.16 | 16807162.05
Existing | CZ02 | cDXHP | 11323917.46 | 12268475.05
Existing | CZ03 | cDXHP | 10889154.73 | 10679728.45
Existing | CZ04 | cDXHP | 11442997.74 | 9775567.63
Existing | CZ05 | cDXHP | 10957535.31 | 10995712.82
Existing | CZ06 | cDXHP | 11198952.87 | 6143671.88
Existing | CZ07 | cDXHP | 11387997.3 | 5941241.37
Existing | CZ08 | cDXHP | 11712722.2 | 6634606.44
Existing | CZ09 | cDXHP | 11926344.32 | 6238600.51
Existing | CZ10 | cDXHP | 12585000.51 | 7688814.61
Existing | CZ11 | cDXHP | 13214053.1 | 10426850.87
Existing | CZ12 | cDXHP | 12523689.29 | 10569906.8
Existing | CZ13 | cDXHP | 13472805.69 | 9305183.25
Existing | CZ14 | cDXHP | 14312673.5 | 7981224.58
Existing | CZ15 | cDXHP | 16003266.31 | 5727642.14
Existing | CZ16 | cDXHP | 12488058.92 | 12003562.24
New Construction | CZ01 | cDXHP | 9464752.8 | 17163290.55
New Construction | CZ02 | cDXHP | 10010725.4 | 12605501.14
New Construction | CZ03 | cDXHP | 9638046.62 | 11063474.81
New Construction | CZ04 | cDXHP | 10100017.66 | 10101021.51
New Construction | CZ05 | cDXHP | 9698640.58 | 11398589.16
New Construction | CZ06 | cDXHP | 9862589.74 | 6384164.27
New Construction | CZ07 | cDXHP | 10033608.75 | 6150697.36
New Construction | CZ08 | cDXHP | 10314278.71 | 6862706.52
New Construction | CZ09 | cDXHP | 10460483.37 | 6438053.53
New Construction | CZ10 | cDXHP | 11128223.97 | 7902519.1
New Construction | CZ11 | cDXHP | 11671250.76 | 10614467.25
New Construction | CZ12 | cDXHP | 11080293.71 | 10812378.7
New Construction | CZ13 | cDXHP | 11903922.69 | 9487843.22
New Construction | CZ14 | cDXHP | 12641716.42 | 8143329.25
New Construction | CZ15 | cDXHP | 14225631.1 | 5880593.59
New Construction | CZ16 | cDXHP | 11008560.72 | 12183443.6
Existing | CZ01 | cDXOH | 10467824.31 | 16866668.06
Existing | CZ02 | cDXOH | 11221885.33 | 12299326.47
Existing | CZ03 | cDXOH | 10832551.76 | 10699216.3
Existing | CZ04 | cDXOH | 11392802.08 | 9791269.2
Existing | CZ05 | cDXOH | 10904248.95 | 11011717.74
Existing | CZ06 | cDXOH | 11202624.87 | 6146295.33
Existing | CZ07 | cDXOH | 11388520.36 | 5943728.04
Existing | CZ08 | cDXOH | 11703767.16 | 6638627.96
Existing | CZ09 | cDXOH | 11921006.55 | 6241548.64
Existing | CZ10 | cDXOH | 12546250.42 | 7697547.59
Existing | CZ11 | cDXOH | 13109677.82 | 10456057.5
Existing | CZ12 | cDXOH | 12424464.15 | 10598517.25
Existing | CZ13 | cDXOH | 13394437.95 | 9327872.44
Existing | CZ14 | cDXOH | 14253239.26 | 7994620.38
Existing | CZ15 | cDXOH | 15990200.87 | 5729590.29
Existing | CZ16 | cDXOH | 12300457.69 | 12053034.37
New Construction | CZ01 | cDXOH | 9303915.71 | 17240681.27
New Construction | CZ02 | cDXOH | 9906724.98 | 12644862.65
New Construction | CZ03 | cDXOH | 9577959.21 | 11089797.55
New Construction | CZ04 | cDXOH | 10046923.97 | 10121693.88
New Construction | CZ05 | cDXOH | 9639001.26 | 11420776.89
New Construction | CZ06 | cDXOH | 9863590.96 | 6388498
New Construction | CZ07 | cDXOH | 10031627.89 | 6155001.01
New Construction | CZ08 | cDXOH | 10302557.62 | 6868672.64
New Construction | CZ09 | cDXOH | 10452337.62 | 6442508.29
New Construction | CZ10 | cDXOH | 11083676.81 | 7913771.45
New Construction | CZ11 | cDXOH | 11564068.69 | 10650534.61
New Construction | CZ12 | cDXOH | 10976446.18 | 10849170.35
New Construction | CZ13 | cDXOH | 11820410.64 | 9517620.95
New Construction | CZ14 | cDXOH | 12574766.18 | 8161018.2
New Construction | CZ15 | cDXOH | 14205909.78 | 5883552.99
New Construction | CZ16 | cDXOH | 10810435.38 | 12246813.59
Existing | CZ01 | cPVVG | 9948035.08 | 17729205.13
Existing | CZ02 | cPVVG | 10632902.67 | 12833433.94
Existing | CZ03 | cPVVG | 10261493.76 | 11050241.08
Existing | CZ04 | cPVVG | 10808493.28 | 10102822.04
Existing | CZ05 | cPVVG | 10345983.75 | 11327605.34
Existing | CZ06 | cPVVG | 10667386.74 | 6229241.58
Existing | CZ07 | cPVVG | 10850408.24 | 6021258.09
Existing | CZ08 | cPVVG | 11137206.96 | 6753550.32
Existing | CZ09 | cPVVG | 11330116.1 | 6339340.23
Existing | CZ10 | cPVVG | 11960879.5 | 7903219.71
Existing | CZ11 | cPVVG | 12486249.29 | 10980658.33
Existing | CZ12 | cPVVG | 11841464.66 | 11086845.58
Existing | CZ13 | cPVVG | 12794721.36 | 9731994.71
Existing | CZ14 | cPVVG | 13615799.27 | 8280697.45
Existing | CZ15 | cPVVG | 15395724.73 | 5806535.46
Existing | CZ16 | cPVVG | 11618553.58 | 12838603.35
New Construction | CZ01 | cPVVG | 8961342.27 | 18016062.03
New Construction | CZ02 | cPVVG | 9517489.08 | 13120157.81
New Construction | CZ03 | cPVVG | 9195624.65 | 11413772.67
New Construction | CZ04 | cPVVG | 9655689.86 | 10405749.79
New Construction | CZ05 | cPVVG | 9265171.25 | 11715209.68
New Construction | CZ06 | cPVVG | 9498365.14 | 6466023.65
New Construction | CZ07 | cPVVG | 9663080.71 | 6228706.93
New Construction | CZ08 | cPVVG | 9920578.39 | 6976529.99
New Construction | CZ09 | cPVVG | 10053863.61 | 6533540.29
New Construction | CZ10 | cPVVG | 10678728.59 | 8103723.89
New Construction | CZ11 | cPVVG | 11146977.03 | 11117082.09
New Construction | CZ12 | cPVVG | 10586106.23 | 11287824.2
New Construction | CZ13 | cPVVG | 11414914.49 | 9888608.14
New Construction | CZ14 | cPVVG | 12147544.96 | 8433881.26
New Construction | CZ15 | cPVVG | 13815895.34 | 5967611.49
New Construction | CZ16 | cPVVG | 10343214.13 | 12964187.5

## Energy Usage by End Use
Energy Consumption by End Use - Manufacturing Biotech
Climate Zone | HVAC System | Vintage | End Use | Electricity (kBtu) | Natural Gas (kBtu) | Note
CZ01 | cAVVG | Existing | Heating | 0 | 14803653.51
CZ01 | cAVVG | Existing | Cooling | 80746.9 | 0
CZ01 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ01 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ01 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ01 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ01 | cAVVG | Existing | Fans | 2581957.48 | 0
CZ01 | cAVVG | Existing | Pumps | 10063.94 | 0
CZ01 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ01 | cAVVG | Existing | Humidification | 0 | 0
CZ01 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ01 | cAVVG | Existing | Water Systems | 0 | 660996.33
CZ01 | cAVVG | Existing | Refrigeration | 0 | 0
CZ01 | cAVVG | Existing | Generators | 0 | 0
CZ01 | cAVVG | Existing | Total End Uses | 9869190.45 | 18112690.25
CZ02 | cAVVG | Existing | Heating | 0 | 9843179.94
CZ02 | cAVVG | Existing | Cooling | 732770.81 | 0
CZ02 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ02 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ02 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ02 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ02 | cAVVG | Existing | Fans | 2631707.63 | 0
CZ02 | cAVVG | Existing | Pumps | 23101.67 | 0
CZ02 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ02 | cAVVG | Existing | Humidification | 0 | 0
CZ02 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ02 | cAVVG | Existing | Water Systems | 0 | 607375.32
CZ02 | cAVVG | Existing | Refrigeration | 0 | 0
CZ02 | cAVVG | Existing | Generators | 0 | 0
CZ02 | cAVVG | Existing | Total End Uses | 10584002.24 | 13098595.67
CZ03 | cAVVG | Existing | Heating | 0 | 7965218.98
CZ03 | cAVVG | Existing | Cooling | 395971.24 | 0
CZ03 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ03 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ03 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ03 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ03 | cAVVG | Existing | Fans | 2598689.54 | 0
CZ03 | cAVVG | Existing | Pumps | 22553.53 | 0
CZ03 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ03 | cAVVG | Existing | Humidification | 0 | 0
CZ03 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ03 | cAVVG | Existing | Water Systems | 0 | 604994.87
CZ03 | cAVVG | Existing | Refrigeration | 0 | 0
CZ03 | cAVVG | Existing | Generators | 0 | 0
CZ03 | cAVVG | Existing | Total End Uses | 10213636.44 | 11218254.26
CZ04 | cAVVG | Existing | Heating | 0 | 7047886.43
CZ04 | cAVVG | Existing | Cooling | 891925.54 | 0
CZ04 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ04 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ04 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ04 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ04 | cAVVG | Existing | Fans | 2654841.18 | 0
CZ04 | cAVVG | Existing | Pumps | 25381.16 | 0
CZ04 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ04 | cAVVG | Existing | Humidification | 0 | 0
CZ04 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ04 | cAVVG | Existing | Water Systems | 0 | 584219.24
CZ04 | cAVVG | Existing | Refrigeration | 0 | 0
CZ04 | cAVVG | Existing | Generators | 0 | 0
CZ04 | cAVVG | Existing | Total End Uses | 10768570.01 | 10280146.08
CZ05 | cAVVG | Existing | Heating | 0 | 8255729.69
CZ05 | cAVVG | Existing | Cooling | 498060.47 | 0
CZ05 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ05 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ05 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ05 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ05 | cAVVG | Existing | Fans | 2580499.22 | 0
CZ05 | cAVVG | Existing | Pumps | 21522.55 | 0
CZ05 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ05 | cAVVG | Existing | Humidification | 0 | 0
CZ05 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ05 | cAVVG | Existing | Water Systems | 0 | 605046.98
CZ05 | cAVVG | Existing | Refrigeration | 0 | 0
CZ05 | cAVVG | Existing | Generators | 0 | 0
CZ05 | cAVVG | Existing | Total End Uses | 10296504.37 | 11508817.08
CZ06 | cAVVG | Existing | Heating | 0 | 3092473.26
CZ06 | cAVVG | Existing | Cooling | 847222.41 | 0
CZ06 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ06 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ06 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ06 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ06 | cAVVG | Existing | Fans | 2651118.86 | 0
CZ06 | cAVVG | Existing | Pumps | 33328.12 | 0
CZ06 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ06 | cAVVG | Existing | Humidification | 0 | 0
CZ06 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ06 | cAVVG | Existing | Water Systems | 0 | 557316.25
CZ06 | cAVVG | Existing | Refrigeration | 0 | 0
CZ06 | cAVVG | Existing | Generators | 0 | 0
CZ06 | cAVVG | Existing | Total End Uses | 10728091.51 | 6297829.92
CZ07 | cAVVG | Existing | Heating | 0 | 2895792.23
CZ07 | cAVVG | Existing | Cooling | 988452.61 | 0
CZ07 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ07 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ07 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ07 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ07 | cAVVG | Existing | Fans | 2727334.29 | 0
CZ07 | cAVVG | Existing | Pumps | 36127.78 | 0
CZ07 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ07 | cAVVG | Existing | Humidification | 0 | 0
CZ07 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ07 | cAVVG | Existing | Water Systems | 0 | 550191.89
CZ07 | cAVVG | Existing | Refrigeration | 0 | 0
CZ07 | cAVVG | Existing | Generators | 0 | 0
CZ07 | cAVVG | Existing | Total End Uses | 10948336.81 | 6094024.53
CZ08 | cAVVG | Existing | Heating | 0 | 3659940.42
CZ08 | cAVVG | Existing | Cooling | 1236213.67 | 0
CZ08 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ08 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ08 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ08 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ08 | cAVVG | Existing | Fans | 2703721.65 | 0
CZ08 | cAVVG | Existing | Pumps | 32009.19 | 0
CZ08 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ08 | cAVVG | Existing | Humidification | 0 | 0
CZ08 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ08 | cAVVG | Existing | Water Systems | 0 | 549428.74
CZ08 | cAVVG | Existing | Refrigeration | 0 | 0
CZ08 | cAVVG | Existing | Generators | 0 | 0
CZ08 | cAVVG | Existing | Total End Uses | 11168366.65 | 6857409.58
CZ09 | cAVVG | Existing | Heating | 0 | 3254143.09
CZ09 | cAVVG | Existing | Cooling | 1473191.78 | 0
CZ09 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ09 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ09 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ09 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ09 | cAVVG | Existing | Fans | 2739838.63 | 0
CZ09 | cAVVG | Existing | Pumps | 40269.18 | 0
CZ09 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ09 | cAVVG | Existing | Humidification | 0 | 0
CZ09 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ09 | cAVVG | Existing | Water Systems | 0 | 541811.71
CZ09 | cAVVG | Existing | Refrigeration | 0 | 0
CZ09 | cAVVG | Existing | Generators | 0 | 0
CZ09 | cAVVG | Existing | Total End Uses | 11449721.72 | 6443995.22
CZ10 | cAVVG | Existing | Heating | 0 | 4864908.63
CZ10 | cAVVG | Existing | Cooling | 2150137.97 | 0
CZ10 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ10 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ10 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ10 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ10 | cAVVG | Existing | Fans | 2640119.52 | 0
CZ10 | cAVVG | Existing | Pumps | 33883.98 | 0
CZ10 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ10 | cAVVG | Existing | Humidification | 0 | 0
CZ10 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ10 | cAVVG | Existing | Water Systems | 0 | 537463.77
CZ10 | cAVVG | Existing | Refrigeration | 0 | 0
CZ10 | cAVVG | Existing | Generators | 0 | 0
CZ10 | cAVVG | Existing | Total End Uses | 12020563.6 | 8050412.8
CZ11 | cAVVG | Existing | Heating | 0 | 8048333.3
CZ11 | cAVVG | Existing | Cooling | 2553081.65 | 0
CZ11 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ11 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ11 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ11 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ11 | cAVVG | Existing | Fans | 2748090.94 | 0
CZ11 | cAVVG | Existing | Pumps | 32357.6 | 0
CZ11 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ11 | cAVVG | Existing | Humidification | 0 | 0
CZ11 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ11 | cAVVG | Existing | Water Systems | 0 | 549467.74
CZ11 | cAVVG | Existing | Refrigeration | 0 | 0
CZ11 | cAVVG | Existing | Generators | 0 | 0
CZ11 | cAVVG | Existing | Total End Uses | 12529952.32 | 11245841.46
CZ12 | cAVVG | Existing | Heating | 0 | 8101253.35
CZ12 | cAVVG | Existing | Cooling | 1902582.69 | 0
CZ12 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ12 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ12 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ12 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ12 | cAVVG | Existing | Fans | 2740270.62 | 0
CZ12 | cAVVG | Existing | Pumps | 31389.22 | 0
CZ12 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ12 | cAVVG | Existing | Humidification | 0 | 0
CZ12 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ12 | cAVVG | Existing | Water Systems | 0 | 564941.48
CZ12 | cAVVG | Existing | Refrigeration | 0 | 0
CZ12 | cAVVG | Existing | Generators | 0 | 0
CZ12 | cAVVG | Existing | Total End Uses | 11870664.66 | 11314235.24
CZ13 | cAVVG | Existing | Heating | 0 | 6740982.39
CZ13 | cAVVG | Existing | Cooling | 2860986.99 | 0
CZ13 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ13 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ13 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ13 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ13 | cAVVG | Existing | Fans | 2790956.7 | 0
CZ13 | cAVVG | Existing | Pumps | 35845.14 | 0
CZ13 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ13 | cAVVG | Existing | Humidification | 0 | 0
CZ13 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ13 | cAVVG | Existing | Water Systems | 0 | 533497.77
CZ13 | cAVVG | Existing | Refrigeration | 0 | 0
CZ13 | cAVVG | Existing | Generators | 0 | 0
CZ13 | cAVVG | Existing | Total End Uses | 12884210.97 | 9922520.57
CZ14 | cAVVG | Existing | Heating | 0 | 5300915.77
CZ14 | cAVVG | Existing | Cooling | 3846219.18 | 0
CZ14 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ14 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ14 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ14 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ14 | cAVVG | Existing | Fans | 2705598.17 | 0
CZ14 | cAVVG | Existing | Pumps | 46264.91 | 0
CZ14 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ14 | cAVVG | Existing | Humidification | 0 | 0
CZ14 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ14 | cAVVG | Existing | Water Systems | 0 | 506434.16
CZ14 | cAVVG | Existing | Refrigeration | 0 | 0
CZ14 | cAVVG | Existing | Generators | 0 | 0
CZ14 | cAVVG | Existing | Total End Uses | 13794504.39 | 8455390.34
CZ15 | cAVVG | Existing | Heating | 0 | 2831353.79
CZ15 | cAVVG | Existing | Cooling | 5441389.1 | 0
CZ15 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ15 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ15 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ15 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ15 | cAVVG | Existing | Fans | 2969787.75 | 0
CZ15 | cAVVG | Existing | Pumps | 45090.06 | 0
CZ15 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ15 | cAVVG | Existing | Humidification | 0 | 0
CZ15 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ15 | cAVVG | Existing | Water Systems | 0 | 449539
CZ15 | cAVVG | Existing | Refrigeration | 0 | 0
CZ15 | cAVVG | Existing | Generators | 0 | 0
CZ15 | cAVVG | Existing | Total End Uses | 15652689.04 | 5928933.2
CZ16 | cAVVG | Existing | Heating | 0 | 9911648.26
CZ16 | cAVVG | Existing | Cooling | 2136285.66 | 0
CZ16 | cAVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ16 | cAVVG | Existing | Exterior Lighting | 0 | 0
CZ16 | cAVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ16 | cAVVG | Existing | Exterior Equipment | 0 | 0
CZ16 | cAVVG | Existing | Fans | 2251412.51 | 0
CZ16 | cAVVG | Existing | Pumps | 31449.91 | 0
CZ16 | cAVVG | Existing | Heat Rejection | 0 | 0
CZ16 | cAVVG | Existing | Humidification | 0 | 0
CZ16 | cAVVG | Existing | Heat Recovery | 0 | 0
CZ16 | cAVVG | Existing | Water Systems | 0 | 597407.1
CZ16 | cAVVG | Existing | Refrigeration | 0 | 0
CZ16 | cAVVG | Existing | Generators | 0 | 0
CZ16 | cAVVG | Existing | Total End Uses | 11615570.22 | 13157095.78
CZ01 | cAVVG | New Construction | Heating | 0 | 15227554.78
CZ01 | cAVVG | New Construction | Cooling | 78408.85 | 0
CZ01 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ01 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ01 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ01 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ01 | cAVVG | New Construction | Fans | 2539815.19 | 0
CZ01 | cAVVG | New Construction | Pumps | 7900.42 | 0
CZ01 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ01 | cAVVG | New Construction | Humidification | 0 | 0
CZ01 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ01 | cAVVG | New Construction | Water Systems | 0 | 660803.04
CZ01 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ01 | cAVVG | New Construction | Generators | 0 | 0
CZ01 | cAVVG | New Construction | Total End Uses | 8894848.2 | 18536398.23
CZ02 | cAVVG | New Construction | Heating | 0 | 10182254.17
CZ02 | cAVVG | New Construction | Cooling | 646256.83 | 0
CZ02 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ02 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ02 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ02 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ02 | cAVVG | New Construction | Fans | 2571482.12 | 0
CZ02 | cAVVG | New Construction | Pumps | 17782.86 | 0
CZ02 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ02 | cAVVG | New Construction | Humidification | 0 | 0
CZ02 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ02 | cAVVG | New Construction | Water Systems | 0 | 607107.29
CZ02 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ02 | cAVVG | New Construction | Generators | 0 | 0
CZ02 | cAVVG | New Construction | Total End Uses | 9504245.54 | 13437401.87
CZ03 | cAVVG | New Construction | Heating | 0 | 8396358.4
CZ03 | cAVVG | New Construction | Cooling | 343892.9 | 0
CZ03 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ03 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ03 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ03 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ03 | cAVVG | New Construction | Fans | 2551140.51 | 0
CZ03 | cAVVG | New Construction | Pumps | 17888.91 | 0
CZ03 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ03 | cAVVG | New Construction | Humidification | 0 | 0
CZ03 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ03 | cAVVG | New Construction | Water Systems | 0 | 604730.41
CZ03 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ03 | cAVVG | New Construction | Generators | 0 | 0
CZ03 | cAVVG | New Construction | Total End Uses | 9181646.05 | 11649129.23
CZ04 | cAVVG | New Construction | Heating | 0 | 7387092.59
CZ04 | cAVVG | New Construction | Cooling | 775104.17 | 0
CZ04 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ04 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ04 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ04 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ04 | cAVVG | New Construction | Fans | 2586085.66 | 0
CZ04 | cAVVG | New Construction | Pumps | 19498.39 | 0
CZ04 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ04 | cAVVG | New Construction | Humidification | 0 | 0
CZ04 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ04 | cAVVG | New Construction | Water Systems | 0 | 583908.58
CZ04 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ04 | cAVVG | New Construction | Generators | 0 | 0
CZ04 | cAVVG | New Construction | Total End Uses | 9649411.94 | 10619041.58
CZ05 | cAVVG | New Construction | Heating | 0 | 8731215.26
CZ05 | cAVVG | New Construction | Cooling | 436664.76 | 0
CZ05 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ05 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ05 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ05 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ05 | cAVVG | New Construction | Fans | 2530492.01 | 0
CZ05 | cAVVG | New Construction | Pumps | 16689.09 | 0
CZ05 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ05 | cAVVG | New Construction | Humidification | 0 | 0
CZ05 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ05 | cAVVG | New Construction | Water Systems | 0 | 604776.41
CZ05 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ05 | cAVVG | New Construction | Generators | 0 | 0
CZ05 | cAVVG | New Construction | Total End Uses | 9252569.59 | 11984032.08
CZ06 | cAVVG | New Construction | Heating | 0 | 3346061.51
CZ06 | cAVVG | New Construction | Cooling | 699156.36 | 0
CZ06 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ06 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ06 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ06 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ06 | cAVVG | New Construction | Fans | 2579134.64 | 0
CZ06 | cAVVG | New Construction | Pumps | 25630.82 | 0
CZ06 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ06 | cAVVG | New Construction | Humidification | 0 | 0
CZ06 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ06 | cAVVG | New Construction | Water Systems | 0 | 557006.84
CZ06 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ06 | cAVVG | New Construction | Generators | 0 | 0
CZ06 | cAVVG | New Construction | Total End Uses | 9572645.55 | 6551108.77
CZ07 | cAVVG | New Construction | Heating | 0 | 3118221.33
CZ07 | cAVVG | New Construction | Cooling | 794413.09 | 0
CZ07 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ07 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ07 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ07 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ07 | cAVVG | New Construction | Fans | 2612058.6 | 0
CZ07 | cAVVG | New Construction | Pumps | 23614.38 | 0
CZ07 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ07 | cAVVG | New Construction | Humidification | 0 | 0
CZ07 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ07 | cAVVG | New Construction | Water Systems | 0 | 549821.18
CZ07 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ07 | cAVVG | New Construction | Generators | 0 | 0
CZ07 | cAVVG | New Construction | Total End Uses | 9698809.79 | 6316082.92
CZ08 | cAVVG | New Construction | Heating | 0 | 3890293.02
CZ08 | cAVVG | New Construction | Cooling | 1051897.45 | 0
CZ08 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ08 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ08 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ08 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ08 | cAVVG | New Construction | Fans | 2618639.28 | 0
CZ08 | cAVVG | New Construction | Pumps | 24522.02 | 0
CZ08 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ08 | cAVVG | New Construction | Humidification | 0 | 0
CZ08 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ08 | cAVVG | New Construction | Water Systems | 0 | 548996.51
CZ08 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ08 | cAVVG | New Construction | Generators | 0 | 0
CZ08 | cAVVG | New Construction | Total End Uses | 9963782.49 | 7087329.94
CZ09 | cAVVG | New Construction | Heating | 0 | 3441221.11
CZ09 | cAVVG | New Construction | Cooling | 1202734 | 0
CZ09 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ09 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ09 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ09 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ09 | cAVVG | New Construction | Fans | 2607397.43 | 0
CZ09 | cAVVG | New Construction | Pumps | 25079.5 | 0
CZ09 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ09 | cAVVG | New Construction | Humidification | 0 | 0
CZ09 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ09 | cAVVG | New Construction | Water Systems | 0 | 541322.26
CZ09 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ09 | cAVVG | New Construction | Generators | 0 | 0
CZ09 | cAVVG | New Construction | Total End Uses | 10103934.65 | 6630583.78
CZ10 | cAVVG | New Construction | Heating | 0 | 5083039.48
CZ10 | cAVVG | New Construction | Cooling | 1914602.8 | 0
CZ10 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ10 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ10 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ10 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ10 | cAVVG | New Construction | Fans | 2538086.05 | 0
CZ10 | cAVVG | New Construction | Pumps | 26639.42 | 0
CZ10 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ10 | cAVVG | New Construction | Humidification | 0 | 0
CZ10 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ10 | cAVVG | New Construction | Water Systems | 0 | 537005.31
CZ10 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ10 | cAVVG | New Construction | Generators | 0 | 0
CZ10 | cAVVG | New Construction | Total End Uses | 10748051.99 | 8268085.2
CZ11 | cAVVG | New Construction | Heating | 0 | 8168349.64
CZ11 | cAVVG | New Construction | Cooling | 2285703.11 | 0
CZ11 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ11 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ11 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ11 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ11 | cAVVG | New Construction | Fans | 2633309.09 | 0
CZ11 | cAVVG | New Construction | Pumps | 24884.55 | 0
CZ11 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ11 | cAVVG | New Construction | Humidification | 0 | 0
CZ11 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ11 | cAVVG | New Construction | Water Systems | 0 | 548988.92
CZ11 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ11 | cAVVG | New Construction | Generators | 0 | 0
CZ11 | cAVVG | New Construction | Total End Uses | 11212620.49 | 11365378.97
CZ12 | cAVVG | New Construction | Heating | 0 | 8316089.76
CZ12 | cAVVG | New Construction | Cooling | 1696384.79 | 0
CZ12 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ12 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ12 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ12 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ12 | cAVVG | New Construction | Fans | 2642850.34 | 0
CZ12 | cAVVG | New Construction | Pumps | 24549.33 | 0
CZ12 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ12 | cAVVG | New Construction | Humidification | 0 | 0
CZ12 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ12 | cAVVG | New Construction | Water Systems | 0 | 564545.71
CZ12 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ12 | cAVVG | New Construction | Generators | 0 | 0
CZ12 | cAVVG | New Construction | Total End Uses | 10632508.19 | 11528675.88
CZ13 | cAVVG | New Construction | Heating | 0 | 6901922.48
CZ13 | cAVVG | New Construction | Cooling | 2550428.84 | 0
CZ13 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ13 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ13 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ13 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ13 | cAVVG | New Construction | Fans | 2663504.95 | 0
CZ13 | cAVVG | New Construction | Pumps | 27835.91 | 0
CZ13 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ13 | cAVVG | New Construction | Humidification | 0 | 0
CZ13 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ13 | cAVVG | New Construction | Water Systems | 0 | 532816.78
CZ13 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ13 | cAVVG | New Construction | Generators | 0 | 0
CZ13 | cAVVG | New Construction | Total End Uses | 11510493.43 | 10082779.67
CZ14 | cAVVG | New Construction | Heating | 0 | 5437140.86
CZ14 | cAVVG | New Construction | Cooling | 3445192.95 | 0
CZ14 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ14 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ14 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ14 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ14 | cAVVG | New Construction | Fans | 2504960.68 | 0
CZ14 | cAVVG | New Construction | Pumps | 26179.15 | 0
CZ14 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ14 | cAVVG | New Construction | Humidification | 0 | 0
CZ14 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ14 | cAVVG | New Construction | Water Systems | 0 | 505677.87
CZ14 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ14 | cAVVG | New Construction | Generators | 0 | 0
CZ14 | cAVVG | New Construction | Total End Uses | 12245056.51 | 8590859.15
CZ15 | cAVVG | New Construction | Heating | 0 | 2980687.86
CZ15 | cAVVG | New Construction | Cooling | 4943021.03 | 0
CZ15 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ15 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ15 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ15 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ15 | cAVVG | New Construction | Fans | 2819712.44 | 0
CZ15 | cAVVG | New Construction | Pumps | 35409.46 | 0
CZ15 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ15 | cAVVG | New Construction | Humidification | 0 | 0
CZ15 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ15 | cAVVG | New Construction | Water Systems | 0 | 448903.63
CZ15 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ15 | cAVVG | New Construction | Generators | 0 | 0
CZ15 | cAVVG | New Construction | Total End Uses | 14066866.65 | 6077631.9
CZ16 | cAVVG | New Construction | Heating | 0 | 10014683.7
CZ16 | cAVVG | New Construction | Cooling | 1903342.46 | 0
CZ16 | cAVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ16 | cAVVG | New Construction | Exterior Lighting | 0 | 0
CZ16 | cAVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ16 | cAVVG | New Construction | Exterior Equipment | 0 | 0
CZ16 | cAVVG | New Construction | Fans | 2166515.05 | 0
CZ16 | cAVVG | New Construction | Pumps | 24079.33 | 0
CZ16 | cAVVG | New Construction | Heat Rejection | 0 | 0
CZ16 | cAVVG | New Construction | Humidification | 0 | 0
CZ16 | cAVVG | New Construction | Heat Recovery | 0 | 0
CZ16 | cAVVG | New Construction | Water Systems | 0 | 597077.66
CZ16 | cAVVG | New Construction | Refrigeration | 0 | 0
CZ16 | cAVVG | New Construction | Generators | 0 | 0
CZ16 | cAVVG | New Construction | Total End Uses | 10362660.57 | 13259801.77
CZ01 | cDXGF | Existing | Heating | 0 | 14160240.82
CZ01 | cDXGF | Existing | Cooling | 87309.57 | 0
CZ01 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ01 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ01 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXGF | Existing | Fans | 3182353.87 | 0
CZ01 | cDXGF | Existing | Pumps | 1667.07 | 0
CZ01 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ01 | cDXGF | Existing | Humidification | 0 | 0
CZ01 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ01 | cDXGF | Existing | Water Systems | 0 | 660962.43
CZ01 | cDXGF | Existing | Refrigeration | 0 | 0
CZ01 | cDXGF | Existing | Generators | 0 | 0
CZ01 | cDXGF | Existing | Total End Uses | 10467752.63 | 17469243.66
CZ02 | cDXGF | Existing | Heating | 0 | 9393878.41
CZ02 | cDXGF | Existing | Cooling | 685564.65 | 0
CZ02 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ02 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ02 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXGF | Existing | Fans | 3339302.69 | 0
CZ02 | cDXGF | Existing | Pumps | 1883.36 | 0
CZ02 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ02 | cDXGF | Existing | Humidification | 0 | 0
CZ02 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ02 | cDXGF | Existing | Water Systems | 0 | 607367.6
CZ02 | cDXGF | Existing | Refrigeration | 0 | 0
CZ02 | cDXGF | Existing | Generators | 0 | 0
CZ02 | cDXGF | Existing | Total End Uses | 11223172.83 | 12649286.42
CZ03 | cDXGF | Existing | Heating | 0 | 7661180.27
CZ03 | cDXGF | Existing | Cooling | 347278.44 | 0
CZ03 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ03 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ03 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXGF | Existing | Fans | 3287612.83 | 0
CZ03 | cDXGF | Existing | Pumps | 1894.25 | 0
CZ03 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ03 | cDXGF | Existing | Humidification | 0 | 0
CZ03 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ03 | cDXGF | Existing | Water Systems | 0 | 604984.58
CZ03 | cDXGF | Existing | Refrigeration | 0 | 0
CZ03 | cDXGF | Existing | Generators | 0 | 0
CZ03 | cDXGF | Existing | Total End Uses | 10833207.64 | 10914205.26
CZ04 | cDXGF | Existing | Heating | 0 | 6743901.44
CZ04 | cDXGF | Existing | Cooling | 838122.29 | 0
CZ04 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ04 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ04 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXGF | Existing | Fans | 3357166.72 | 0
CZ04 | cDXGF | Existing | Pumps | 1947.03 | 0
CZ04 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ04 | cDXGF | Existing | Humidification | 0 | 0
CZ04 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ04 | cDXGF | Existing | Water Systems | 0 | 584210.37
CZ04 | cDXGF | Existing | Refrigeration | 0 | 0
CZ04 | cDXGF | Existing | Generators | 0 | 0
CZ04 | cDXGF | Existing | Total End Uses | 11393658.17 | 9976152.22
CZ05 | cDXGF | Existing | Heating | 0 | 7949479.83
CZ05 | cDXGF | Existing | Cooling | 455905.89 | 0
CZ05 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ05 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ05 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXGF | Existing | Fans | 3251908.28 | 0
CZ05 | cDXGF | Existing | Pumps | 1795.96 | 0
CZ05 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ05 | cDXGF | Existing | Humidification | 0 | 0
CZ05 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ05 | cDXGF | Existing | Water Systems | 0 | 605035.15
CZ05 | cDXGF | Existing | Refrigeration | 0 | 0
CZ05 | cDXGF | Existing | Generators | 0 | 0
CZ05 | cDXGF | Existing | Total End Uses | 10906032.26 | 11202555.39
CZ06 | cDXGF | Existing | Heating | 0 | 2976018.89
CZ06 | cDXGF | Existing | Cooling | 730049.97 | 0
CZ06 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ06 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ06 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXGF | Existing | Fans | 3274625.9 | 0
CZ06 | cDXGF | Existing | Pumps | 1954.19 | 0
CZ06 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ06 | cDXGF | Existing | Humidification | 0 | 0
CZ06 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ06 | cDXGF | Existing | Water Systems | 0 | 557321.33
CZ06 | cDXGF | Existing | Refrigeration | 0 | 0
CZ06 | cDXGF | Existing | Generators | 0 | 0
CZ06 | cDXGF | Existing | Total End Uses | 11203052.2 | 6181380.64
CZ07 | cDXGF | Existing | Heating | 0 | 2778988.13
CZ07 | cDXGF | Existing | Cooling | 871122.22 | 0
CZ07 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ07 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ07 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXGF | Existing | Fans | 3319321.46 | 0
CZ07 | cDXGF | Existing | Pumps | 2009.26 | 0
CZ07 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ07 | cDXGF | Existing | Humidification | 0 | 0
CZ07 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ07 | cDXGF | Existing | Water Systems | 0 | 550196.14
CZ07 | cDXGF | Existing | Refrigeration | 0 | 0
CZ07 | cDXGF | Existing | Generators | 0 | 0
CZ07 | cDXGF | Existing | Total End Uses | 11388875.07 | 5977224.68
CZ08 | cDXGF | Existing | Heating | 0 | 3497848.42
CZ08 | cDXGF | Existing | Cooling | 1133512.4 | 0
CZ08 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ08 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ08 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXGF | Existing | Fans | 3372571.94 | 0
CZ08 | cDXGF | Existing | Pumps | 2051.97 | 0
CZ08 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ08 | cDXGF | Existing | Humidification | 0 | 0
CZ08 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ08 | cDXGF | Existing | Water Systems | 0 | 549414.99
CZ08 | cDXGF | Existing | Refrigeration | 0 | 0
CZ08 | cDXGF | Existing | Generators | 0 | 0
CZ08 | cDXGF | Existing | Total End Uses | 11704558.45 | 6695303.82
CZ09 | cDXGF | Existing | Heating | 0 | 3096314.35
CZ09 | cDXGF | Existing | Cooling | 1320706.02 | 0
CZ09 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ09 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ09 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXGF | Existing | Fans | 3402651.73 | 0
CZ09 | cDXGF | Existing | Pumps | 2077.93 | 0
CZ09 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ09 | cDXGF | Existing | Humidification | 0 | 0
CZ09 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ09 | cDXGF | Existing | Water Systems | 0 | 541819.23
CZ09 | cDXGF | Existing | Refrigeration | 0 | 0
CZ09 | cDXGF | Existing | Generators | 0 | 0
CZ09 | cDXGF | Existing | Total End Uses | 11921857.81 | 6286173.99
CZ10 | cDXGF | Existing | Heating | 0 | 4634561.84
CZ10 | cDXGF | Existing | Cooling | 2044946.01 | 0
CZ10 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ10 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ10 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXGF | Existing | Fans | 3304862.38 | 0
CZ10 | cDXGF | Existing | Pumps | 2103.98 | 0
CZ10 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ10 | cDXGF | Existing | Humidification | 0 | 0
CZ10 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ10 | cDXGF | Existing | Water Systems | 0 | 537464.91
CZ10 | cDXGF | Existing | Refrigeration | 0 | 0
CZ10 | cDXGF | Existing | Generators | 0 | 0
CZ10 | cDXGF | Existing | Total End Uses | 12548334.5 | 7820067.16
CZ11 | cDXGF | Existing | Heating | 0 | 7589439.08
CZ11 | cDXGF | Existing | Cooling | 2444591.47 | 0
CZ11 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ11 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ11 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXGF | Existing | Fans | 3467203.94 | 0
CZ11 | cDXGF | Existing | Pumps | 2091.83 | 0
CZ11 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ11 | cDXGF | Existing | Humidification | 0 | 0
CZ11 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ11 | cDXGF | Existing | Water Systems | 0 | 549484.47
CZ11 | cDXGF | Existing | Refrigeration | 0 | 0
CZ11 | cDXGF | Existing | Generators | 0 | 0
CZ11 | cDXGF | Existing | Total End Uses | 13110309.37 | 10786963.96
CZ12 | cDXGF | Existing | Heating | 0 | 7703724.06
CZ12 | cDXGF | Existing | Cooling | 1809483.14 | 0
CZ12 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ12 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ12 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXGF | Existing | Fans | 3416703.29 | 0
CZ12 | cDXGF | Existing | Pumps | 2030.73 | 0
CZ12 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ12 | cDXGF | Existing | Humidification | 0 | 0
CZ12 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ12 | cDXGF | Existing | Water Systems | 0 | 564945.17
CZ12 | cDXGF | Existing | Refrigeration | 0 | 0
CZ12 | cDXGF | Existing | Generators | 0 | 0
CZ12 | cDXGF | Existing | Total End Uses | 12424639.29 | 10916709.64
CZ13 | cDXGF | Existing | Heating | 0 | 6400818.53
CZ13 | cDXGF | Existing | Cooling | 2742098.15 | 0
CZ13 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ13 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ13 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXGF | Existing | Fans | 3453609.55 | 0
CZ13 | cDXGF | Existing | Pumps | 2186.91 | 0
CZ13 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ13 | cDXGF | Existing | Humidification | 0 | 0
CZ13 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ13 | cDXGF | Existing | Water Systems | 0 | 533507.98
CZ13 | cDXGF | Existing | Refrigeration | 0 | 0
CZ13 | cDXGF | Existing | Generators | 0 | 0
CZ13 | cDXGF | Existing | Total End Uses | 13394316.75 | 9582366.92
CZ14 | cDXGF | Existing | Heating | 0 | 5007997.14
CZ14 | cDXGF | Existing | Cooling | 3688733.81 | 0
CZ14 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ14 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ14 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXGF | Existing | Fans | 3367220.43 | 0
CZ14 | cDXGF | Existing | Pumps | 2181.8 | 0
CZ14 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ14 | cDXGF | Existing | Humidification | 0 | 0
CZ14 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ14 | cDXGF | Existing | Water Systems | 0 | 506422.4
CZ14 | cDXGF | Existing | Refrigeration | 0 | 0
CZ14 | cDXGF | Existing | Generators | 0 | 0
CZ14 | cDXGF | Existing | Total End Uses | 14254558.17 | 8162459.96
CZ15 | cDXGF | Existing | Heating | 0 | 2668843.33
CZ15 | cDXGF | Existing | Cooling | 5183902.59 | 0
CZ15 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ15 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ15 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXGF | Existing | Fans | 3608718.31 | 0
CZ15 | cDXGF | Existing | Pumps | 2327.5 | 0
CZ15 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ15 | cDXGF | Existing | Humidification | 0 | 0
CZ15 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ15 | cDXGF | Existing | Water Systems | 0 | 449566.58
CZ15 | cDXGF | Existing | Refrigeration | 0 | 0
CZ15 | cDXGF | Existing | Generators | 0 | 0
CZ15 | cDXGF | Existing | Total End Uses | 15991370.53 | 5766450.32
CZ16 | cDXGF | Existing | Heating | 0 | 9347580.31
CZ16 | cDXGF | Existing | Cooling | 2071450.01 | 0
CZ16 | cDXGF | Existing | Interior Lighting | 2428283.52 | 0
CZ16 | cDXGF | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXGF | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ16 | cDXGF | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXGF | Existing | Fans | 3014407.65 | 0
CZ16 | cDXGF | Existing | Pumps | 1861.44 | 0
CZ16 | cDXGF | Existing | Heat Rejection | 0 | 0
CZ16 | cDXGF | Existing | Humidification | 0 | 0
CZ16 | cDXGF | Existing | Heat Recovery | 0 | 0
CZ16 | cDXGF | Existing | Water Systems | 0 | 597407.63
CZ16 | cDXGF | Existing | Refrigeration | 0 | 0
CZ16 | cDXGF | Existing | Generators | 0 | 0
CZ16 | cDXGF | Existing | Total End Uses | 12284141.24 | 12593028.35
CZ01 | cDXGF | New Construction | Heating | 0 | 14523674.27
CZ01 | cDXGF | New Construction | Cooling | 80499.9 | 0
CZ01 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ01 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ01 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXGF | New Construction | Fans | 2954829.06 | 0
CZ01 | cDXGF | New Construction | Pumps | 1398.93 | 0
CZ01 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXGF | New Construction | Humidification | 0 | 0
CZ01 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXGF | New Construction | Water Systems | 0 | 660762.59
CZ01 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ01 | cDXGF | New Construction | Generators | 0 | 0
CZ01 | cDXGF | New Construction | Total End Uses | 9305451.62 | 17832477.27
CZ02 | cDXGF | New Construction | Heating | 0 | 9734809.42
CZ02 | cDXGF | New Construction | Cooling | 600668.41 | 0
CZ02 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ02 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ02 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXGF | New Construction | Fans | 3040371.99 | 0
CZ02 | cDXGF | New Construction | Pumps | 1541.72 | 0
CZ02 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXGF | New Construction | Humidification | 0 | 0
CZ02 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXGF | New Construction | Water Systems | 0 | 607082.05
CZ02 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ02 | cDXGF | New Construction | Generators | 0 | 0
CZ02 | cDXGF | New Construction | Total End Uses | 9911305.84 | 12989931.88
CZ03 | cDXGF | New Construction | Heating | 0 | 8059958.13
CZ03 | cDXGF | New Construction | Cooling | 297094.32 | 0
CZ03 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ03 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ03 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXGF | New Construction | Fans | 3012301.53 | 0
CZ03 | cDXGF | New Construction | Pumps | 1570.52 | 0
CZ03 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXGF | New Construction | Humidification | 0 | 0
CZ03 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXGF | New Construction | Water Systems | 0 | 604726.84
CZ03 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ03 | cDXGF | New Construction | Generators | 0 | 0
CZ03 | cDXGF | New Construction | Total End Uses | 9579690.09 | 11312725.38
CZ04 | cDXGF | New Construction | Heating | 0 | 7079718.88
CZ04 | cDXGF | New Construction | Cooling | 725764.64 | 0
CZ04 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ04 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ04 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXGF | New Construction | Fans | 3052989.59 | 0
CZ04 | cDXGF | New Construction | Pumps | 1587.51 | 0
CZ04 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXGF | New Construction | Humidification | 0 | 0
CZ04 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXGF | New Construction | Water Systems | 0 | 583897.81
CZ04 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ04 | cDXGF | New Construction | Generators | 0 | 0
CZ04 | cDXGF | New Construction | Total End Uses | 10049065.46 | 10311657.1
CZ05 | cDXGF | New Construction | Heating | 0 | 8373825.07
CZ05 | cDXGF | New Construction | Cooling | 394082.04 | 0
CZ05 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ05 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ05 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXGF | New Construction | Fans | 2978940.13 | 0
CZ05 | cDXGF | New Construction | Pumps | 1456.01 | 0
CZ05 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXGF | New Construction | Humidification | 0 | 0
CZ05 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXGF | New Construction | Water Systems | 0 | 604736.56
CZ05 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ05 | cDXGF | New Construction | Generators | 0 | 0
CZ05 | cDXGF | New Construction | Total End Uses | 9643201.92 | 11626602.04
CZ06 | cDXGF | New Construction | Heating | 0 | 3226858.02
CZ06 | cDXGF | New Construction | Cooling | 606068.09 | 0
CZ06 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ06 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ06 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXGF | New Construction | Fans | 2987765.55 | 0
CZ06 | cDXGF | New Construction | Pumps | 1585.41 | 0
CZ06 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXGF | New Construction | Humidification | 0 | 0
CZ06 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXGF | New Construction | Water Systems | 0 | 556947.51
CZ06 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ06 | cDXGF | New Construction | Generators | 0 | 0
CZ06 | cDXGF | New Construction | Total End Uses | 9864142.78 | 6431845.94
CZ07 | cDXGF | New Construction | Heating | 0 | 2998987.93
CZ07 | cDXGF | New Construction | Cooling | 721617.89 | 0
CZ07 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ07 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ07 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXGF | New Construction | Fans | 3040186.06 | 0
CZ07 | cDXGF | New Construction | Pumps | 1646.88 | 0
CZ07 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXGF | New Construction | Humidification | 0 | 0
CZ07 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXGF | New Construction | Water Systems | 0 | 549792.44
CZ07 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ07 | cDXGF | New Construction | Generators | 0 | 0
CZ07 | cDXGF | New Construction | Total End Uses | 10032174.56 | 6196820.78
CZ08 | cDXGF | New Construction | Heating | 0 | 3736037.2
CZ08 | cDXGF | New Construction | Cooling | 969395.49 | 0
CZ08 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ08 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ08 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXGF | New Construction | Fans | 3064035.94 | 0
CZ08 | cDXGF | New Construction | Pumps | 1661.55 | 0
CZ08 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXGF | New Construction | Humidification | 0 | 0
CZ08 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXGF | New Construction | Water Systems | 0 | 548995.27
CZ08 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ08 | cDXGF | New Construction | Generators | 0 | 0
CZ08 | cDXGF | New Construction | Total End Uses | 10303816.71 | 6933072.88
CZ09 | cDXGF | New Construction | Heating | 0 | 3303357.38
CZ09 | cDXGF | New Construction | Cooling | 1120232.98 | 0
CZ09 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ09 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ09 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXGF | New Construction | Fans | 3062890.49 | 0
CZ09 | cDXGF | New Construction | Pumps | 1675.78 | 0
CZ09 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXGF | New Construction | Humidification | 0 | 0
CZ09 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXGF | New Construction | Water Systems | 0 | 541309.87
CZ09 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ09 | cDXGF | New Construction | Generators | 0 | 0
CZ09 | cDXGF | New Construction | Total End Uses | 10453522.98 | 6492707.66
CZ10 | cDXGF | New Construction | Heating | 0 | 4857296.63
CZ10 | cDXGF | New Construction | Cooling | 1820885.93 | 0
CZ10 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ10 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ10 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXGF | New Construction | Fans | 2995969.75 | 0
CZ10 | cDXGF | New Construction | Pumps | 1697.03 | 0
CZ10 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXGF | New Construction | Humidification | 0 | 0
CZ10 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXGF | New Construction | Water Systems | 0 | 536915.23
CZ10 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ10 | cDXGF | New Construction | Generators | 0 | 0
CZ10 | cDXGF | New Construction | Total End Uses | 11087276.44 | 8042252.27
CZ11 | cDXGF | New Construction | Heating | 0 | 7778475.9
CZ11 | cDXGF | New Construction | Cooling | 2191374.53 | 0
CZ11 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ11 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ11 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXGF | New Construction | Fans | 3105010.63 | 0
CZ11 | cDXGF | New Construction | Pumps | 1686.13 | 0
CZ11 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXGF | New Construction | Humidification | 0 | 0
CZ11 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXGF | New Construction | Water Systems | 0 | 548967.04
CZ11 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ11 | cDXGF | New Construction | Generators | 0 | 0
CZ11 | cDXGF | New Construction | Total End Uses | 11566795.02 | 10975483.35
CZ12 | cDXGF | New Construction | Heating | 0 | 7950300.49
CZ12 | cDXGF | New Construction | Cooling | 1611808.32 | 0
CZ12 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ12 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ12 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXGF | New Construction | Fans | 3097363.32 | 0
CZ12 | cDXGF | New Construction | Pumps | 1627.03 | 0
CZ12 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXGF | New Construction | Humidification | 0 | 0
CZ12 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXGF | New Construction | Water Systems | 0 | 564556.83
CZ12 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ12 | cDXGF | New Construction | Generators | 0 | 0
CZ12 | cDXGF | New Construction | Total End Uses | 10979522.4 | 11162897.73
CZ13 | cDXGF | New Construction | Heating | 0 | 6592290.61
CZ13 | cDXGF | New Construction | Cooling | 2446544.62 | 0
CZ13 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ13 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ13 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXGF | New Construction | Fans | 3105440.19 | 0
CZ13 | cDXGF | New Construction | Pumps | 1778.7 | 0
CZ13 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXGF | New Construction | Humidification | 0 | 0
CZ13 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXGF | New Construction | Water Systems | 0 | 532781.6
CZ13 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ13 | cDXGF | New Construction | Generators | 0 | 0
CZ13 | cDXGF | New Construction | Total End Uses | 11822487.25 | 9773112.62
CZ14 | cDXGF | New Construction | Heating | 0 | 5179642.1
CZ14 | cDXGF | New Construction | Cooling | 3327200.92 | 0
CZ14 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ14 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ14 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXGF | New Construction | Fans | 2979790.09 | 0
CZ14 | cDXGF | New Construction | Pumps | 1772.69 | 0
CZ14 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXGF | New Construction | Humidification | 0 | 0
CZ14 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXGF | New Construction | Water Systems | 0 | 505738.68
CZ14 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ14 | cDXGF | New Construction | Generators | 0 | 0
CZ14 | cDXGF | New Construction | Total End Uses | 12577487.44 | 8333421.19
CZ15 | cDXGF | New Construction | Heating | 0 | 2835576.76
CZ15 | cDXGF | New Construction | Cooling | 4705896.25 | 0
CZ15 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ15 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ15 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXGF | New Construction | Fans | 3232194.46 | 0
CZ15 | cDXGF | New Construction | Pumps | 1882.85 | 0
CZ15 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXGF | New Construction | Humidification | 0 | 0
CZ15 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXGF | New Construction | Water Systems | 0 | 448898.3
CZ15 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ15 | cDXGF | New Construction | Generators | 0 | 0
CZ15 | cDXGF | New Construction | Total End Uses | 14208697.29 | 5932515.47
CZ16 | cDXGF | New Construction | Heating | 0 | 9520833.47
CZ16 | cDXGF | New Construction | Cooling | 1846243.11 | 0
CZ16 | cDXGF | New Construction | Interior Lighting | 1500585.11 | 0
CZ16 | cDXGF | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXGF | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ16 | cDXGF | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXGF | New Construction | Fans | 2694322.52 | 0
CZ16 | cDXGF | New Construction | Pumps | 1495.24 | 0
CZ16 | cDXGF | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXGF | New Construction | Humidification | 0 | 0
CZ16 | cDXGF | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXGF | New Construction | Water Systems | 0 | 597060.14
CZ16 | cDXGF | New Construction | Refrigeration | 0 | 0
CZ16 | cDXGF | New Construction | Generators | 0 | 0
CZ16 | cDXGF | New Construction | Total End Uses | 10810784.59 | 12765934.02
CZ01 | cDXHP | Existing | Heating | 159997.04 | 13498159.2
CZ01 | cDXHP | Existing | Cooling | 86801.11 | 0
CZ01 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ01 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ01 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXHP | Existing | Fans | 3182353.81 | 0
CZ01 | cDXHP | Existing | Pumps | 1667.06 | 0
CZ01 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ01 | cDXHP | Existing | Humidification | 0 | 0
CZ01 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ01 | cDXHP | Existing | Water Systems | 0 | 660962.44
CZ01 | cDXHP | Existing | Refrigeration | 0 | 0
CZ01 | cDXHP | Existing | Generators | 0 | 0
CZ01 | cDXHP | Existing | Total End Uses | 10627241.16 | 16807162.05
CZ02 | cDXHP | Existing | Heating | 102615.53 | 9013067.69
CZ02 | cDXHP | Existing | Cooling | 683808.75 | 0
CZ02 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ02 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ02 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXHP | Existing | Fans | 3339187.96 | 0
CZ02 | cDXHP | Existing | Pumps | 1883.09 | 0
CZ02 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ02 | cDXHP | Existing | Humidification | 0 | 0
CZ02 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ02 | cDXHP | Existing | Water Systems | 0 | 607366.95
CZ02 | cDXHP | Existing | Refrigeration | 0 | 0
CZ02 | cDXHP | Existing | Generators | 0 | 0
CZ02 | cDXHP | Existing | Total End Uses | 11323917.46 | 12268475.05
CZ03 | cDXHP | Existing | Heating | 57953.31 | 7426703.5
CZ03 | cDXHP | Existing | Cooling | 345275.97 | 0
CZ03 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ03 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ03 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXHP | Existing | Fans | 3287609.15 | 0
CZ03 | cDXHP | Existing | Pumps | 1894.17 | 0
CZ03 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ03 | cDXHP | Existing | Humidification | 0 | 0
CZ03 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ03 | cDXHP | Existing | Water Systems | 0 | 604984.55
CZ03 | cDXHP | Existing | Refrigeration | 0 | 0
CZ03 | cDXHP | Existing | Generators | 0 | 0
CZ03 | cDXHP | Existing | Total End Uses | 10889154.73 | 10679728.45
CZ04 | cDXHP | Existing | Heating | 49921.41 | 6543285.43
CZ04 | cDXHP | Existing | Cooling | 837596.19 | 0
CZ04 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ04 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ04 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXHP | Existing | Fans | 3357111.08 | 0
CZ04 | cDXHP | Existing | Pumps | 1946.93 | 0
CZ04 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ04 | cDXHP | Existing | Humidification | 0 | 0
CZ04 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ04 | cDXHP | Existing | Water Systems | 0 | 584241.79
CZ04 | cDXHP | Existing | Refrigeration | 0 | 0
CZ04 | cDXHP | Existing | Generators | 0 | 0
CZ04 | cDXHP | Existing | Total End Uses | 11442997.74 | 9775567.63
CZ05 | cDXHP | Existing | Heating | 53092.02 | 7742637.22
CZ05 | cDXHP | Existing | Cooling | 454327.02 | 0
CZ05 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ05 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ05 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXHP | Existing | Fans | 3251898.29 | 0
CZ05 | cDXHP | Existing | Pumps | 1795.86 | 0
CZ05 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ05 | cDXHP | Existing | Humidification | 0 | 0
CZ05 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ05 | cDXHP | Existing | Water Systems | 0 | 605035.19
CZ05 | cDXHP | Existing | Refrigeration | 0 | 0
CZ05 | cDXHP | Existing | Generators | 0 | 0
CZ05 | cDXHP | Existing | Total End Uses | 10957535.31 | 10995712.82
CZ06 | cDXHP | Existing | Heating | 8940.88 | 2938309.12
CZ06 | cDXHP | Existing | Cooling | 717021.81 | 0
CZ06 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ06 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ06 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXHP | Existing | Fans | 3274613.99 | 0
CZ06 | cDXHP | Existing | Pumps | 1954.06 | 0
CZ06 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ06 | cDXHP | Existing | Humidification | 0 | 0
CZ06 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ06 | cDXHP | Existing | Water Systems | 0 | 557322.35
CZ06 | cDXHP | Existing | Refrigeration | 0 | 0
CZ06 | cDXHP | Existing | Generators | 0 | 0
CZ06 | cDXHP | Existing | Total End Uses | 11198952.87 | 6143671.88
CZ07 | cDXHP | Existing | Heating | 8551.49 | 2743004.69
CZ07 | cDXHP | Existing | Cooling | 861694.36 | 0
CZ07 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ07 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ07 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXHP | Existing | Fans | 3319320.08 | 0
CZ07 | cDXHP | Existing | Pumps | 2009.24 | 0
CZ07 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ07 | cDXHP | Existing | Humidification | 0 | 0
CZ07 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ07 | cDXHP | Existing | Water Systems | 0 | 550196.27
CZ07 | cDXHP | Existing | Refrigeration | 0 | 0
CZ07 | cDXHP | Existing | Generators | 0 | 0
CZ07 | cDXHP | Existing | Total End Uses | 11387997.3 | 5941241.37
CZ08 | cDXHP | Existing | Heating | 14614.02 | 3437149.77
CZ08 | cDXHP | Existing | Cooling | 1127074.31 | 0
CZ08 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ08 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ08 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXHP | Existing | Fans | 3372559.77 | 0
CZ08 | cDXHP | Existing | Pumps | 2051.97 | 0
CZ08 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ08 | cDXHP | Existing | Humidification | 0 | 0
CZ08 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ08 | cDXHP | Existing | Water Systems | 0 | 549416.25
CZ08 | cDXHP | Existing | Refrigeration | 0 | 0
CZ08 | cDXHP | Existing | Generators | 0 | 0
CZ08 | cDXHP | Existing | Total End Uses | 11712722.2 | 6634606.44
CZ09 | cDXHP | Existing | Heating | 11403.99 | 3048740.52
CZ09 | cDXHP | Existing | Cooling | 1313840.25 | 0
CZ09 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ09 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ09 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXHP | Existing | Fans | 3402600.11 | 0
CZ09 | cDXHP | Existing | Pumps | 2077.84 | 0
CZ09 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ09 | cDXHP | Existing | Humidification | 0 | 0
CZ09 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ09 | cDXHP | Existing | Water Systems | 0 | 541819.58
CZ09 | cDXHP | Existing | Refrigeration | 0 | 0
CZ09 | cDXHP | Existing | Generators | 0 | 0
CZ09 | cDXHP | Existing | Total End Uses | 11926344.32 | 6238600.51
CZ10 | cDXHP | Existing | Heating | 35347.02 | 4503307.57
CZ10 | cDXHP | Existing | Cooling | 2046316.3 | 0
CZ10 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ10 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ10 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXHP | Existing | Fans | 3304811.22 | 0
CZ10 | cDXHP | Existing | Pumps | 2103.84 | 0
CZ10 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ10 | cDXHP | Existing | Humidification | 0 | 0
CZ10 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ10 | cDXHP | Existing | Water Systems | 0 | 537466.63
CZ10 | cDXHP | Existing | Refrigeration | 0 | 0
CZ10 | cDXHP | Existing | Generators | 0 | 0
CZ10 | cDXHP | Existing | Total End Uses | 12585000.51 | 7688814.61
CZ11 | cDXHP | Existing | Heating | 95489.18 | 7229319.6
CZ11 | cDXHP | Existing | Cooling | 2453236.66 | 0
CZ11 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ11 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ11 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXHP | Existing | Fans | 3466813.41 | 0
CZ11 | cDXHP | Existing | Pumps | 2091.72 | 0
CZ11 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ11 | cDXHP | Existing | Humidification | 0 | 0
CZ11 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ11 | cDXHP | Existing | Water Systems | 0 | 549490.86
CZ11 | cDXHP | Existing | Refrigeration | 0 | 0
CZ11 | cDXHP | Existing | Generators | 0 | 0
CZ11 | cDXHP | Existing | Total End Uses | 13214053.1 | 10426850.87
CZ12 | cDXHP | Existing | Heating | 93101.95 | 7356924.45
CZ12 | cDXHP | Existing | Cooling | 1815629.94 | 0
CZ12 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ12 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ12 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXHP | Existing | Fans | 3416504.81 | 0
CZ12 | cDXHP | Existing | Pumps | 2030.46 | 0
CZ12 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ12 | cDXHP | Existing | Humidification | 0 | 0
CZ12 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ12 | cDXHP | Existing | Water Systems | 0 | 564941.94
CZ12 | cDXHP | Existing | Refrigeration | 0 | 0
CZ12 | cDXHP | Existing | Generators | 0 | 0
CZ12 | cDXHP | Existing | Total End Uses | 12523689.29 | 10569906.8
CZ13 | cDXHP | Existing | Heating | 72564.66 | 6123635.91
CZ13 | cDXHP | Existing | Cooling | 2748190.67 | 0
CZ13 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ13 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ13 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXHP | Existing | Fans | 3453441.3 | 0
CZ13 | cDXHP | Existing | Pumps | 2186.94 | 0
CZ13 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ13 | cDXHP | Existing | Humidification | 0 | 0
CZ13 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ13 | cDXHP | Existing | Water Systems | 0 | 533506.93
CZ13 | cDXHP | Existing | Refrigeration | 0 | 0
CZ13 | cDXHP | Existing | Generators | 0 | 0
CZ13 | cDXHP | Existing | Total End Uses | 13472805.69 | 9305183.25
CZ14 | cDXHP | Existing | Heating | 48306.61 | 4826751.68
CZ14 | cDXHP | Existing | Cooling | 3698871.95 | 0
CZ14 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ14 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ14 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXHP | Existing | Fans | 3366890.97 | 0
CZ14 | cDXHP | Existing | Pumps | 2181.84 | 0
CZ14 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ14 | cDXHP | Existing | Humidification | 0 | 0
CZ14 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ14 | cDXHP | Existing | Water Systems | 0 | 506432.48
CZ14 | cDXHP | Existing | Refrigeration | 0 | 0
CZ14 | cDXHP | Existing | Generators | 0 | 0
CZ14 | cDXHP | Existing | Total End Uses | 14312673.5 | 7981224.58
CZ15 | cDXHP | Existing | Heating | 10101.68 | 2630035.08
CZ15 | cDXHP | Existing | Cooling | 5185733.27 | 0
CZ15 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ15 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ15 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXHP | Existing | Fans | 3608681.72 | 0
CZ15 | cDXHP | Existing | Pumps | 2327.5 | 0
CZ15 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ15 | cDXHP | Existing | Humidification | 0 | 0
CZ15 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ15 | cDXHP | Existing | Water Systems | 0 | 449566.65
CZ15 | cDXHP | Existing | Refrigeration | 0 | 0
CZ15 | cDXHP | Existing | Generators | 0 | 0
CZ15 | cDXHP | Existing | Total End Uses | 16003266.31 | 5727642.14
CZ16 | cDXHP | Existing | Heating | 192681.95 | 8758114.5
CZ16 | cDXHP | Existing | Cooling | 2083137.82 | 0
CZ16 | cDXHP | Existing | Interior Lighting | 2428283.52 | 0
CZ16 | cDXHP | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXHP | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ16 | cDXHP | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXHP | Existing | Fans | 3013956.03 | 0
CZ16 | cDXHP | Existing | Pumps | 1860.99 | 0
CZ16 | cDXHP | Existing | Heat Rejection | 0 | 0
CZ16 | cDXHP | Existing | Humidification | 0 | 0
CZ16 | cDXHP | Existing | Heat Recovery | 0 | 0
CZ16 | cDXHP | Existing | Water Systems | 0 | 597407.33
CZ16 | cDXHP | Existing | Refrigeration | 0 | 0
CZ16 | cDXHP | Existing | Generators | 0 | 0
CZ16 | cDXHP | Existing | Total End Uses | 12488058.92 | 12003562.24
CZ01 | cDXHP | New Construction | Heating | 159941.45 | 13854487.87
CZ01 | cDXHP | New Construction | Cooling | 79859.68 | 0
CZ01 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ01 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ01 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXHP | New Construction | Fans | 2954829.01 | 0
CZ01 | cDXHP | New Construction | Pumps | 1398.93 | 0
CZ01 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXHP | New Construction | Humidification | 0 | 0
CZ01 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXHP | New Construction | Water Systems | 0 | 660762.27
CZ01 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ01 | cDXHP | New Construction | Generators | 0 | 0
CZ01 | cDXHP | New Construction | Total End Uses | 9464752.8 | 17163290.55
CZ02 | cDXHP | New Construction | Heating | 100782.88 | 9350380.43
CZ02 | cDXHP | New Construction | Cooling | 599388.13 | 0
CZ02 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ02 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ02 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXHP | New Construction | Fans | 3040289.22 | 0
CZ02 | cDXHP | New Construction | Pumps | 1541.43 | 0
CZ02 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXHP | New Construction | Humidification | 0 | 0
CZ02 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXHP | New Construction | Water Systems | 0 | 607080.29
CZ02 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ02 | cDXHP | New Construction | Generators | 0 | 0
CZ02 | cDXHP | New Construction | Total End Uses | 10010725.4 | 12605501.14
CZ03 | cDXHP | New Construction | Heating | 60490.15 | 7810708.69
CZ03 | cDXHP | New Construction | Cooling | 294958.68 | 0
CZ03 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ03 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ03 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXHP | New Construction | Fans | 3012303.69 | 0
CZ03 | cDXHP | New Construction | Pumps | 1570.37 | 0
CZ03 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXHP | New Construction | Humidification | 0 | 0
CZ03 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXHP | New Construction | Water Systems | 0 | 604725.71
CZ03 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ03 | cDXHP | New Construction | Generators | 0 | 0
CZ03 | cDXHP | New Construction | Total End Uses | 9638046.62 | 11063474.81
CZ04 | cDXHP | New Construction | Heating | 51341.38 | 6869101.88
CZ04 | cDXHP | New Construction | Cooling | 725544.72 | 0
CZ04 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ04 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ04 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXHP | New Construction | Fans | 3052820.72 | 0
CZ04 | cDXHP | New Construction | Pumps | 1587.12 | 0
CZ04 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXHP | New Construction | Humidification | 0 | 0
CZ04 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXHP | New Construction | Water Systems | 0 | 583879.21
CZ04 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ04 | cDXHP | New Construction | Generators | 0 | 0
CZ04 | cDXHP | New Construction | Total End Uses | 10100017.66 | 10101021.51
CZ05 | cDXHP | New Construction | Heating | 57115.26 | 8145811.92
CZ05 | cDXHP | New Construction | Cooling | 392407.87 | 0
CZ05 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ05 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ05 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXHP | New Construction | Fans | 2978937.8 | 0
CZ05 | cDXHP | New Construction | Pumps | 1455.93 | 0
CZ05 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXHP | New Construction | Humidification | 0 | 0
CZ05 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXHP | New Construction | Water Systems | 0 | 604736.83
CZ05 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ05 | cDXHP | New Construction | Generators | 0 | 0
CZ05 | cDXHP | New Construction | Total End Uses | 9698640.58 | 11398589.16
CZ06 | cDXHP | New Construction | Heating | 11138.92 | 3179183.8
CZ06 | cDXHP | New Construction | Cooling | 593465.58 | 0
CZ06 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ06 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ06 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXHP | New Construction | Fans | 2987676.54 | 0
CZ06 | cDXHP | New Construction | Pumps | 1584.97 | 0
CZ06 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXHP | New Construction | Humidification | 0 | 0
CZ06 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXHP | New Construction | Water Systems | 0 | 556940.06
CZ06 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ06 | cDXHP | New Construction | Generators | 0 | 0
CZ06 | cDXHP | New Construction | Total End Uses | 9862589.74 | 6384164.27
CZ07 | cDXHP | New Construction | Heating | 10773.23 | 2952865.09
CZ07 | cDXHP | New Construction | Cooling | 712276.2 | 0
CZ07 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ07 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ07 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXHP | New Construction | Fans | 3040188.75 | 0
CZ07 | cDXHP | New Construction | Pumps | 1646.85 | 0
CZ07 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXHP | New Construction | Humidification | 0 | 0
CZ07 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXHP | New Construction | Water Systems | 0 | 549791.85
CZ07 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ07 | cDXHP | New Construction | Generators | 0 | 0
CZ07 | cDXHP | New Construction | Total End Uses | 10033608.75 | 6150697.36
CZ08 | cDXHP | New Construction | Heating | 16684.71 | 3665673.04
CZ08 | cDXHP | New Construction | Cooling | 963208.32 | 0
CZ08 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ08 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ08 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXHP | New Construction | Fans | 3064000.67 | 0
CZ08 | cDXHP | New Construction | Pumps | 1661.3 | 0
CZ08 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXHP | New Construction | Humidification | 0 | 0
CZ08 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXHP | New Construction | Water Systems | 0 | 548993.07
CZ08 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ08 | cDXHP | New Construction | Generators | 0 | 0
CZ08 | cDXHP | New Construction | Total End Uses | 10314278.71 | 6862706.52
CZ09 | cDXHP | New Construction | Heating | 12920.71 | 3248704.85
CZ09 | cDXHP | New Construction | Cooling | 1114327.07 | 0
CZ09 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ09 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ09 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXHP | New Construction | Fans | 3062836.46 | 0
CZ09 | cDXHP | New Construction | Pumps | 1675.39 | 0
CZ09 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXHP | New Construction | Humidification | 0 | 0
CZ09 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXHP | New Construction | Water Systems | 0 | 541308.27
CZ09 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ09 | cDXHP | New Construction | Generators | 0 | 0
CZ09 | cDXHP | New Construction | Total End Uses | 10460483.37 | 6438053.53
CZ10 | cDXHP | New Construction | Heating | 36766.86 | 4717555.39
CZ10 | cDXHP | New Construction | Cooling | 1825199.38 | 0
CZ10 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ10 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ10 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXHP | New Construction | Fans | 2995838.36 | 0
CZ10 | cDXHP | New Construction | Pumps | 1695.64 | 0
CZ10 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXHP | New Construction | Humidification | 0 | 0
CZ10 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXHP | New Construction | Water Systems | 0 | 536923.3
CZ10 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ10 | cDXHP | New Construction | Generators | 0 | 0
CZ10 | cDXHP | New Construction | Total End Uses | 11128223.97 | 7902519.1
CZ11 | cDXHP | New Construction | Heating | 93796.26 | 7417543.59
CZ11 | cDXHP | New Construction | Cooling | 2202308.99 | 0
CZ11 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ11 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ11 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXHP | New Construction | Fans | 3104736.77 | 0
CZ11 | cDXHP | New Construction | Pumps | 1685 | 0
CZ11 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXHP | New Construction | Humidification | 0 | 0
CZ11 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXHP | New Construction | Water Systems | 0 | 548883.25
CZ11 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ11 | cDXHP | New Construction | Generators | 0 | 0
CZ11 | cDXHP | New Construction | Total End Uses | 11671250.76 | 10614467.25
CZ12 | cDXHP | New Construction | Heating | 91913.29 | 7599813.6
CZ12 | cDXHP | New Construction | Cooling | 1620938.23 | 0
CZ12 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ12 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ12 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXHP | New Construction | Fans | 3097092.38 | 0
CZ12 | cDXHP | New Construction | Pumps | 1626.08 | 0
CZ12 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXHP | New Construction | Humidification | 0 | 0
CZ12 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXHP | New Construction | Water Systems | 0 | 564524.69
CZ12 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ12 | cDXHP | New Construction | Generators | 0 | 0
CZ12 | cDXHP | New Construction | Total End Uses | 11080293.71 | 10812378.7
CZ13 | cDXHP | New Construction | Heating | 73122.17 | 6306965.11
CZ13 | cDXHP | New Construction | Cooling | 2455073.23 | 0
CZ13 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ13 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ13 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXHP | New Construction | Fans | 3105225.09 | 0
CZ13 | cDXHP | New Construction | Pumps | 1778.48 | 0
CZ13 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXHP | New Construction | Humidification | 0 | 0
CZ13 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXHP | New Construction | Water Systems | 0 | 532837.7
CZ13 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ13 | cDXHP | New Construction | Generators | 0 | 0
CZ13 | cDXHP | New Construction | Total End Uses | 11903922.69 | 9487843.22
CZ14 | cDXHP | New Construction | Heating | 49826.03 | 4989483.64
CZ14 | cDXHP | New Construction | Cooling | 3342243.4 | 0
CZ14 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ14 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ14 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXHP | New Construction | Fans | 2979152.51 | 0
CZ14 | cDXHP | New Construction | Pumps | 1770.76 | 0
CZ14 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXHP | New Construction | Humidification | 0 | 0
CZ14 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXHP | New Construction | Water Systems | 0 | 505805.19
CZ14 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ14 | cDXHP | New Construction | Generators | 0 | 0
CZ14 | cDXHP | New Construction | Total End Uses | 12641716.42 | 8143329.25
CZ15 | cDXHP | New Construction | Heating | 13175.64 | 2783690.69
CZ15 | cDXHP | New Construction | Cooling | 4709778.68 | 0
CZ15 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ15 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ15 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXHP | New Construction | Fans | 3232070.84 | 0
CZ15 | cDXHP | New Construction | Pumps | 1882.21 | 0
CZ15 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXHP | New Construction | Humidification | 0 | 0
CZ15 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXHP | New Construction | Water Systems | 0 | 448862.48
CZ15 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ15 | cDXHP | New Construction | Generators | 0 | 0
CZ15 | cDXHP | New Construction | Total End Uses | 14225631.1 | 5880593.59
CZ16 | cDXHP | New Construction | Heating | 184254.5 | 8938350.06
CZ16 | cDXHP | New Construction | Cooling | 1860177.81 | 0
CZ16 | cDXHP | New Construction | Interior Lighting | 1500585.11 | 0
CZ16 | cDXHP | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXHP | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ16 | cDXHP | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXHP | New Construction | Fans | 2693911.48 | 0
CZ16 | cDXHP | New Construction | Pumps | 1493.2 | 0
CZ16 | cDXHP | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXHP | New Construction | Humidification | 0 | 0
CZ16 | cDXHP | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXHP | New Construction | Water Systems | 0 | 597053.13
CZ16 | cDXHP | New Construction | Refrigeration | 0 | 0
CZ16 | cDXHP | New Construction | Generators | 0 | 0
CZ16 | cDXHP | New Construction | Total End Uses | 11008560.72 | 12183443.6
CZ01 | cDXOH | Existing | Heating | 0 | 13557662.33
CZ01 | cDXOH | Existing | Cooling | 85622.95 | 0
CZ01 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ01 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ01 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ01 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ01 | cDXOH | Existing | Fans | 3184113.85 | 0
CZ01 | cDXOH | Existing | Pumps | 1665.37 | 0
CZ01 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ01 | cDXOH | Existing | Humidification | 0 | 0
CZ01 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ01 | cDXOH | Existing | Water Systems | 0 | 660965.32
CZ01 | cDXOH | Existing | Refrigeration | 0 | 0
CZ01 | cDXOH | Existing | Generators | 0 | 0
CZ01 | cDXOH | Existing | Total End Uses | 10467824.31 | 16866668.06
CZ02 | cDXOH | Existing | Heating | 0 | 9043917.78
CZ02 | cDXOH | Existing | Cooling | 683224.68 | 0
CZ02 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ02 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ02 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ02 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ02 | cDXOH | Existing | Fans | 3340358.71 | 0
CZ02 | cDXOH | Existing | Pumps | 1879.8 | 0
CZ02 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ02 | cDXOH | Existing | Humidification | 0 | 0
CZ02 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ02 | cDXOH | Existing | Water Systems | 0 | 607368.28
CZ02 | cDXOH | Existing | Refrigeration | 0 | 0
CZ02 | cDXOH | Existing | Generators | 0 | 0
CZ02 | cDXOH | Existing | Total End Uses | 11221885.33 | 12299326.47
CZ03 | cDXOH | Existing | Heating | 0 | 7446180.25
CZ03 | cDXOH | Existing | Cooling | 346567.04 | 0
CZ03 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ03 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ03 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ03 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ03 | cDXOH | Existing | Fans | 3287669.14 | 0
CZ03 | cDXOH | Existing | Pumps | 1893.45 | 0
CZ03 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ03 | cDXOH | Existing | Humidification | 0 | 0
CZ03 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ03 | cDXOH | Existing | Water Systems | 0 | 604995.64
CZ03 | cDXOH | Existing | Refrigeration | 0 | 0
CZ03 | cDXOH | Existing | Generators | 0 | 0
CZ03 | cDXOH | Existing | Total End Uses | 10832551.76 | 10699216.3
CZ04 | cDXOH | Existing | Heating | 0 | 6559018.06
CZ04 | cDXOH | Existing | Cooling | 837194.19 | 0
CZ04 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ04 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ04 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ04 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ04 | cDXOH | Existing | Fans | 3357239.17 | 0
CZ04 | cDXOH | Existing | Pumps | 1946.58 | 0
CZ04 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ04 | cDXOH | Existing | Humidification | 0 | 0
CZ04 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ04 | cDXOH | Existing | Water Systems | 0 | 584210.73
CZ04 | cDXOH | Existing | Refrigeration | 0 | 0
CZ04 | cDXOH | Existing | Generators | 0 | 0
CZ04 | cDXOH | Existing | Total End Uses | 11392802.08 | 9791269.2
CZ05 | cDXOH | Existing | Heating | 0 | 7758641.22
CZ05 | cDXOH | Existing | Cooling | 454187.07 | 0
CZ05 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ05 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ05 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ05 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ05 | cDXOH | Existing | Fans | 3251844.02 | 0
CZ05 | cDXOH | Existing | Pumps | 1795.72 | 0
CZ05 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ05 | cDXOH | Existing | Humidification | 0 | 0
CZ05 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ05 | cDXOH | Existing | Water Systems | 0 | 605036.11
CZ05 | cDXOH | Existing | Refrigeration | 0 | 0
CZ05 | cDXOH | Existing | Generators | 0 | 0
CZ05 | cDXOH | Existing | Total End Uses | 10904248.95 | 11011717.74
CZ06 | cDXOH | Existing | Heating | 0 | 2940932.79
CZ06 | cDXOH | Existing | Cooling | 729675.22 | 0
CZ06 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ06 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ06 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ06 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ06 | cDXOH | Existing | Fans | 3274573.39 | 0
CZ06 | cDXOH | Existing | Pumps | 1954.13 | 0
CZ06 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ06 | cDXOH | Existing | Humidification | 0 | 0
CZ06 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ06 | cDXOH | Existing | Water Systems | 0 | 557322.13
CZ06 | cDXOH | Existing | Refrigeration | 0 | 0
CZ06 | cDXOH | Existing | Generators | 0 | 0
CZ06 | cDXOH | Existing | Total End Uses | 11202624.87 | 6146295.33
CZ07 | cDXOH | Existing | Heating | 0 | 2745490.73
CZ07 | cDXOH | Existing | Cooling | 870802.38 | 0
CZ07 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ07 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ07 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ07 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ07 | cDXOH | Existing | Fans | 3319286.6 | 0
CZ07 | cDXOH | Existing | Pumps | 2009.24 | 0
CZ07 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ07 | cDXOH | Existing | Humidification | 0 | 0
CZ07 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ07 | cDXOH | Existing | Water Systems | 0 | 550196.9
CZ07 | cDXOH | Existing | Refrigeration | 0 | 0
CZ07 | cDXOH | Existing | Generators | 0 | 0
CZ07 | cDXOH | Existing | Total End Uses | 11388520.36 | 5943728.04
CZ08 | cDXOH | Existing | Heating | 0 | 3441172.38
CZ08 | cDXOH | Existing | Cooling | 1132717.33 | 0
CZ08 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ08 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ08 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ08 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ08 | cDXOH | Existing | Fans | 3372575.77 | 0
CZ08 | cDXOH | Existing | Pumps | 2051.92 | 0
CZ08 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ08 | cDXOH | Existing | Humidification | 0 | 0
CZ08 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ08 | cDXOH | Existing | Water Systems | 0 | 549415.17
CZ08 | cDXOH | Existing | Refrigeration | 0 | 0
CZ08 | cDXOH | Existing | Generators | 0 | 0
CZ08 | cDXOH | Existing | Total End Uses | 11703767.16 | 6638627.96
CZ09 | cDXOH | Existing | Heating | 0 | 3051687.02
CZ09 | cDXOH | Existing | Cooling | 1319902.72 | 0
CZ09 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ09 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ09 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ09 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ09 | cDXOH | Existing | Fans | 3402603.82 | 0
CZ09 | cDXOH | Existing | Pumps | 2077.88 | 0
CZ09 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ09 | cDXOH | Existing | Humidification | 0 | 0
CZ09 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ09 | cDXOH | Existing | Water Systems | 0 | 541821.21
CZ09 | cDXOH | Existing | Refrigeration | 0 | 0
CZ09 | cDXOH | Existing | Generators | 0 | 0
CZ09 | cDXOH | Existing | Total End Uses | 11921006.55 | 6241548.64
CZ10 | cDXOH | Existing | Heating | 0 | 4512040.45
CZ10 | cDXOH | Existing | Cooling | 2042845.83 | 0
CZ10 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ10 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ10 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ10 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ10 | cDXOH | Existing | Fans | 3304878.47 | 0
CZ10 | cDXOH | Existing | Pumps | 2103.98 | 0
CZ10 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ10 | cDXOH | Existing | Humidification | 0 | 0
CZ10 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ10 | cDXOH | Existing | Water Systems | 0 | 537466.72
CZ10 | cDXOH | Existing | Refrigeration | 0 | 0
CZ10 | cDXOH | Existing | Generators | 0 | 0
CZ10 | cDXOH | Existing | Total End Uses | 12546250.42 | 7697547.59
CZ11 | cDXOH | Existing | Heating | 0 | 7258526.89
CZ11 | cDXOH | Existing | Cooling | 2442517.99 | 0
CZ11 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ11 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ11 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ11 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ11 | cDXOH | Existing | Fans | 3468648.03 | 0
CZ11 | cDXOH | Existing | Pumps | 2089.66 | 0
CZ11 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ11 | cDXOH | Existing | Humidification | 0 | 0
CZ11 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ11 | cDXOH | Existing | Water Systems | 0 | 549490.21
CZ11 | cDXOH | Existing | Refrigeration | 0 | 0
CZ11 | cDXOH | Existing | Generators | 0 | 0
CZ11 | cDXOH | Existing | Total End Uses | 13109677.82 | 10456057.5
CZ12 | cDXOH | Existing | Heating | 0 | 7385526.96
CZ12 | cDXOH | Existing | Cooling | 1807611.7 | 0
CZ12 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ12 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ12 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ12 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ12 | cDXOH | Existing | Fans | 3418403.55 | 0
CZ12 | cDXOH | Existing | Pumps | 2026.77 | 0
CZ12 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ12 | cDXOH | Existing | Humidification | 0 | 0
CZ12 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ12 | cDXOH | Existing | Water Systems | 0 | 564949.87
CZ12 | cDXOH | Existing | Refrigeration | 0 | 0
CZ12 | cDXOH | Existing | Generators | 0 | 0
CZ12 | cDXOH | Existing | Total End Uses | 12424464.15 | 10598517.25
CZ13 | cDXOH | Existing | Heating | 0 | 6146325.83
CZ13 | cDXOH | Existing | Cooling | 2740881.28 | 0
CZ13 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ13 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ13 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ13 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ13 | cDXOH | Existing | Fans | 3454948.37 | 0
CZ13 | cDXOH | Existing | Pumps | 2186.17 | 0
CZ13 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ13 | cDXOH | Existing | Humidification | 0 | 0
CZ13 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ13 | cDXOH | Existing | Water Systems | 0 | 533506.19
CZ13 | cDXOH | Existing | Refrigeration | 0 | 0
CZ13 | cDXOH | Existing | Generators | 0 | 0
CZ13 | cDXOH | Existing | Total End Uses | 13394437.95 | 9327872.44
CZ14 | cDXOH | Existing | Heating | 0 | 4840157.45
CZ14 | cDXOH | Existing | Cooling | 3687329.97 | 0
CZ14 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ14 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ14 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ14 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ14 | cDXOH | Existing | Fans | 3367305.87 | 0
CZ14 | cDXOH | Existing | Pumps | 2181.28 | 0
CZ14 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ14 | cDXOH | Existing | Humidification | 0 | 0
CZ14 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ14 | cDXOH | Existing | Water Systems | 0 | 506422.51
CZ14 | cDXOH | Existing | Refrigeration | 0 | 0
CZ14 | cDXOH | Existing | Generators | 0 | 0
CZ14 | cDXOH | Existing | Total End Uses | 14253239.26 | 7994620.38
CZ15 | cDXOH | Existing | Heating | 0 | 2631983.66
CZ15 | cDXOH | Existing | Cooling | 5182733.87 | 0
CZ15 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ15 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ15 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ15 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ15 | cDXOH | Existing | Fans | 3608717.39 | 0
CZ15 | cDXOH | Existing | Pumps | 2327.48 | 0
CZ15 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ15 | cDXOH | Existing | Humidification | 0 | 0
CZ15 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ15 | cDXOH | Existing | Water Systems | 0 | 449566.22
CZ15 | cDXOH | Existing | Refrigeration | 0 | 0
CZ15 | cDXOH | Existing | Generators | 0 | 0
CZ15 | cDXOH | Existing | Total End Uses | 15990200.87 | 5729590.29
CZ16 | cDXOH | Existing | Heating | 0 | 8807575.22
CZ16 | cDXOH | Existing | Cooling | 2065725.72 | 0
CZ16 | cDXOH | Existing | Interior Lighting | 2428283.52 | 0
CZ16 | cDXOH | Existing | Exterior Lighting | 0 | 0
CZ16 | cDXOH | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ16 | cDXOH | Existing | Exterior Equipment | 0 | 0
CZ16 | cDXOH | Existing | Fans | 3036470.54 | 0
CZ16 | cDXOH | Existing | Pumps | 1839.3 | 0
CZ16 | cDXOH | Existing | Heat Rejection | 0 | 0
CZ16 | cDXOH | Existing | Humidification | 0 | 0
CZ16 | cDXOH | Existing | Heat Recovery | 0 | 0
CZ16 | cDXOH | Existing | Water Systems | 0 | 597418.74
CZ16 | cDXOH | Existing | Refrigeration | 0 | 0
CZ16 | cDXOH | Existing | Generators | 0 | 0
CZ16 | cDXOH | Existing | Total End Uses | 12300457.69 | 12053034.37
CZ01 | cDXOH | New Construction | Heating | 0 | 13931843.35
CZ01 | cDXOH | New Construction | Cooling | 78021.23 | 0
CZ01 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ01 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ01 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ01 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ01 | cDXOH | New Construction | Fans | 2955776.94 | 0
CZ01 | cDXOH | New Construction | Pumps | 1393.81 | 0
CZ01 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ01 | cDXOH | New Construction | Humidification | 0 | 0
CZ01 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ01 | cDXOH | New Construction | Water Systems | 0 | 660797.51
CZ01 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ01 | cDXOH | New Construction | Generators | 0 | 0
CZ01 | cDXOH | New Construction | Total End Uses | 9303915.71 | 17240681.27
CZ02 | cDXOH | New Construction | Heating | 0 | 9389719.64
CZ02 | cDXOH | New Construction | Cooling | 595574.28 | 0
CZ02 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ02 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ02 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ02 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ02 | cDXOH | New Construction | Fans | 3040890.94 | 0
CZ02 | cDXOH | New Construction | Pumps | 1536.02 | 0
CZ02 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ02 | cDXOH | New Construction | Humidification | 0 | 0
CZ02 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ02 | cDXOH | New Construction | Water Systems | 0 | 607102.6
CZ02 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ02 | cDXOH | New Construction | Generators | 0 | 0
CZ02 | cDXOH | New Construction | Total End Uses | 9906724.98 | 12644862.65
CZ03 | cDXOH | New Construction | Heating | 0 | 7836992.07
CZ03 | cDXOH | New Construction | Cooling | 295335.29 | 0
CZ03 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ03 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ03 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ03 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ03 | cDXOH | New Construction | Fans | 3012330.66 | 0
CZ03 | cDXOH | New Construction | Pumps | 1569.54 | 0
CZ03 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ03 | cDXOH | New Construction | Humidification | 0 | 0
CZ03 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ03 | cDXOH | New Construction | Water Systems | 0 | 604765.06
CZ03 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ03 | cDXOH | New Construction | Generators | 0 | 0
CZ03 | cDXOH | New Construction | Total End Uses | 9577959.21 | 11089797.55
CZ04 | cDXOH | New Construction | Heating | 0 | 6889756.53
CZ04 | cDXOH | New Construction | Cooling | 723609.26 | 0
CZ04 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ04 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ04 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ04 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ04 | cDXOH | New Construction | Fans | 3053004.03 | 0
CZ04 | cDXOH | New Construction | Pumps | 1586.95 | 0
CZ04 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ04 | cDXOH | New Construction | Humidification | 0 | 0
CZ04 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ04 | cDXOH | New Construction | Water Systems | 0 | 583896.94
CZ04 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ04 | cDXOH | New Construction | Generators | 0 | 0
CZ04 | cDXOH | New Construction | Total End Uses | 10046923.97 | 10121693.88
CZ05 | cDXOH | New Construction | Heating | 0 | 8167993.87
CZ05 | cDXOH | New Construction | Cooling | 389894.77 | 0
CZ05 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ05 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ05 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ05 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ05 | cDXOH | New Construction | Fans | 2978927.11 | 0
CZ05 | cDXOH | New Construction | Pumps | 1455.66 | 0
CZ05 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ05 | cDXOH | New Construction | Humidification | 0 | 0
CZ05 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ05 | cDXOH | New Construction | Water Systems | 0 | 604742.61
CZ05 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ05 | cDXOH | New Construction | Generators | 0 | 0
CZ05 | cDXOH | New Construction | Total End Uses | 9639001.26 | 11420776.89
CZ06 | cDXOH | New Construction | Heating | 0 | 3183498.18
CZ06 | cDXOH | New Construction | Cooling | 605507.57 | 0
CZ06 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ06 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ06 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ06 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ06 | cDXOH | New Construction | Fans | 2987774.25 | 0
CZ06 | cDXOH | New Construction | Pumps | 1585.4 | 0
CZ06 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ06 | cDXOH | New Construction | Humidification | 0 | 0
CZ06 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ06 | cDXOH | New Construction | Water Systems | 0 | 556959.41
CZ06 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ06 | cDXOH | New Construction | Generators | 0 | 0
CZ06 | cDXOH | New Construction | Total End Uses | 9863590.96 | 6388498
CZ07 | cDXOH | New Construction | Heating | 0 | 2957182.87
CZ07 | cDXOH | New Construction | Cooling | 721059.96 | 0
CZ07 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ07 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ07 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ07 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ07 | cDXOH | New Construction | Fans | 3040197.33 | 0
CZ07 | cDXOH | New Construction | Pumps | 1646.87 | 0
CZ07 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ07 | cDXOH | New Construction | Humidification | 0 | 0
CZ07 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ07 | cDXOH | New Construction | Water Systems | 0 | 549777.73
CZ07 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ07 | cDXOH | New Construction | Generators | 0 | 0
CZ07 | cDXOH | New Construction | Total End Uses | 10031627.89 | 6155001.01
CZ08 | cDXOH | New Construction | Heating | 0 | 3671631.52
CZ08 | cDXOH | New Construction | Cooling | 968125.25 | 0
CZ08 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ08 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ08 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ08 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ08 | cDXOH | New Construction | Fans | 3064047.03 | 0
CZ08 | cDXOH | New Construction | Pumps | 1661.61 | 0
CZ08 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ08 | cDXOH | New Construction | Humidification | 0 | 0
CZ08 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ08 | cDXOH | New Construction | Water Systems | 0 | 549000.7
CZ08 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ08 | cDXOH | New Construction | Generators | 0 | 0
CZ08 | cDXOH | New Construction | Total End Uses | 10302557.62 | 6868672.64
CZ09 | cDXOH | New Construction | Heating | 0 | 3253125.58
CZ09 | cDXOH | New Construction | Cooling | 1119045.6 | 0
CZ09 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ09 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ09 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ09 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ09 | cDXOH | New Construction | Fans | 3062892.65 | 0
CZ09 | cDXOH | New Construction | Pumps | 1675.65 | 0
CZ09 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ09 | cDXOH | New Construction | Humidification | 0 | 0
CZ09 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ09 | cDXOH | New Construction | Water Systems | 0 | 541342.29
CZ09 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ09 | cDXOH | New Construction | Generators | 0 | 0
CZ09 | cDXOH | New Construction | Total End Uses | 10452337.62 | 6442508.29
CZ10 | cDXOH | New Construction | Heating | 0 | 4728800.98
CZ10 | cDXOH | New Construction | Cooling | 1817269.81 | 0
CZ10 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ10 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ10 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ10 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ10 | cDXOH | New Construction | Fans | 2995986.26 | 0
CZ10 | cDXOH | New Construction | Pumps | 1697.01 | 0
CZ10 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ10 | cDXOH | New Construction | Humidification | 0 | 0
CZ10 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ10 | cDXOH | New Construction | Water Systems | 0 | 536930.06
CZ10 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ10 | cDXOH | New Construction | Generators | 0 | 0
CZ10 | cDXOH | New Construction | Total End Uses | 11083676.81 | 7913771.45
CZ11 | cDXOH | New Construction | Heating | 0 | 7453560.33
CZ11 | cDXOH | New Construction | Cooling | 2187603.02 | 0
CZ11 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ11 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ11 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ11 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ11 | cDXOH | New Construction | Fans | 3106062.84 | 0
CZ11 | cDXOH | New Construction | Pumps | 1679.1 | 0
CZ11 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ11 | cDXOH | New Construction | Humidification | 0 | 0
CZ11 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ11 | cDXOH | New Construction | Water Systems | 0 | 548933.87
CZ11 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ11 | cDXOH | New Construction | Generators | 0 | 0
CZ11 | cDXOH | New Construction | Total End Uses | 11564068.69 | 10650534.61
CZ12 | cDXOH | New Construction | Heating | 0 | 7636554.93
CZ12 | cDXOH | New Construction | Cooling | 1607906.5 | 0
CZ12 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ12 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ12 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ12 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ12 | cDXOH | New Construction | Fans | 3098196.84 | 0
CZ12 | cDXOH | New Construction | Pumps | 1619.11 | 0
CZ12 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ12 | cDXOH | New Construction | Humidification | 0 | 0
CZ12 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ12 | cDXOH | New Construction | Water Systems | 0 | 564575.01
CZ12 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ12 | cDXOH | New Construction | Generators | 0 | 0
CZ12 | cDXOH | New Construction | Total End Uses | 10976446.18 | 10849170.35
CZ13 | cDXOH | New Construction | Heating | 0 | 6336775.68
CZ13 | cDXOH | New Construction | Cooling | 2443915.7 | 0
CZ13 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ13 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ13 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ13 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ13 | cDXOH | New Construction | Fans | 3105996.51 | 0
CZ13 | cDXOH | New Construction | Pumps | 1774.7 | 0
CZ13 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ13 | cDXOH | New Construction | Humidification | 0 | 0
CZ13 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ13 | cDXOH | New Construction | Water Systems | 0 | 532804.86
CZ13 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ13 | cDXOH | New Construction | Generators | 0 | 0
CZ13 | cDXOH | New Construction | Total End Uses | 11820410.64 | 9517620.95
CZ14 | cDXOH | New Construction | Heating | 0 | 5007221.81
CZ14 | cDXOH | New Construction | Cooling | 3324279.32 | 0
CZ14 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ14 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ14 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ14 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ14 | cDXOH | New Construction | Fans | 2979992.49 | 0
CZ14 | cDXOH | New Construction | Pumps | 1770.64 | 0
CZ14 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ14 | cDXOH | New Construction | Humidification | 0 | 0
CZ14 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ14 | cDXOH | New Construction | Water Systems | 0 | 505755.99
CZ14 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ14 | cDXOH | New Construction | Generators | 0 | 0
CZ14 | cDXOH | New Construction | Total End Uses | 12574766.18 | 8161018.2
CZ15 | cDXOH | New Construction | Heating | 0 | 2786575.29
CZ15 | cDXOH | New Construction | Cooling | 4703150.5 | 0
CZ15 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ15 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ15 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ15 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ15 | cDXOH | New Construction | Fans | 3232152.65 | 0
CZ15 | cDXOH | New Construction | Pumps | 1882.9 | 0
CZ15 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ15 | cDXOH | New Construction | Humidification | 0 | 0
CZ15 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ15 | cDXOH | New Construction | Water Systems | 0 | 448937.29
CZ15 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ15 | cDXOH | New Construction | Generators | 0 | 0
CZ15 | cDXOH | New Construction | Total End Uses | 14205909.78 | 5883552.99
CZ16 | cDXOH | New Construction | Heating | 0 | 9001688.99
CZ16 | cDXOH | New Construction | Cooling | 1836409.71 | 0
CZ16 | cDXOH | New Construction | Interior Lighting | 1500585.11 | 0
CZ16 | cDXOH | New Construction | Exterior Lighting | 0 | 0
CZ16 | cDXOH | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ16 | cDXOH | New Construction | Exterior Equipment | 0 | 0
CZ16 | cDXOH | New Construction | Fans | 2703847.27 | 0
CZ16 | cDXOH | New Construction | Pumps | 1454.67 | 0
CZ16 | cDXOH | New Construction | Heat Rejection | 0 | 0
CZ16 | cDXOH | New Construction | Humidification | 0 | 0
CZ16 | cDXOH | New Construction | Heat Recovery | 0 | 0
CZ16 | cDXOH | New Construction | Water Systems | 0 | 597084.19
CZ16 | cDXOH | New Construction | Refrigeration | 0 | 0
CZ16 | cDXOH | New Construction | Generators | 0 | 0
CZ16 | cDXOH | New Construction | Total End Uses | 10810435.38 | 12246813.59
CZ01 | cPVVG | Existing | Heating | 0 | 14420202.77
CZ01 | cPVVG | Existing | Cooling | 90439.53 | 0
CZ01 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ01 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ01 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ01 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ01 | cPVVG | Existing | Fans | 2659512.08 | 0
CZ01 | cPVVG | Existing | Pumps | 1661.34 | 0
CZ01 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ01 | cPVVG | Existing | Humidification | 0 | 0
CZ01 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ01 | cPVVG | Existing | Water Systems | 0 | 660961.95
CZ01 | cPVVG | Existing | Refrigeration | 0 | 0
CZ01 | cPVVG | Existing | Generators | 0 | 0
CZ01 | cPVVG | Existing | Total End Uses | 9948035.08 | 17729205.13
CZ02 | cPVVG | Existing | Heating | 0 | 9578025.06
CZ02 | cPVVG | Existing | Cooling | 674726.6 | 0
CZ02 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ02 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ02 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ02 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ02 | cPVVG | Existing | Fans | 2759874.16 | 0
CZ02 | cPVVG | Existing | Pumps | 1879.77 | 0
CZ02 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ02 | cPVVG | Existing | Humidification | 0 | 0
CZ02 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ02 | cPVVG | Existing | Water Systems | 0 | 607368.46
CZ02 | cPVVG | Existing | Refrigeration | 0 | 0
CZ02 | cPVVG | Existing | Generators | 0 | 0
CZ02 | cPVVG | Existing | Total End Uses | 10632902.67 | 12833433.94
CZ03 | cPVVG | Existing | Heating | 0 | 7797199.32
CZ03 | cPVVG | Existing | Cooling | 351922.24 | 0
CZ03 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ03 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ03 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ03 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ03 | cPVVG | Existing | Fans | 2711261.35 | 0
CZ03 | cPVVG | Existing | Pumps | 1888.04 | 0
CZ03 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ03 | cPVVG | Existing | Humidification | 0 | 0
CZ03 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ03 | cPVVG | Existing | Water Systems | 0 | 605001.35
CZ03 | cPVVG | Existing | Refrigeration | 0 | 0
CZ03 | cPVVG | Existing | Generators | 0 | 0
CZ03 | cPVVG | Existing | Total End Uses | 10261493.76 | 11050241.08
CZ04 | cPVVG | Existing | Heating | 0 | 6870538.26
CZ04 | cPVVG | Existing | Cooling | 828039.97 | 0
CZ04 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ04 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ04 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ04 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ04 | cPVVG | Existing | Fans | 2782088.97 | 0
CZ04 | cPVVG | Existing | Pumps | 1942.21 | 0
CZ04 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ04 | cPVVG | Existing | Humidification | 0 | 0
CZ04 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ04 | cPVVG | Existing | Water Systems | 0 | 584243.37
CZ04 | cPVVG | Existing | Refrigeration | 0 | 0
CZ04 | cPVVG | Existing | Generators | 0 | 0
CZ04 | cPVVG | Existing | Total End Uses | 10808493.28 | 10102822.04
CZ05 | cPVVG | Existing | Heating | 0 | 8074552.58
CZ05 | cPVVG | Existing | Cooling | 454214.32 | 0
CZ05 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ05 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ05 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ05 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ05 | cPVVG | Existing | Fans | 2693557.95 | 0
CZ05 | cPVVG | Existing | Pumps | 1789.34 | 0
CZ05 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ05 | cPVVG | Existing | Humidification | 0 | 0
CZ05 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ05 | cPVVG | Existing | Water Systems | 0 | 605012.35
CZ05 | cPVVG | Existing | Refrigeration | 0 | 0
CZ05 | cPVVG | Existing | Generators | 0 | 0
CZ05 | cPVVG | Existing | Total End Uses | 10345983.75 | 11327605.34
CZ06 | cPVVG | Existing | Heating | 0 | 3023882.21
CZ06 | cPVVG | Existing | Cooling | 734761 | 0
CZ06 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ06 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ06 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ06 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ06 | cPVVG | Existing | Fans | 2734252.45 | 0
CZ06 | cPVVG | Existing | Pumps | 1951.15 | 0
CZ06 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ06 | cPVVG | Existing | Humidification | 0 | 0
CZ06 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ06 | cPVVG | Existing | Water Systems | 0 | 557318.96
CZ06 | cPVVG | Existing | Refrigeration | 0 | 0
CZ06 | cPVVG | Existing | Generators | 0 | 0
CZ06 | cPVVG | Existing | Total End Uses | 10667386.74 | 6229241.58
CZ07 | cPVVG | Existing | Heating | 0 | 2823020.11
CZ07 | cPVVG | Existing | Cooling | 859362.42 | 0
CZ07 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ07 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ07 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ07 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ07 | cPVVG | Existing | Fans | 2792616.78 | 0
CZ07 | cPVVG | Existing | Pumps | 2006.91 | 0
CZ07 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ07 | cPVVG | Existing | Humidification | 0 | 0
CZ07 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ07 | cPVVG | Existing | Water Systems | 0 | 550197.57
CZ07 | cPVVG | Existing | Refrigeration | 0 | 0
CZ07 | cPVVG | Existing | Generators | 0 | 0
CZ07 | cPVVG | Existing | Total End Uses | 10850408.24 | 6021258.09
CZ08 | cPVVG | Existing | Heating | 0 | 3556067.37
CZ08 | cPVVG | Existing | Cooling | 1118685.03 | 0
CZ08 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ08 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ08 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ08 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ08 | cPVVG | Existing | Fans | 2820050.88 | 0
CZ08 | cPVVG | Existing | Pumps | 2048.92 | 0
CZ08 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ08 | cPVVG | Existing | Humidification | 0 | 0
CZ08 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ08 | cPVVG | Existing | Water Systems | 0 | 549442.54
CZ08 | cPVVG | Existing | Refrigeration | 0 | 0
CZ08 | cPVVG | Existing | Generators | 0 | 0
CZ08 | cPVVG | Existing | Total End Uses | 11137206.96 | 6753550.32
CZ09 | cPVVG | Existing | Heating | 0 | 3149476.76
CZ09 | cPVVG | Existing | Cooling | 1298496.64 | 0
CZ09 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ09 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ09 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ09 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ09 | cPVVG | Existing | Fans | 2833121.89 | 0
CZ09 | cPVVG | Existing | Pumps | 2075.44 | 0
CZ09 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ09 | cPVVG | Existing | Humidification | 0 | 0
CZ09 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ09 | cPVVG | Existing | Water Systems | 0 | 541823.06
CZ09 | cPVVG | Existing | Refrigeration | 0 | 0
CZ09 | cPVVG | Existing | Generators | 0 | 0
CZ09 | cPVVG | Existing | Total End Uses | 11330116.1 | 6339340.23
CZ10 | cPVVG | Existing | Heating | 0 | 4717716.26
CZ10 | cPVVG | Existing | Cooling | 2009497.22 | 0
CZ10 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ10 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ10 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ10 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ10 | cPVVG | Existing | Fans | 2752859.07 | 0
CZ10 | cPVVG | Existing | Pumps | 2101.08 | 0
CZ10 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ10 | cPVVG | Existing | Humidification | 0 | 0
CZ10 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ10 | cPVVG | Existing | Water Systems | 0 | 537463.04
CZ10 | cPVVG | Existing | Refrigeration | 0 | 0
CZ10 | cPVVG | Existing | Generators | 0 | 0
CZ10 | cPVVG | Existing | Total End Uses | 11960879.5 | 7903219.71
CZ11 | cPVVG | Existing | Heating | 0 | 7783132.82
CZ11 | cPVVG | Existing | Cooling | 2410109.4 | 0
CZ11 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ11 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ11 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ11 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ11 | cPVVG | Existing | Fans | 2877628.15 | 0
CZ11 | cPVVG | Existing | Pumps | 2089.61 | 0
CZ11 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ11 | cPVVG | Existing | Humidification | 0 | 0
CZ11 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ11 | cPVVG | Existing | Water Systems | 0 | 549485.1
CZ11 | cPVVG | Existing | Refrigeration | 0 | 0
CZ11 | cPVVG | Existing | Generators | 0 | 0
CZ11 | cPVVG | Existing | Total End Uses | 12486249.29 | 10980658.33
CZ12 | cPVVG | Existing | Heating | 0 | 7873864.43
CZ12 | cPVVG | Existing | Cooling | 1783536.09 | 0
CZ12 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ12 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ12 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ12 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ12 | cPVVG | Existing | Fans | 2859478.65 | 0
CZ12 | cPVVG | Existing | Pumps | 2027.79 | 0
CZ12 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ12 | cPVVG | Existing | Humidification | 0 | 0
CZ12 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ12 | cPVVG | Existing | Water Systems | 0 | 564940.74
CZ12 | cPVVG | Existing | Refrigeration | 0 | 0
CZ12 | cPVVG | Existing | Generators | 0 | 0
CZ12 | cPVVG | Existing | Total End Uses | 11841464.66 | 11086845.58
CZ13 | cPVVG | Existing | Heating | 0 | 6550463.64
CZ13 | cPVVG | Existing | Cooling | 2705209.62 | 0
CZ13 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ13 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ13 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ13 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ13 | cPVVG | Existing | Fans | 2890904.76 | 0
CZ13 | cPVVG | Existing | Pumps | 2184.86 | 0
CZ13 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ13 | cPVVG | Existing | Humidification | 0 | 0
CZ13 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ13 | cPVVG | Existing | Water Systems | 0 | 533490.66
CZ13 | cPVVG | Existing | Refrigeration | 0 | 0
CZ13 | cPVVG | Existing | Generators | 0 | 0
CZ13 | cPVVG | Existing | Total End Uses | 12794721.36 | 9731994.71
CZ14 | cPVVG | Existing | Heating | 0 | 5126232.9
CZ14 | cPVVG | Existing | Cooling | 3636537.82 | 0
CZ14 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ14 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ14 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ14 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ14 | cPVVG | Existing | Fans | 2780658.27 | 0
CZ14 | cPVVG | Existing | Pumps | 2181.05 | 0
CZ14 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ14 | cPVVG | Existing | Humidification | 0 | 0
CZ14 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ14 | cPVVG | Existing | Water Systems | 0 | 506424.14
CZ14 | cPVVG | Existing | Refrigeration | 0 | 0
CZ14 | cPVVG | Existing | Generators | 0 | 0
CZ14 | cPVVG | Existing | Total End Uses | 13615799.27 | 8280697.45
CZ15 | cPVVG | Existing | Heating | 0 | 2708940.6
CZ15 | cPVVG | Existing | Cooling | 5113696.77 | 0
CZ15 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ15 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ15 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ15 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ15 | cPVVG | Existing | Fans | 3083279.33 | 0
CZ15 | cPVVG | Existing | Pumps | 2326.49 | 0
CZ15 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ15 | cPVVG | Existing | Humidification | 0 | 0
CZ15 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ15 | cPVVG | Existing | Water Systems | 0 | 449554.45
CZ15 | cPVVG | Existing | Refrigeration | 0 | 0
CZ15 | cPVVG | Existing | Generators | 0 | 0
CZ15 | cPVVG | Existing | Total End Uses | 15395724.73 | 5806535.46
CZ16 | cPVVG | Existing | Heating | 0 | 9593155.34
CZ16 | cPVVG | Existing | Cooling | 2037292.47 | 0
CZ16 | cPVVG | Existing | Interior Lighting | 2428283.52 | 0
CZ16 | cPVVG | Existing | Exterior Lighting | 0 | 0
CZ16 | cPVVG | Existing | Interior Equipment | 4768138.62 | 2648040.41
CZ16 | cPVVG | Existing | Exterior Equipment | 0 | 0
CZ16 | cPVVG | Existing | Fans | 2382978.89 | 0
CZ16 | cPVVG | Existing | Pumps | 1860.08 | 0
CZ16 | cPVVG | Existing | Heat Rejection | 0 | 0
CZ16 | cPVVG | Existing | Humidification | 0 | 0
CZ16 | cPVVG | Existing | Heat Recovery | 0 | 0
CZ16 | cPVVG | Existing | Water Systems | 0 | 597407.6
CZ16 | cPVVG | Existing | Refrigeration | 0 | 0
CZ16 | cPVVG | Existing | Generators | 0 | 0
CZ16 | cPVVG | Existing | Total End Uses | 11618553.58 | 12838603.35
CZ01 | cPVVG | New Construction | Heating | 0 | 14707253.95
CZ01 | cPVVG | New Construction | Cooling | 83758.61 | 0
CZ01 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ01 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ01 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ01 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ01 | cPVVG | New Construction | Fans | 2607461.39 | 0
CZ01 | cPVVG | New Construction | Pumps | 1398.55 | 0
CZ01 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ01 | cPVVG | New Construction | Humidification | 0 | 0
CZ01 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ01 | cPVVG | New Construction | Water Systems | 0 | 660767.67
CZ01 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ01 | cPVVG | New Construction | Generators | 0 | 0
CZ01 | cPVVG | New Construction | Total End Uses | 8961342.27 | 18016062.03
CZ02 | cPVVG | New Construction | Heating | 0 | 9865035.39
CZ02 | cPVVG | New Construction | Cooling | 592489.22 | 0
CZ02 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ02 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ02 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ02 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ02 | cPVVG | New Construction | Fans | 2654735.15 | 0
CZ02 | cPVVG | New Construction | Pumps | 1540.98 | 0
CZ02 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ02 | cPVVG | New Construction | Humidification | 0 | 0
CZ02 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ02 | cPVVG | New Construction | Water Systems | 0 | 607082.02
CZ02 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ02 | cPVVG | New Construction | Generators | 0 | 0
CZ02 | cPVVG | New Construction | Total End Uses | 9517489.08 | 13120157.81
CZ03 | cPVVG | New Construction | Heating | 0 | 8160996.08
CZ03 | cPVVG | New Construction | Cooling | 299803.75 | 0
CZ03 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ03 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ03 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ03 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ03 | cPVVG | New Construction | Fans | 2625528.13 | 0
CZ03 | cPVVG | New Construction | Pumps | 1569.03 | 0
CZ03 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ03 | cPVVG | New Construction | Humidification | 0 | 0
CZ03 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ03 | cPVVG | New Construction | Water Systems | 0 | 604736.18
CZ03 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ03 | cPVVG | New Construction | Generators | 0 | 0
CZ03 | cPVVG | New Construction | Total End Uses | 9195624.65 | 11413772.67
CZ04 | cPVVG | New Construction | Heating | 0 | 7173822.46
CZ04 | cPVVG | New Construction | Cooling | 717558.89 | 0
CZ04 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ04 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ04 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ04 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ04 | cPVVG | New Construction | Fans | 2667821.14 | 0
CZ04 | cPVVG | New Construction | Pumps | 1586.11 | 0
CZ04 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ04 | cPVVG | New Construction | Humidification | 0 | 0
CZ04 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ04 | cPVVG | New Construction | Water Systems | 0 | 583886.91
CZ04 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ04 | cPVVG | New Construction | Generators | 0 | 0
CZ04 | cPVVG | New Construction | Total End Uses | 9655689.86 | 10405749.79
CZ05 | cPVVG | New Construction | Heating | 0 | 8462412.99
CZ05 | cPVVG | New Construction | Cooling | 391410.69 | 0
CZ05 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ05 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ05 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ05 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ05 | cPVVG | New Construction | Fans | 2603582.44 | 0
CZ05 | cPVVG | New Construction | Pumps | 1454.39 | 0
CZ05 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ05 | cPVVG | New Construction | Humidification | 0 | 0
CZ05 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ05 | cPVVG | New Construction | Water Systems | 0 | 604756.28
CZ05 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ05 | cPVVG | New Construction | Generators | 0 | 0
CZ05 | cPVVG | New Construction | Total End Uses | 9265171.25 | 11715209.68
CZ06 | cPVVG | New Construction | Heating | 0 | 3261092.07
CZ06 | cPVVG | New Construction | Cooling | 607506.49 | 0
CZ06 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ06 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ06 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ06 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ06 | cPVVG | New Construction | Fans | 2620550.46 | 0
CZ06 | cPVVG | New Construction | Pumps | 1584.46 | 0
CZ06 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ06 | cPVVG | New Construction | Humidification | 0 | 0
CZ06 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ06 | cPVVG | New Construction | Water Systems | 0 | 556891.17
CZ06 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ06 | cPVVG | New Construction | Generators | 0 | 0
CZ06 | cPVVG | New Construction | Total End Uses | 9498365.14 | 6466023.65
CZ07 | cPVVG | New Construction | Heating | 0 | 3030854.41
CZ07 | cPVVG | New Construction | Cooling | 711748.99 | 0
CZ07 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ07 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ07 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ07 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ07 | cPVVG | New Construction | Fans | 2680961.62 | 0
CZ07 | cPVVG | New Construction | Pumps | 1646.38 | 0
CZ07 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ07 | cPVVG | New Construction | Humidification | 0 | 0
CZ07 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ07 | cPVVG | New Construction | Water Systems | 0 | 549812.12
CZ07 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ07 | cPVVG | New Construction | Generators | 0 | 0
CZ07 | cPVVG | New Construction | Total End Uses | 9663080.71 | 6228706.93
CZ08 | cPVVG | New Construction | Heating | 0 | 3779517.39
CZ08 | cPVVG | New Construction | Cooling | 957653.95 | 0
CZ08 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ08 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ08 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ08 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ08 | cPVVG | New Construction | Fans | 2692539.88 | 0
CZ08 | cPVVG | New Construction | Pumps | 1660.82 | 0
CZ08 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ08 | cPVVG | New Construction | Humidification | 0 | 0
CZ08 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ08 | cPVVG | New Construction | Water Systems | 0 | 548972.19
CZ08 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ08 | cPVVG | New Construction | Generators | 0 | 0
CZ08 | cPVVG | New Construction | Total End Uses | 9920578.39 | 6976529.99
CZ09 | cPVVG | New Construction | Heating | 0 | 3344187.57
CZ09 | cPVVG | New Construction | Cooling | 1103437.26 | 0
CZ09 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ09 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ09 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ09 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ09 | cPVVG | New Construction | Fans | 2680028.02 | 0
CZ09 | cPVVG | New Construction | Pumps | 1674.6 | 0
CZ09 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ09 | cPVVG | New Construction | Humidification | 0 | 0
CZ09 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ09 | cPVVG | New Construction | Water Systems | 0 | 541312.31
CZ09 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ09 | cPVVG | New Construction | Generators | 0 | 0
CZ09 | cPVVG | New Construction | Total End Uses | 10053863.61 | 6533540.29
CZ10 | cPVVG | New Construction | Heating | 0 | 4918720.44
CZ10 | cPVVG | New Construction | Cooling | 1795944.16 | 0
CZ10 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ10 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ10 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ10 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ10 | cPVVG | New Construction | Fans | 2612364.55 | 0
CZ10 | cPVVG | New Construction | Pumps | 1696.16 | 0
CZ10 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ10 | cPVVG | New Construction | Humidification | 0 | 0
CZ10 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ10 | cPVVG | New Construction | Water Systems | 0 | 536963.03
CZ10 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ10 | cPVVG | New Construction | Generators | 0 | 0
CZ10 | cPVVG | New Construction | Total End Uses | 10678728.59 | 8103723.89
CZ11 | cPVVG | New Construction | Heating | 0 | 7920101.62
CZ11 | cPVVG | New Construction | Cooling | 2169340.19 | 0
CZ11 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ11 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ11 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ11 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ11 | cPVVG | New Construction | Fans | 2707227.5 | 0
CZ11 | cPVVG | New Construction | Pumps | 1685.6 | 0
CZ11 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ11 | cPVVG | New Construction | Humidification | 0 | 0
CZ11 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ11 | cPVVG | New Construction | Water Systems | 0 | 548940.05
CZ11 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ11 | cPVVG | New Construction | Generators | 0 | 0
CZ11 | cPVVG | New Construction | Total End Uses | 11146977.03 | 11117082.09
CZ12 | cPVVG | New Construction | Heating | 0 | 8075260.84
CZ12 | cPVVG | New Construction | Cooling | 1594066.62 | 0
CZ12 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ12 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ12 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ12 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ12 | cPVVG | New Construction | Fans | 2721689.7 | 0
CZ12 | cPVVG | New Construction | Pumps | 1626.18 | 0
CZ12 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ12 | cPVVG | New Construction | Humidification | 0 | 0
CZ12 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ12 | cPVVG | New Construction | Water Systems | 0 | 564522.95
CZ12 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ12 | cPVVG | New Construction | Generators | 0 | 0
CZ12 | cPVVG | New Construction | Total End Uses | 10586106.23 | 11287824.2
CZ13 | cPVVG | New Construction | Heating | 0 | 6707707.59
CZ13 | cPVVG | New Construction | Cooling | 2422376.22 | 0
CZ13 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ13 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ13 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ13 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ13 | cPVVG | New Construction | Fans | 2722036.38 | 0
CZ13 | cPVVG | New Construction | Pumps | 1778.17 | 0
CZ13 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ13 | cPVVG | New Construction | Humidification | 0 | 0
CZ13 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ13 | cPVVG | New Construction | Water Systems | 0 | 532860.14
CZ13 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ13 | cPVVG | New Construction | Generators | 0 | 0
CZ13 | cPVVG | New Construction | Total End Uses | 11414914.49 | 9888608.14
CZ14 | cPVVG | New Construction | Heating | 0 | 5280131.63
CZ14 | cPVVG | New Construction | Cooling | 3294209.95 | 0
CZ14 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ14 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ14 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ14 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ14 | cPVVG | New Construction | Fans | 2582838.63 | 0
CZ14 | cPVVG | New Construction | Pumps | 1772.65 | 0
CZ14 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ14 | cPVVG | New Construction | Humidification | 0 | 0
CZ14 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ14 | cPVVG | New Construction | Water Systems | 0 | 505709.22
CZ14 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ14 | cPVVG | New Construction | Generators | 0 | 0
CZ14 | cPVVG | New Construction | Total End Uses | 12147544.96 | 8433881.26
CZ15 | cPVVG | New Construction | Heating | 0 | 2870732.17
CZ15 | cPVVG | New Construction | Cooling | 4662215.85 | 0
CZ15 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ15 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ15 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ15 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ15 | cPVVG | New Construction | Fans | 2883073.02 | 0
CZ15 | cPVVG | New Construction | Pumps | 1882.74 | 0
CZ15 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ15 | cPVVG | New Construction | Humidification | 0 | 0
CZ15 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ15 | cPVVG | New Construction | Water Systems | 0 | 448838.92
CZ15 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ15 | cPVVG | New Construction | Generators | 0 | 0
CZ15 | cPVVG | New Construction | Total End Uses | 13815895.34 | 5967611.49
CZ16 | cPVVG | New Construction | Heating | 0 | 9719110.97
CZ16 | cPVVG | New Construction | Cooling | 1821914.17 | 0
CZ16 | cPVVG | New Construction | Interior Lighting | 1500585.11 | 0
CZ16 | cPVVG | New Construction | Exterior Lighting | 0 | 0
CZ16 | cPVVG | New Construction | Interior Equipment | 4768138.62 | 2648040.41
CZ16 | cPVVG | New Construction | Exterior Equipment | 0 | 0
CZ16 | cPVVG | New Construction | Fans | 2251083.36 | 0
CZ16 | cPVVG | New Construction | Pumps | 1492.87 | 0
CZ16 | cPVVG | New Construction | Heat Rejection | 0 | 0
CZ16 | cPVVG | New Construction | Humidification | 0 | 0
CZ16 | cPVVG | New Construction | Heat Recovery | 0 | 0
CZ16 | cPVVG | New Construction | Water Systems | 0 | 597036.12
CZ16 | cPVVG | New Construction | Refrigeration | 0 | 0
CZ16 | cPVVG | New Construction | Generators | 0 | 0
CZ16 | cPVVG | New Construction | Total End Uses | 10343214.13 | 12964187.5

## Raw_endusebreakdownannual (hidden)
Vintage | Climate Zone | HVAC System | End Use | Electricity [kBtu] | Natural Gas [kBtu]
Existing | CZ01 | cAVVG | Heating | 0 | 14803653.51
Existing | CZ01 | cAVVG | Cooling | 80746.9 | 0
Existing | CZ01 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ01 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ01 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ01 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ01 | cAVVG | Fans | 2581957.48 | 0
Existing | CZ01 | cAVVG | Pumps | 10063.94 | 0
Existing | CZ01 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ01 | cAVVG | Humidification | 0 | 0
Existing | CZ01 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ01 | cAVVG | Water Systems | 0 | 660996.33
Existing | CZ01 | cAVVG | Refrigeration | 0 | 0
Existing | CZ01 | cAVVG | Generators | 0 | 0
Existing | CZ01 | cAVVG | Total End Uses | 9869190.45 | 18112690.25
Existing | CZ02 | cAVVG | Heating | 0 | 9843179.94
Existing | CZ02 | cAVVG | Cooling | 732770.81 | 0
Existing | CZ02 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ02 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ02 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ02 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ02 | cAVVG | Fans | 2631707.63 | 0
Existing | CZ02 | cAVVG | Pumps | 23101.67 | 0
Existing | CZ02 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ02 | cAVVG | Humidification | 0 | 0
Existing | CZ02 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ02 | cAVVG | Water Systems | 0 | 607375.32
Existing | CZ02 | cAVVG | Refrigeration | 0 | 0
Existing | CZ02 | cAVVG | Generators | 0 | 0
Existing | CZ02 | cAVVG | Total End Uses | 10584002.24 | 13098595.67
Existing | CZ03 | cAVVG | Heating | 0 | 7965218.98
Existing | CZ03 | cAVVG | Cooling | 395971.24 | 0
Existing | CZ03 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ03 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ03 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ03 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ03 | cAVVG | Fans | 2598689.54 | 0
Existing | CZ03 | cAVVG | Pumps | 22553.53 | 0
Existing | CZ03 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ03 | cAVVG | Humidification | 0 | 0
Existing | CZ03 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ03 | cAVVG | Water Systems | 0 | 604994.87
Existing | CZ03 | cAVVG | Refrigeration | 0 | 0
Existing | CZ03 | cAVVG | Generators | 0 | 0
Existing | CZ03 | cAVVG | Total End Uses | 10213636.44 | 11218254.26
Existing | CZ04 | cAVVG | Heating | 0 | 7047886.43
Existing | CZ04 | cAVVG | Cooling | 891925.54 | 0
Existing | CZ04 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ04 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ04 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ04 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ04 | cAVVG | Fans | 2654841.18 | 0
Existing | CZ04 | cAVVG | Pumps | 25381.16 | 0
Existing | CZ04 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ04 | cAVVG | Humidification | 0 | 0
Existing | CZ04 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ04 | cAVVG | Water Systems | 0 | 584219.24
Existing | CZ04 | cAVVG | Refrigeration | 0 | 0
Existing | CZ04 | cAVVG | Generators | 0 | 0
Existing | CZ04 | cAVVG | Total End Uses | 10768570.01 | 10280146.08
Existing | CZ05 | cAVVG | Heating | 0 | 8255729.69
Existing | CZ05 | cAVVG | Cooling | 498060.47 | 0
Existing | CZ05 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ05 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ05 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ05 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ05 | cAVVG | Fans | 2580499.22 | 0
Existing | CZ05 | cAVVG | Pumps | 21522.55 | 0
Existing | CZ05 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ05 | cAVVG | Humidification | 0 | 0
Existing | CZ05 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ05 | cAVVG | Water Systems | 0 | 605046.98
Existing | CZ05 | cAVVG | Refrigeration | 0 | 0
Existing | CZ05 | cAVVG | Generators | 0 | 0
Existing | CZ05 | cAVVG | Total End Uses | 10296504.37 | 11508817.08
Existing | CZ06 | cAVVG | Heating | 0 | 3092473.26
Existing | CZ06 | cAVVG | Cooling | 847222.41 | 0
Existing | CZ06 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ06 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ06 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ06 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ06 | cAVVG | Fans | 2651118.86 | 0
Existing | CZ06 | cAVVG | Pumps | 33328.12 | 0
Existing | CZ06 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ06 | cAVVG | Humidification | 0 | 0
Existing | CZ06 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ06 | cAVVG | Water Systems | 0 | 557316.25
Existing | CZ06 | cAVVG | Refrigeration | 0 | 0
Existing | CZ06 | cAVVG | Generators | 0 | 0
Existing | CZ06 | cAVVG | Total End Uses | 10728091.51 | 6297829.92
Existing | CZ07 | cAVVG | Heating | 0 | 2895792.23
Existing | CZ07 | cAVVG | Cooling | 988452.61 | 0
Existing | CZ07 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ07 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ07 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ07 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ07 | cAVVG | Fans | 2727334.29 | 0
Existing | CZ07 | cAVVG | Pumps | 36127.78 | 0
Existing | CZ07 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ07 | cAVVG | Humidification | 0 | 0
Existing | CZ07 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ07 | cAVVG | Water Systems | 0 | 550191.89
Existing | CZ07 | cAVVG | Refrigeration | 0 | 0
Existing | CZ07 | cAVVG | Generators | 0 | 0
Existing | CZ07 | cAVVG | Total End Uses | 10948336.81 | 6094024.53
Existing | CZ08 | cAVVG | Heating | 0 | 3659940.42
Existing | CZ08 | cAVVG | Cooling | 1236213.67 | 0
Existing | CZ08 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ08 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ08 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ08 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ08 | cAVVG | Fans | 2703721.65 | 0
Existing | CZ08 | cAVVG | Pumps | 32009.19 | 0
Existing | CZ08 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ08 | cAVVG | Humidification | 0 | 0
Existing | CZ08 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ08 | cAVVG | Water Systems | 0 | 549428.74
Existing | CZ08 | cAVVG | Refrigeration | 0 | 0
Existing | CZ08 | cAVVG | Generators | 0 | 0
Existing | CZ08 | cAVVG | Total End Uses | 11168366.65 | 6857409.58
Existing | CZ09 | cAVVG | Heating | 0 | 3254143.09
Existing | CZ09 | cAVVG | Cooling | 1473191.78 | 0
Existing | CZ09 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ09 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ09 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ09 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ09 | cAVVG | Fans | 2739838.63 | 0
Existing | CZ09 | cAVVG | Pumps | 40269.18 | 0
Existing | CZ09 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ09 | cAVVG | Humidification | 0 | 0
Existing | CZ09 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ09 | cAVVG | Water Systems | 0 | 541811.71
Existing | CZ09 | cAVVG | Refrigeration | 0 | 0
Existing | CZ09 | cAVVG | Generators | 0 | 0
Existing | CZ09 | cAVVG | Total End Uses | 11449721.72 | 6443995.22
Existing | CZ10 | cAVVG | Heating | 0 | 4864908.63
Existing | CZ10 | cAVVG | Cooling | 2150137.97 | 0
Existing | CZ10 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ10 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ10 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ10 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ10 | cAVVG | Fans | 2640119.52 | 0
Existing | CZ10 | cAVVG | Pumps | 33883.98 | 0
Existing | CZ10 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ10 | cAVVG | Humidification | 0 | 0
Existing | CZ10 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ10 | cAVVG | Water Systems | 0 | 537463.77
Existing | CZ10 | cAVVG | Refrigeration | 0 | 0
Existing | CZ10 | cAVVG | Generators | 0 | 0
Existing | CZ10 | cAVVG | Total End Uses | 12020563.6 | 8050412.8
Existing | CZ11 | cAVVG | Heating | 0 | 8048333.3
Existing | CZ11 | cAVVG | Cooling | 2553081.65 | 0
Existing | CZ11 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ11 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ11 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ11 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ11 | cAVVG | Fans | 2748090.94 | 0
Existing | CZ11 | cAVVG | Pumps | 32357.6 | 0
Existing | CZ11 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ11 | cAVVG | Humidification | 0 | 0
Existing | CZ11 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ11 | cAVVG | Water Systems | 0 | 549467.74
Existing | CZ11 | cAVVG | Refrigeration | 0 | 0
Existing | CZ11 | cAVVG | Generators | 0 | 0
Existing | CZ11 | cAVVG | Total End Uses | 12529952.32 | 11245841.46
Existing | CZ12 | cAVVG | Heating | 0 | 8101253.35
Existing | CZ12 | cAVVG | Cooling | 1902582.69 | 0
Existing | CZ12 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ12 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ12 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ12 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ12 | cAVVG | Fans | 2740270.62 | 0
Existing | CZ12 | cAVVG | Pumps | 31389.22 | 0
Existing | CZ12 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ12 | cAVVG | Humidification | 0 | 0
Existing | CZ12 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ12 | cAVVG | Water Systems | 0 | 564941.48
Existing | CZ12 | cAVVG | Refrigeration | 0 | 0
Existing | CZ12 | cAVVG | Generators | 0 | 0
Existing | CZ12 | cAVVG | Total End Uses | 11870664.66 | 11314235.24
Existing | CZ13 | cAVVG | Heating | 0 | 6740982.39
Existing | CZ13 | cAVVG | Cooling | 2860986.99 | 0
Existing | CZ13 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ13 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ13 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ13 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ13 | cAVVG | Fans | 2790956.7 | 0
Existing | CZ13 | cAVVG | Pumps | 35845.14 | 0
Existing | CZ13 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ13 | cAVVG | Humidification | 0 | 0
Existing | CZ13 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ13 | cAVVG | Water Systems | 0 | 533497.77
Existing | CZ13 | cAVVG | Refrigeration | 0 | 0
Existing | CZ13 | cAVVG | Generators | 0 | 0
Existing | CZ13 | cAVVG | Total End Uses | 12884210.97 | 9922520.57
Existing | CZ14 | cAVVG | Heating | 0 | 5300915.77
Existing | CZ14 | cAVVG | Cooling | 3846219.18 | 0
Existing | CZ14 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ14 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ14 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ14 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ14 | cAVVG | Fans | 2705598.17 | 0
Existing | CZ14 | cAVVG | Pumps | 46264.91 | 0
Existing | CZ14 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ14 | cAVVG | Humidification | 0 | 0
Existing | CZ14 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ14 | cAVVG | Water Systems | 0 | 506434.16
Existing | CZ14 | cAVVG | Refrigeration | 0 | 0
Existing | CZ14 | cAVVG | Generators | 0 | 0
Existing | CZ14 | cAVVG | Total End Uses | 13794504.39 | 8455390.34
Existing | CZ15 | cAVVG | Heating | 0 | 2831353.79
Existing | CZ15 | cAVVG | Cooling | 5441389.1 | 0
Existing | CZ15 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ15 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ15 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ15 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ15 | cAVVG | Fans | 2969787.75 | 0
Existing | CZ15 | cAVVG | Pumps | 45090.06 | 0
Existing | CZ15 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ15 | cAVVG | Humidification | 0 | 0
Existing | CZ15 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ15 | cAVVG | Water Systems | 0 | 449539
Existing | CZ15 | cAVVG | Refrigeration | 0 | 0
Existing | CZ15 | cAVVG | Generators | 0 | 0
Existing | CZ15 | cAVVG | Total End Uses | 15652689.04 | 5928933.2
Existing | CZ16 | cAVVG | Heating | 0 | 9911648.26
Existing | CZ16 | cAVVG | Cooling | 2136285.66 | 0
Existing | CZ16 | cAVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ16 | cAVVG | Exterior Lighting | 0 | 0
Existing | CZ16 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ16 | cAVVG | Exterior Equipment | 0 | 0
Existing | CZ16 | cAVVG | Fans | 2251412.51 | 0
Existing | CZ16 | cAVVG | Pumps | 31449.91 | 0
Existing | CZ16 | cAVVG | Heat Rejection | 0 | 0
Existing | CZ16 | cAVVG | Humidification | 0 | 0
Existing | CZ16 | cAVVG | Heat Recovery | 0 | 0
Existing | CZ16 | cAVVG | Water Systems | 0 | 597407.1
Existing | CZ16 | cAVVG | Refrigeration | 0 | 0
Existing | CZ16 | cAVVG | Generators | 0 | 0
Existing | CZ16 | cAVVG | Total End Uses | 11615570.22 | 13157095.78
New Construction | CZ01 | cAVVG | Heating | 0 | 15227554.78
New Construction | CZ01 | cAVVG | Cooling | 78408.85 | 0
New Construction | CZ01 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ01 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ01 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ01 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ01 | cAVVG | Fans | 2539815.19 | 0
New Construction | CZ01 | cAVVG | Pumps | 7900.42 | 0
New Construction | CZ01 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ01 | cAVVG | Humidification | 0 | 0
New Construction | CZ01 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ01 | cAVVG | Water Systems | 0 | 660803.04
New Construction | CZ01 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ01 | cAVVG | Generators | 0 | 0
New Construction | CZ01 | cAVVG | Total End Uses | 8894848.2 | 18536398.23
New Construction | CZ02 | cAVVG | Heating | 0 | 10182254.17
New Construction | CZ02 | cAVVG | Cooling | 646256.83 | 0
New Construction | CZ02 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ02 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ02 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ02 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ02 | cAVVG | Fans | 2571482.12 | 0
New Construction | CZ02 | cAVVG | Pumps | 17782.86 | 0
New Construction | CZ02 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ02 | cAVVG | Humidification | 0 | 0
New Construction | CZ02 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ02 | cAVVG | Water Systems | 0 | 607107.29
New Construction | CZ02 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ02 | cAVVG | Generators | 0 | 0
New Construction | CZ02 | cAVVG | Total End Uses | 9504245.54 | 13437401.87
New Construction | CZ03 | cAVVG | Heating | 0 | 8396358.4
New Construction | CZ03 | cAVVG | Cooling | 343892.9 | 0
New Construction | CZ03 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ03 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ03 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ03 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ03 | cAVVG | Fans | 2551140.51 | 0
New Construction | CZ03 | cAVVG | Pumps | 17888.91 | 0
New Construction | CZ03 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ03 | cAVVG | Humidification | 0 | 0
New Construction | CZ03 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ03 | cAVVG | Water Systems | 0 | 604730.41
New Construction | CZ03 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ03 | cAVVG | Generators | 0 | 0
New Construction | CZ03 | cAVVG | Total End Uses | 9181646.05 | 11649129.23
New Construction | CZ04 | cAVVG | Heating | 0 | 7387092.59
New Construction | CZ04 | cAVVG | Cooling | 775104.17 | 0
New Construction | CZ04 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ04 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ04 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ04 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ04 | cAVVG | Fans | 2586085.66 | 0
New Construction | CZ04 | cAVVG | Pumps | 19498.39 | 0
New Construction | CZ04 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ04 | cAVVG | Humidification | 0 | 0
New Construction | CZ04 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ04 | cAVVG | Water Systems | 0 | 583908.58
New Construction | CZ04 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ04 | cAVVG | Generators | 0 | 0
New Construction | CZ04 | cAVVG | Total End Uses | 9649411.94 | 10619041.58
New Construction | CZ05 | cAVVG | Heating | 0 | 8731215.26
New Construction | CZ05 | cAVVG | Cooling | 436664.76 | 0
New Construction | CZ05 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ05 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ05 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ05 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ05 | cAVVG | Fans | 2530492.01 | 0
New Construction | CZ05 | cAVVG | Pumps | 16689.09 | 0
New Construction | CZ05 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ05 | cAVVG | Humidification | 0 | 0
New Construction | CZ05 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ05 | cAVVG | Water Systems | 0 | 604776.41
New Construction | CZ05 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ05 | cAVVG | Generators | 0 | 0
New Construction | CZ05 | cAVVG | Total End Uses | 9252569.59 | 11984032.08
New Construction | CZ06 | cAVVG | Heating | 0 | 3346061.51
New Construction | CZ06 | cAVVG | Cooling | 699156.36 | 0
New Construction | CZ06 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ06 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ06 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ06 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ06 | cAVVG | Fans | 2579134.64 | 0
New Construction | CZ06 | cAVVG | Pumps | 25630.82 | 0
New Construction | CZ06 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ06 | cAVVG | Humidification | 0 | 0
New Construction | CZ06 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ06 | cAVVG | Water Systems | 0 | 557006.84
New Construction | CZ06 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ06 | cAVVG | Generators | 0 | 0
New Construction | CZ06 | cAVVG | Total End Uses | 9572645.55 | 6551108.77
New Construction | CZ07 | cAVVG | Heating | 0 | 3118221.33
New Construction | CZ07 | cAVVG | Cooling | 794413.09 | 0
New Construction | CZ07 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ07 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ07 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ07 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ07 | cAVVG | Fans | 2612058.6 | 0
New Construction | CZ07 | cAVVG | Pumps | 23614.38 | 0
New Construction | CZ07 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ07 | cAVVG | Humidification | 0 | 0
New Construction | CZ07 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ07 | cAVVG | Water Systems | 0 | 549821.18
New Construction | CZ07 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ07 | cAVVG | Generators | 0 | 0
New Construction | CZ07 | cAVVG | Total End Uses | 9698809.79 | 6316082.92
New Construction | CZ08 | cAVVG | Heating | 0 | 3890293.02
New Construction | CZ08 | cAVVG | Cooling | 1051897.45 | 0
New Construction | CZ08 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ08 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ08 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ08 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ08 | cAVVG | Fans | 2618639.28 | 0
New Construction | CZ08 | cAVVG | Pumps | 24522.02 | 0
New Construction | CZ08 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ08 | cAVVG | Humidification | 0 | 0
New Construction | CZ08 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ08 | cAVVG | Water Systems | 0 | 548996.51
New Construction | CZ08 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ08 | cAVVG | Generators | 0 | 0
New Construction | CZ08 | cAVVG | Total End Uses | 9963782.49 | 7087329.94
New Construction | CZ09 | cAVVG | Heating | 0 | 3441221.11
New Construction | CZ09 | cAVVG | Cooling | 1202734 | 0
New Construction | CZ09 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ09 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ09 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ09 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ09 | cAVVG | Fans | 2607397.43 | 0
New Construction | CZ09 | cAVVG | Pumps | 25079.5 | 0
New Construction | CZ09 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ09 | cAVVG | Humidification | 0 | 0
New Construction | CZ09 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ09 | cAVVG | Water Systems | 0 | 541322.26
New Construction | CZ09 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ09 | cAVVG | Generators | 0 | 0
New Construction | CZ09 | cAVVG | Total End Uses | 10103934.65 | 6630583.78
New Construction | CZ10 | cAVVG | Heating | 0 | 5083039.48
New Construction | CZ10 | cAVVG | Cooling | 1914602.8 | 0
New Construction | CZ10 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ10 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ10 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ10 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ10 | cAVVG | Fans | 2538086.05 | 0
New Construction | CZ10 | cAVVG | Pumps | 26639.42 | 0
New Construction | CZ10 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ10 | cAVVG | Humidification | 0 | 0
New Construction | CZ10 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ10 | cAVVG | Water Systems | 0 | 537005.31
New Construction | CZ10 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ10 | cAVVG | Generators | 0 | 0
New Construction | CZ10 | cAVVG | Total End Uses | 10748051.99 | 8268085.2
New Construction | CZ11 | cAVVG | Heating | 0 | 8168349.64
New Construction | CZ11 | cAVVG | Cooling | 2285703.11 | 0
New Construction | CZ11 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ11 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ11 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ11 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ11 | cAVVG | Fans | 2633309.09 | 0
New Construction | CZ11 | cAVVG | Pumps | 24884.55 | 0
New Construction | CZ11 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ11 | cAVVG | Humidification | 0 | 0
New Construction | CZ11 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ11 | cAVVG | Water Systems | 0 | 548988.92
New Construction | CZ11 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ11 | cAVVG | Generators | 0 | 0
New Construction | CZ11 | cAVVG | Total End Uses | 11212620.49 | 11365378.97
New Construction | CZ12 | cAVVG | Heating | 0 | 8316089.76
New Construction | CZ12 | cAVVG | Cooling | 1696384.79 | 0
New Construction | CZ12 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ12 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ12 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ12 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ12 | cAVVG | Fans | 2642850.34 | 0
New Construction | CZ12 | cAVVG | Pumps | 24549.33 | 0
New Construction | CZ12 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ12 | cAVVG | Humidification | 0 | 0
New Construction | CZ12 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ12 | cAVVG | Water Systems | 0 | 564545.71
New Construction | CZ12 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ12 | cAVVG | Generators | 0 | 0
New Construction | CZ12 | cAVVG | Total End Uses | 10632508.19 | 11528675.88
New Construction | CZ13 | cAVVG | Heating | 0 | 6901922.48
New Construction | CZ13 | cAVVG | Cooling | 2550428.84 | 0
New Construction | CZ13 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ13 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ13 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ13 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ13 | cAVVG | Fans | 2663504.95 | 0
New Construction | CZ13 | cAVVG | Pumps | 27835.91 | 0
New Construction | CZ13 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ13 | cAVVG | Humidification | 0 | 0
New Construction | CZ13 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ13 | cAVVG | Water Systems | 0 | 532816.78
New Construction | CZ13 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ13 | cAVVG | Generators | 0 | 0
New Construction | CZ13 | cAVVG | Total End Uses | 11510493.43 | 10082779.67
New Construction | CZ14 | cAVVG | Heating | 0 | 5437140.86
New Construction | CZ14 | cAVVG | Cooling | 3445192.95 | 0
New Construction | CZ14 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ14 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ14 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ14 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ14 | cAVVG | Fans | 2504960.68 | 0
New Construction | CZ14 | cAVVG | Pumps | 26179.15 | 0
New Construction | CZ14 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ14 | cAVVG | Humidification | 0 | 0
New Construction | CZ14 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ14 | cAVVG | Water Systems | 0 | 505677.87
New Construction | CZ14 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ14 | cAVVG | Generators | 0 | 0
New Construction | CZ14 | cAVVG | Total End Uses | 12245056.51 | 8590859.15
New Construction | CZ15 | cAVVG | Heating | 0 | 2980687.86
New Construction | CZ15 | cAVVG | Cooling | 4943021.03 | 0
New Construction | CZ15 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ15 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ15 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ15 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ15 | cAVVG | Fans | 2819712.44 | 0
New Construction | CZ15 | cAVVG | Pumps | 35409.46 | 0
New Construction | CZ15 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ15 | cAVVG | Humidification | 0 | 0
New Construction | CZ15 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ15 | cAVVG | Water Systems | 0 | 448903.63
New Construction | CZ15 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ15 | cAVVG | Generators | 0 | 0
New Construction | CZ15 | cAVVG | Total End Uses | 14066866.65 | 6077631.9
New Construction | CZ16 | cAVVG | Heating | 0 | 10014683.7
New Construction | CZ16 | cAVVG | Cooling | 1903342.46 | 0
New Construction | CZ16 | cAVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ16 | cAVVG | Exterior Lighting | 0 | 0
New Construction | CZ16 | cAVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ16 | cAVVG | Exterior Equipment | 0 | 0
New Construction | CZ16 | cAVVG | Fans | 2166515.05 | 0
New Construction | CZ16 | cAVVG | Pumps | 24079.33 | 0
New Construction | CZ16 | cAVVG | Heat Rejection | 0 | 0
New Construction | CZ16 | cAVVG | Humidification | 0 | 0
New Construction | CZ16 | cAVVG | Heat Recovery | 0 | 0
New Construction | CZ16 | cAVVG | Water Systems | 0 | 597077.66
New Construction | CZ16 | cAVVG | Refrigeration | 0 | 0
New Construction | CZ16 | cAVVG | Generators | 0 | 0
New Construction | CZ16 | cAVVG | Total End Uses | 10362660.57 | 13259801.77
Existing | CZ01 | cDXGF | Heating | 0 | 14160240.82
Existing | CZ01 | cDXGF | Cooling | 87309.57 | 0
Existing | CZ01 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ01 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ01 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXGF | Fans | 3182353.87 | 0
Existing | CZ01 | cDXGF | Pumps | 1667.07 | 0
Existing | CZ01 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ01 | cDXGF | Humidification | 0 | 0
Existing | CZ01 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ01 | cDXGF | Water Systems | 0 | 660962.43
Existing | CZ01 | cDXGF | Refrigeration | 0 | 0
Existing | CZ01 | cDXGF | Generators | 0 | 0
Existing | CZ01 | cDXGF | Total End Uses | 10467752.63 | 17469243.66
Existing | CZ02 | cDXGF | Heating | 0 | 9393878.41
Existing | CZ02 | cDXGF | Cooling | 685564.65 | 0
Existing | CZ02 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ02 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ02 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXGF | Fans | 3339302.69 | 0
Existing | CZ02 | cDXGF | Pumps | 1883.36 | 0
Existing | CZ02 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ02 | cDXGF | Humidification | 0 | 0
Existing | CZ02 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ02 | cDXGF | Water Systems | 0 | 607367.6
Existing | CZ02 | cDXGF | Refrigeration | 0 | 0
Existing | CZ02 | cDXGF | Generators | 0 | 0
Existing | CZ02 | cDXGF | Total End Uses | 11223172.83 | 12649286.42
Existing | CZ03 | cDXGF | Heating | 0 | 7661180.27
Existing | CZ03 | cDXGF | Cooling | 347278.44 | 0
Existing | CZ03 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ03 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ03 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXGF | Fans | 3287612.83 | 0
Existing | CZ03 | cDXGF | Pumps | 1894.25 | 0
Existing | CZ03 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ03 | cDXGF | Humidification | 0 | 0
Existing | CZ03 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ03 | cDXGF | Water Systems | 0 | 604984.58
Existing | CZ03 | cDXGF | Refrigeration | 0 | 0
Existing | CZ03 | cDXGF | Generators | 0 | 0
Existing | CZ03 | cDXGF | Total End Uses | 10833207.64 | 10914205.26
Existing | CZ04 | cDXGF | Heating | 0 | 6743901.44
Existing | CZ04 | cDXGF | Cooling | 838122.29 | 0
Existing | CZ04 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ04 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ04 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXGF | Fans | 3357166.72 | 0
Existing | CZ04 | cDXGF | Pumps | 1947.03 | 0
Existing | CZ04 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ04 | cDXGF | Humidification | 0 | 0
Existing | CZ04 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ04 | cDXGF | Water Systems | 0 | 584210.37
Existing | CZ04 | cDXGF | Refrigeration | 0 | 0
Existing | CZ04 | cDXGF | Generators | 0 | 0
Existing | CZ04 | cDXGF | Total End Uses | 11393658.17 | 9976152.22
Existing | CZ05 | cDXGF | Heating | 0 | 7949479.83
Existing | CZ05 | cDXGF | Cooling | 455905.89 | 0
Existing | CZ05 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ05 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ05 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXGF | Fans | 3251908.28 | 0
Existing | CZ05 | cDXGF | Pumps | 1795.96 | 0
Existing | CZ05 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ05 | cDXGF | Humidification | 0 | 0
Existing | CZ05 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ05 | cDXGF | Water Systems | 0 | 605035.15
Existing | CZ05 | cDXGF | Refrigeration | 0 | 0
Existing | CZ05 | cDXGF | Generators | 0 | 0
Existing | CZ05 | cDXGF | Total End Uses | 10906032.26 | 11202555.39
Existing | CZ06 | cDXGF | Heating | 0 | 2976018.89
Existing | CZ06 | cDXGF | Cooling | 730049.97 | 0
Existing | CZ06 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ06 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ06 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXGF | Fans | 3274625.9 | 0
Existing | CZ06 | cDXGF | Pumps | 1954.19 | 0
Existing | CZ06 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ06 | cDXGF | Humidification | 0 | 0
Existing | CZ06 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ06 | cDXGF | Water Systems | 0 | 557321.33
Existing | CZ06 | cDXGF | Refrigeration | 0 | 0
Existing | CZ06 | cDXGF | Generators | 0 | 0
Existing | CZ06 | cDXGF | Total End Uses | 11203052.2 | 6181380.64
Existing | CZ07 | cDXGF | Heating | 0 | 2778988.13
Existing | CZ07 | cDXGF | Cooling | 871122.22 | 0
Existing | CZ07 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ07 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ07 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXGF | Fans | 3319321.46 | 0
Existing | CZ07 | cDXGF | Pumps | 2009.26 | 0
Existing | CZ07 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ07 | cDXGF | Humidification | 0 | 0
Existing | CZ07 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ07 | cDXGF | Water Systems | 0 | 550196.14
Existing | CZ07 | cDXGF | Refrigeration | 0 | 0
Existing | CZ07 | cDXGF | Generators | 0 | 0
Existing | CZ07 | cDXGF | Total End Uses | 11388875.07 | 5977224.68
Existing | CZ08 | cDXGF | Heating | 0 | 3497848.42
Existing | CZ08 | cDXGF | Cooling | 1133512.4 | 0
Existing | CZ08 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ08 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ08 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXGF | Fans | 3372571.94 | 0
Existing | CZ08 | cDXGF | Pumps | 2051.97 | 0
Existing | CZ08 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ08 | cDXGF | Humidification | 0 | 0
Existing | CZ08 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ08 | cDXGF | Water Systems | 0 | 549414.99
Existing | CZ08 | cDXGF | Refrigeration | 0 | 0
Existing | CZ08 | cDXGF | Generators | 0 | 0
Existing | CZ08 | cDXGF | Total End Uses | 11704558.45 | 6695303.82
Existing | CZ09 | cDXGF | Heating | 0 | 3096314.35
Existing | CZ09 | cDXGF | Cooling | 1320706.02 | 0
Existing | CZ09 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ09 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ09 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXGF | Fans | 3402651.73 | 0
Existing | CZ09 | cDXGF | Pumps | 2077.93 | 0
Existing | CZ09 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ09 | cDXGF | Humidification | 0 | 0
Existing | CZ09 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ09 | cDXGF | Water Systems | 0 | 541819.23
Existing | CZ09 | cDXGF | Refrigeration | 0 | 0
Existing | CZ09 | cDXGF | Generators | 0 | 0
Existing | CZ09 | cDXGF | Total End Uses | 11921857.81 | 6286173.99
Existing | CZ10 | cDXGF | Heating | 0 | 4634561.84
Existing | CZ10 | cDXGF | Cooling | 2044946.01 | 0
Existing | CZ10 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ10 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ10 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXGF | Fans | 3304862.38 | 0
Existing | CZ10 | cDXGF | Pumps | 2103.98 | 0
Existing | CZ10 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ10 | cDXGF | Humidification | 0 | 0
Existing | CZ10 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ10 | cDXGF | Water Systems | 0 | 537464.91
Existing | CZ10 | cDXGF | Refrigeration | 0 | 0
Existing | CZ10 | cDXGF | Generators | 0 | 0
Existing | CZ10 | cDXGF | Total End Uses | 12548334.5 | 7820067.16
Existing | CZ11 | cDXGF | Heating | 0 | 7589439.08
Existing | CZ11 | cDXGF | Cooling | 2444591.47 | 0
Existing | CZ11 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ11 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ11 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXGF | Fans | 3467203.94 | 0
Existing | CZ11 | cDXGF | Pumps | 2091.83 | 0
Existing | CZ11 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ11 | cDXGF | Humidification | 0 | 0
Existing | CZ11 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ11 | cDXGF | Water Systems | 0 | 549484.47
Existing | CZ11 | cDXGF | Refrigeration | 0 | 0
Existing | CZ11 | cDXGF | Generators | 0 | 0
Existing | CZ11 | cDXGF | Total End Uses | 13110309.37 | 10786963.96
Existing | CZ12 | cDXGF | Heating | 0 | 7703724.06
Existing | CZ12 | cDXGF | Cooling | 1809483.14 | 0
Existing | CZ12 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ12 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ12 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXGF | Fans | 3416703.29 | 0
Existing | CZ12 | cDXGF | Pumps | 2030.73 | 0
Existing | CZ12 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ12 | cDXGF | Humidification | 0 | 0
Existing | CZ12 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ12 | cDXGF | Water Systems | 0 | 564945.17
Existing | CZ12 | cDXGF | Refrigeration | 0 | 0
Existing | CZ12 | cDXGF | Generators | 0 | 0
Existing | CZ12 | cDXGF | Total End Uses | 12424639.29 | 10916709.64
Existing | CZ13 | cDXGF | Heating | 0 | 6400818.53
Existing | CZ13 | cDXGF | Cooling | 2742098.15 | 0
Existing | CZ13 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ13 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ13 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXGF | Fans | 3453609.55 | 0
Existing | CZ13 | cDXGF | Pumps | 2186.91 | 0
Existing | CZ13 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ13 | cDXGF | Humidification | 0 | 0
Existing | CZ13 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ13 | cDXGF | Water Systems | 0 | 533507.98
Existing | CZ13 | cDXGF | Refrigeration | 0 | 0
Existing | CZ13 | cDXGF | Generators | 0 | 0
Existing | CZ13 | cDXGF | Total End Uses | 13394316.75 | 9582366.92
Existing | CZ14 | cDXGF | Heating | 0 | 5007997.14
Existing | CZ14 | cDXGF | Cooling | 3688733.81 | 0
Existing | CZ14 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ14 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ14 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXGF | Fans | 3367220.43 | 0
Existing | CZ14 | cDXGF | Pumps | 2181.8 | 0
Existing | CZ14 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ14 | cDXGF | Humidification | 0 | 0
Existing | CZ14 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ14 | cDXGF | Water Systems | 0 | 506422.4
Existing | CZ14 | cDXGF | Refrigeration | 0 | 0
Existing | CZ14 | cDXGF | Generators | 0 | 0
Existing | CZ14 | cDXGF | Total End Uses | 14254558.17 | 8162459.96
Existing | CZ15 | cDXGF | Heating | 0 | 2668843.33
Existing | CZ15 | cDXGF | Cooling | 5183902.59 | 0
Existing | CZ15 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ15 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ15 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXGF | Fans | 3608718.31 | 0
Existing | CZ15 | cDXGF | Pumps | 2327.5 | 0
Existing | CZ15 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ15 | cDXGF | Humidification | 0 | 0
Existing | CZ15 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ15 | cDXGF | Water Systems | 0 | 449566.58
Existing | CZ15 | cDXGF | Refrigeration | 0 | 0
Existing | CZ15 | cDXGF | Generators | 0 | 0
Existing | CZ15 | cDXGF | Total End Uses | 15991370.53 | 5766450.32
Existing | CZ16 | cDXGF | Heating | 0 | 9347580.31
Existing | CZ16 | cDXGF | Cooling | 2071450.01 | 0
Existing | CZ16 | cDXGF | Interior Lighting | 2428283.52 | 0
Existing | CZ16 | cDXGF | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ16 | cDXGF | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXGF | Fans | 3014407.65 | 0
Existing | CZ16 | cDXGF | Pumps | 1861.44 | 0
Existing | CZ16 | cDXGF | Heat Rejection | 0 | 0
Existing | CZ16 | cDXGF | Humidification | 0 | 0
Existing | CZ16 | cDXGF | Heat Recovery | 0 | 0
Existing | CZ16 | cDXGF | Water Systems | 0 | 597407.63
Existing | CZ16 | cDXGF | Refrigeration | 0 | 0
Existing | CZ16 | cDXGF | Generators | 0 | 0
Existing | CZ16 | cDXGF | Total End Uses | 12284141.24 | 12593028.35
New Construction | CZ01 | cDXGF | Heating | 0 | 14523674.27
New Construction | CZ01 | cDXGF | Cooling | 80499.9 | 0
New Construction | CZ01 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ01 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ01 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXGF | Fans | 2954829.06 | 0
New Construction | CZ01 | cDXGF | Pumps | 1398.93 | 0
New Construction | CZ01 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXGF | Humidification | 0 | 0
New Construction | CZ01 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXGF | Water Systems | 0 | 660762.59
New Construction | CZ01 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ01 | cDXGF | Generators | 0 | 0
New Construction | CZ01 | cDXGF | Total End Uses | 9305451.62 | 17832477.27
New Construction | CZ02 | cDXGF | Heating | 0 | 9734809.42
New Construction | CZ02 | cDXGF | Cooling | 600668.41 | 0
New Construction | CZ02 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ02 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ02 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXGF | Fans | 3040371.99 | 0
New Construction | CZ02 | cDXGF | Pumps | 1541.72 | 0
New Construction | CZ02 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXGF | Humidification | 0 | 0
New Construction | CZ02 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXGF | Water Systems | 0 | 607082.05
New Construction | CZ02 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ02 | cDXGF | Generators | 0 | 0
New Construction | CZ02 | cDXGF | Total End Uses | 9911305.84 | 12989931.88
New Construction | CZ03 | cDXGF | Heating | 0 | 8059958.13
New Construction | CZ03 | cDXGF | Cooling | 297094.32 | 0
New Construction | CZ03 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ03 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ03 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXGF | Fans | 3012301.53 | 0
New Construction | CZ03 | cDXGF | Pumps | 1570.52 | 0
New Construction | CZ03 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXGF | Humidification | 0 | 0
New Construction | CZ03 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXGF | Water Systems | 0 | 604726.84
New Construction | CZ03 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ03 | cDXGF | Generators | 0 | 0
New Construction | CZ03 | cDXGF | Total End Uses | 9579690.09 | 11312725.38
New Construction | CZ04 | cDXGF | Heating | 0 | 7079718.88
New Construction | CZ04 | cDXGF | Cooling | 725764.64 | 0
New Construction | CZ04 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ04 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ04 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXGF | Fans | 3052989.59 | 0
New Construction | CZ04 | cDXGF | Pumps | 1587.51 | 0
New Construction | CZ04 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXGF | Humidification | 0 | 0
New Construction | CZ04 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXGF | Water Systems | 0 | 583897.81
New Construction | CZ04 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ04 | cDXGF | Generators | 0 | 0
New Construction | CZ04 | cDXGF | Total End Uses | 10049065.46 | 10311657.1
New Construction | CZ05 | cDXGF | Heating | 0 | 8373825.07
New Construction | CZ05 | cDXGF | Cooling | 394082.04 | 0
New Construction | CZ05 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ05 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ05 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXGF | Fans | 2978940.13 | 0
New Construction | CZ05 | cDXGF | Pumps | 1456.01 | 0
New Construction | CZ05 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXGF | Humidification | 0 | 0
New Construction | CZ05 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXGF | Water Systems | 0 | 604736.56
New Construction | CZ05 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ05 | cDXGF | Generators | 0 | 0
New Construction | CZ05 | cDXGF | Total End Uses | 9643201.92 | 11626602.04
New Construction | CZ06 | cDXGF | Heating | 0 | 3226858.02
New Construction | CZ06 | cDXGF | Cooling | 606068.09 | 0
New Construction | CZ06 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ06 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ06 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXGF | Fans | 2987765.55 | 0
New Construction | CZ06 | cDXGF | Pumps | 1585.41 | 0
New Construction | CZ06 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXGF | Humidification | 0 | 0
New Construction | CZ06 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXGF | Water Systems | 0 | 556947.51
New Construction | CZ06 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ06 | cDXGF | Generators | 0 | 0
New Construction | CZ06 | cDXGF | Total End Uses | 9864142.78 | 6431845.94
New Construction | CZ07 | cDXGF | Heating | 0 | 2998987.93
New Construction | CZ07 | cDXGF | Cooling | 721617.89 | 0
New Construction | CZ07 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ07 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ07 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXGF | Fans | 3040186.06 | 0
New Construction | CZ07 | cDXGF | Pumps | 1646.88 | 0
New Construction | CZ07 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXGF | Humidification | 0 | 0
New Construction | CZ07 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXGF | Water Systems | 0 | 549792.44
New Construction | CZ07 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ07 | cDXGF | Generators | 0 | 0
New Construction | CZ07 | cDXGF | Total End Uses | 10032174.56 | 6196820.78
New Construction | CZ08 | cDXGF | Heating | 0 | 3736037.2
New Construction | CZ08 | cDXGF | Cooling | 969395.49 | 0
New Construction | CZ08 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ08 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ08 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXGF | Fans | 3064035.94 | 0
New Construction | CZ08 | cDXGF | Pumps | 1661.55 | 0
New Construction | CZ08 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXGF | Humidification | 0 | 0
New Construction | CZ08 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXGF | Water Systems | 0 | 548995.27
New Construction | CZ08 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ08 | cDXGF | Generators | 0 | 0
New Construction | CZ08 | cDXGF | Total End Uses | 10303816.71 | 6933072.88
New Construction | CZ09 | cDXGF | Heating | 0 | 3303357.38
New Construction | CZ09 | cDXGF | Cooling | 1120232.98 | 0
New Construction | CZ09 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ09 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ09 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXGF | Fans | 3062890.49 | 0
New Construction | CZ09 | cDXGF | Pumps | 1675.78 | 0
New Construction | CZ09 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXGF | Humidification | 0 | 0
New Construction | CZ09 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXGF | Water Systems | 0 | 541309.87
New Construction | CZ09 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ09 | cDXGF | Generators | 0 | 0
New Construction | CZ09 | cDXGF | Total End Uses | 10453522.98 | 6492707.66
New Construction | CZ10 | cDXGF | Heating | 0 | 4857296.63
New Construction | CZ10 | cDXGF | Cooling | 1820885.93 | 0
New Construction | CZ10 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ10 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ10 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXGF | Fans | 2995969.75 | 0
New Construction | CZ10 | cDXGF | Pumps | 1697.03 | 0
New Construction | CZ10 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXGF | Humidification | 0 | 0
New Construction | CZ10 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXGF | Water Systems | 0 | 536915.23
New Construction | CZ10 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ10 | cDXGF | Generators | 0 | 0
New Construction | CZ10 | cDXGF | Total End Uses | 11087276.44 | 8042252.27
New Construction | CZ11 | cDXGF | Heating | 0 | 7778475.9
New Construction | CZ11 | cDXGF | Cooling | 2191374.53 | 0
New Construction | CZ11 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ11 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ11 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXGF | Fans | 3105010.63 | 0
New Construction | CZ11 | cDXGF | Pumps | 1686.13 | 0
New Construction | CZ11 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXGF | Humidification | 0 | 0
New Construction | CZ11 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXGF | Water Systems | 0 | 548967.04
New Construction | CZ11 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ11 | cDXGF | Generators | 0 | 0
New Construction | CZ11 | cDXGF | Total End Uses | 11566795.02 | 10975483.35
New Construction | CZ12 | cDXGF | Heating | 0 | 7950300.49
New Construction | CZ12 | cDXGF | Cooling | 1611808.32 | 0
New Construction | CZ12 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ12 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ12 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXGF | Fans | 3097363.32 | 0
New Construction | CZ12 | cDXGF | Pumps | 1627.03 | 0
New Construction | CZ12 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXGF | Humidification | 0 | 0
New Construction | CZ12 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXGF | Water Systems | 0 | 564556.83
New Construction | CZ12 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ12 | cDXGF | Generators | 0 | 0
New Construction | CZ12 | cDXGF | Total End Uses | 10979522.4 | 11162897.73
New Construction | CZ13 | cDXGF | Heating | 0 | 6592290.61
New Construction | CZ13 | cDXGF | Cooling | 2446544.62 | 0
New Construction | CZ13 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ13 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ13 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXGF | Fans | 3105440.19 | 0
New Construction | CZ13 | cDXGF | Pumps | 1778.7 | 0
New Construction | CZ13 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXGF | Humidification | 0 | 0
New Construction | CZ13 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXGF | Water Systems | 0 | 532781.6
New Construction | CZ13 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ13 | cDXGF | Generators | 0 | 0
New Construction | CZ13 | cDXGF | Total End Uses | 11822487.25 | 9773112.62
New Construction | CZ14 | cDXGF | Heating | 0 | 5179642.1
New Construction | CZ14 | cDXGF | Cooling | 3327200.92 | 0
New Construction | CZ14 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ14 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ14 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXGF | Fans | 2979790.09 | 0
New Construction | CZ14 | cDXGF | Pumps | 1772.69 | 0
New Construction | CZ14 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXGF | Humidification | 0 | 0
New Construction | CZ14 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXGF | Water Systems | 0 | 505738.68
New Construction | CZ14 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ14 | cDXGF | Generators | 0 | 0
New Construction | CZ14 | cDXGF | Total End Uses | 12577487.44 | 8333421.19
New Construction | CZ15 | cDXGF | Heating | 0 | 2835576.76
New Construction | CZ15 | cDXGF | Cooling | 4705896.25 | 0
New Construction | CZ15 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ15 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ15 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXGF | Fans | 3232194.46 | 0
New Construction | CZ15 | cDXGF | Pumps | 1882.85 | 0
New Construction | CZ15 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXGF | Humidification | 0 | 0
New Construction | CZ15 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXGF | Water Systems | 0 | 448898.3
New Construction | CZ15 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ15 | cDXGF | Generators | 0 | 0
New Construction | CZ15 | cDXGF | Total End Uses | 14208697.29 | 5932515.47
New Construction | CZ16 | cDXGF | Heating | 0 | 9520833.47
New Construction | CZ16 | cDXGF | Cooling | 1846243.11 | 0
New Construction | CZ16 | cDXGF | Interior Lighting | 1500585.11 | 0
New Construction | CZ16 | cDXGF | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXGF | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ16 | cDXGF | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXGF | Fans | 2694322.52 | 0
New Construction | CZ16 | cDXGF | Pumps | 1495.24 | 0
New Construction | CZ16 | cDXGF | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXGF | Humidification | 0 | 0
New Construction | CZ16 | cDXGF | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXGF | Water Systems | 0 | 597060.14
New Construction | CZ16 | cDXGF | Refrigeration | 0 | 0
New Construction | CZ16 | cDXGF | Generators | 0 | 0
New Construction | CZ16 | cDXGF | Total End Uses | 10810784.59 | 12765934.02
Existing | CZ01 | cDXHP | Heating | 159997.04 | 13498159.2
Existing | CZ01 | cDXHP | Cooling | 86801.11 | 0
Existing | CZ01 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ01 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ01 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXHP | Fans | 3182353.81 | 0
Existing | CZ01 | cDXHP | Pumps | 1667.06 | 0
Existing | CZ01 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ01 | cDXHP | Humidification | 0 | 0
Existing | CZ01 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ01 | cDXHP | Water Systems | 0 | 660962.44
Existing | CZ01 | cDXHP | Refrigeration | 0 | 0
Existing | CZ01 | cDXHP | Generators | 0 | 0
Existing | CZ01 | cDXHP | Total End Uses | 10627241.16 | 16807162.05
Existing | CZ02 | cDXHP | Heating | 102615.53 | 9013067.69
Existing | CZ02 | cDXHP | Cooling | 683808.75 | 0
Existing | CZ02 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ02 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ02 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXHP | Fans | 3339187.96 | 0
Existing | CZ02 | cDXHP | Pumps | 1883.09 | 0
Existing | CZ02 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ02 | cDXHP | Humidification | 0 | 0
Existing | CZ02 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ02 | cDXHP | Water Systems | 0 | 607366.95
Existing | CZ02 | cDXHP | Refrigeration | 0 | 0
Existing | CZ02 | cDXHP | Generators | 0 | 0
Existing | CZ02 | cDXHP | Total End Uses | 11323917.46 | 12268475.05
Existing | CZ03 | cDXHP | Heating | 57953.31 | 7426703.5
Existing | CZ03 | cDXHP | Cooling | 345275.97 | 0
Existing | CZ03 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ03 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ03 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXHP | Fans | 3287609.15 | 0
Existing | CZ03 | cDXHP | Pumps | 1894.17 | 0
Existing | CZ03 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ03 | cDXHP | Humidification | 0 | 0
Existing | CZ03 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ03 | cDXHP | Water Systems | 0 | 604984.55
Existing | CZ03 | cDXHP | Refrigeration | 0 | 0
Existing | CZ03 | cDXHP | Generators | 0 | 0
Existing | CZ03 | cDXHP | Total End Uses | 10889154.73 | 10679728.45
Existing | CZ04 | cDXHP | Heating | 49921.41 | 6543285.43
Existing | CZ04 | cDXHP | Cooling | 837596.19 | 0
Existing | CZ04 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ04 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ04 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXHP | Fans | 3357111.08 | 0
Existing | CZ04 | cDXHP | Pumps | 1946.93 | 0
Existing | CZ04 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ04 | cDXHP | Humidification | 0 | 0
Existing | CZ04 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ04 | cDXHP | Water Systems | 0 | 584241.79
Existing | CZ04 | cDXHP | Refrigeration | 0 | 0
Existing | CZ04 | cDXHP | Generators | 0 | 0
Existing | CZ04 | cDXHP | Total End Uses | 11442997.74 | 9775567.63
Existing | CZ05 | cDXHP | Heating | 53092.02 | 7742637.22
Existing | CZ05 | cDXHP | Cooling | 454327.02 | 0
Existing | CZ05 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ05 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ05 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXHP | Fans | 3251898.29 | 0
Existing | CZ05 | cDXHP | Pumps | 1795.86 | 0
Existing | CZ05 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ05 | cDXHP | Humidification | 0 | 0
Existing | CZ05 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ05 | cDXHP | Water Systems | 0 | 605035.19
Existing | CZ05 | cDXHP | Refrigeration | 0 | 0
Existing | CZ05 | cDXHP | Generators | 0 | 0
Existing | CZ05 | cDXHP | Total End Uses | 10957535.31 | 10995712.82
Existing | CZ06 | cDXHP | Heating | 8940.88 | 2938309.12
Existing | CZ06 | cDXHP | Cooling | 717021.81 | 0
Existing | CZ06 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ06 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ06 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXHP | Fans | 3274613.99 | 0
Existing | CZ06 | cDXHP | Pumps | 1954.06 | 0
Existing | CZ06 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ06 | cDXHP | Humidification | 0 | 0
Existing | CZ06 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ06 | cDXHP | Water Systems | 0 | 557322.35
Existing | CZ06 | cDXHP | Refrigeration | 0 | 0
Existing | CZ06 | cDXHP | Generators | 0 | 0
Existing | CZ06 | cDXHP | Total End Uses | 11198952.87 | 6143671.88
Existing | CZ07 | cDXHP | Heating | 8551.49 | 2743004.69
Existing | CZ07 | cDXHP | Cooling | 861694.36 | 0
Existing | CZ07 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ07 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ07 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXHP | Fans | 3319320.08 | 0
Existing | CZ07 | cDXHP | Pumps | 2009.24 | 0
Existing | CZ07 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ07 | cDXHP | Humidification | 0 | 0
Existing | CZ07 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ07 | cDXHP | Water Systems | 0 | 550196.27
Existing | CZ07 | cDXHP | Refrigeration | 0 | 0
Existing | CZ07 | cDXHP | Generators | 0 | 0
Existing | CZ07 | cDXHP | Total End Uses | 11387997.3 | 5941241.37
Existing | CZ08 | cDXHP | Heating | 14614.02 | 3437149.77
Existing | CZ08 | cDXHP | Cooling | 1127074.31 | 0
Existing | CZ08 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ08 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ08 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXHP | Fans | 3372559.77 | 0
Existing | CZ08 | cDXHP | Pumps | 2051.97 | 0
Existing | CZ08 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ08 | cDXHP | Humidification | 0 | 0
Existing | CZ08 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ08 | cDXHP | Water Systems | 0 | 549416.25
Existing | CZ08 | cDXHP | Refrigeration | 0 | 0
Existing | CZ08 | cDXHP | Generators | 0 | 0
Existing | CZ08 | cDXHP | Total End Uses | 11712722.2 | 6634606.44
Existing | CZ09 | cDXHP | Heating | 11403.99 | 3048740.52
Existing | CZ09 | cDXHP | Cooling | 1313840.25 | 0
Existing | CZ09 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ09 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ09 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXHP | Fans | 3402600.11 | 0
Existing | CZ09 | cDXHP | Pumps | 2077.84 | 0
Existing | CZ09 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ09 | cDXHP | Humidification | 0 | 0
Existing | CZ09 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ09 | cDXHP | Water Systems | 0 | 541819.58
Existing | CZ09 | cDXHP | Refrigeration | 0 | 0
Existing | CZ09 | cDXHP | Generators | 0 | 0
Existing | CZ09 | cDXHP | Total End Uses | 11926344.32 | 6238600.51
Existing | CZ10 | cDXHP | Heating | 35347.02 | 4503307.57
Existing | CZ10 | cDXHP | Cooling | 2046316.3 | 0
Existing | CZ10 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ10 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ10 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXHP | Fans | 3304811.22 | 0
Existing | CZ10 | cDXHP | Pumps | 2103.84 | 0
Existing | CZ10 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ10 | cDXHP | Humidification | 0 | 0
Existing | CZ10 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ10 | cDXHP | Water Systems | 0 | 537466.63
Existing | CZ10 | cDXHP | Refrigeration | 0 | 0
Existing | CZ10 | cDXHP | Generators | 0 | 0
Existing | CZ10 | cDXHP | Total End Uses | 12585000.51 | 7688814.61
Existing | CZ11 | cDXHP | Heating | 95489.18 | 7229319.6
Existing | CZ11 | cDXHP | Cooling | 2453236.66 | 0
Existing | CZ11 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ11 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ11 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXHP | Fans | 3466813.41 | 0
Existing | CZ11 | cDXHP | Pumps | 2091.72 | 0
Existing | CZ11 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ11 | cDXHP | Humidification | 0 | 0
Existing | CZ11 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ11 | cDXHP | Water Systems | 0 | 549490.86
Existing | CZ11 | cDXHP | Refrigeration | 0 | 0
Existing | CZ11 | cDXHP | Generators | 0 | 0
Existing | CZ11 | cDXHP | Total End Uses | 13214053.1 | 10426850.87
Existing | CZ12 | cDXHP | Heating | 93101.95 | 7356924.45
Existing | CZ12 | cDXHP | Cooling | 1815629.94 | 0
Existing | CZ12 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ12 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ12 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXHP | Fans | 3416504.81 | 0
Existing | CZ12 | cDXHP | Pumps | 2030.46 | 0
Existing | CZ12 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ12 | cDXHP | Humidification | 0 | 0
Existing | CZ12 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ12 | cDXHP | Water Systems | 0 | 564941.94
Existing | CZ12 | cDXHP | Refrigeration | 0 | 0
Existing | CZ12 | cDXHP | Generators | 0 | 0
Existing | CZ12 | cDXHP | Total End Uses | 12523689.29 | 10569906.8
Existing | CZ13 | cDXHP | Heating | 72564.66 | 6123635.91
Existing | CZ13 | cDXHP | Cooling | 2748190.67 | 0
Existing | CZ13 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ13 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ13 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXHP | Fans | 3453441.3 | 0
Existing | CZ13 | cDXHP | Pumps | 2186.94 | 0
Existing | CZ13 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ13 | cDXHP | Humidification | 0 | 0
Existing | CZ13 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ13 | cDXHP | Water Systems | 0 | 533506.93
Existing | CZ13 | cDXHP | Refrigeration | 0 | 0
Existing | CZ13 | cDXHP | Generators | 0 | 0
Existing | CZ13 | cDXHP | Total End Uses | 13472805.69 | 9305183.25
Existing | CZ14 | cDXHP | Heating | 48306.61 | 4826751.68
Existing | CZ14 | cDXHP | Cooling | 3698871.95 | 0
Existing | CZ14 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ14 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ14 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXHP | Fans | 3366890.97 | 0
Existing | CZ14 | cDXHP | Pumps | 2181.84 | 0
Existing | CZ14 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ14 | cDXHP | Humidification | 0 | 0
Existing | CZ14 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ14 | cDXHP | Water Systems | 0 | 506432.48
Existing | CZ14 | cDXHP | Refrigeration | 0 | 0
Existing | CZ14 | cDXHP | Generators | 0 | 0
Existing | CZ14 | cDXHP | Total End Uses | 14312673.5 | 7981224.58
Existing | CZ15 | cDXHP | Heating | 10101.68 | 2630035.08
Existing | CZ15 | cDXHP | Cooling | 5185733.27 | 0
Existing | CZ15 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ15 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ15 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXHP | Fans | 3608681.72 | 0
Existing | CZ15 | cDXHP | Pumps | 2327.5 | 0
Existing | CZ15 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ15 | cDXHP | Humidification | 0 | 0
Existing | CZ15 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ15 | cDXHP | Water Systems | 0 | 449566.65
Existing | CZ15 | cDXHP | Refrigeration | 0 | 0
Existing | CZ15 | cDXHP | Generators | 0 | 0
Existing | CZ15 | cDXHP | Total End Uses | 16003266.31 | 5727642.14
Existing | CZ16 | cDXHP | Heating | 192681.95 | 8758114.5
Existing | CZ16 | cDXHP | Cooling | 2083137.82 | 0
Existing | CZ16 | cDXHP | Interior Lighting | 2428283.52 | 0
Existing | CZ16 | cDXHP | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ16 | cDXHP | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXHP | Fans | 3013956.03 | 0
Existing | CZ16 | cDXHP | Pumps | 1860.99 | 0
Existing | CZ16 | cDXHP | Heat Rejection | 0 | 0
Existing | CZ16 | cDXHP | Humidification | 0 | 0
Existing | CZ16 | cDXHP | Heat Recovery | 0 | 0
Existing | CZ16 | cDXHP | Water Systems | 0 | 597407.33
Existing | CZ16 | cDXHP | Refrigeration | 0 | 0
Existing | CZ16 | cDXHP | Generators | 0 | 0
Existing | CZ16 | cDXHP | Total End Uses | 12488058.92 | 12003562.24
New Construction | CZ01 | cDXHP | Heating | 159941.45 | 13854487.87
New Construction | CZ01 | cDXHP | Cooling | 79859.68 | 0
New Construction | CZ01 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ01 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ01 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXHP | Fans | 2954829.01 | 0
New Construction | CZ01 | cDXHP | Pumps | 1398.93 | 0
New Construction | CZ01 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXHP | Humidification | 0 | 0
New Construction | CZ01 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXHP | Water Systems | 0 | 660762.27
New Construction | CZ01 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ01 | cDXHP | Generators | 0 | 0
New Construction | CZ01 | cDXHP | Total End Uses | 9464752.8 | 17163290.55
New Construction | CZ02 | cDXHP | Heating | 100782.88 | 9350380.43
New Construction | CZ02 | cDXHP | Cooling | 599388.13 | 0
New Construction | CZ02 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ02 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ02 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXHP | Fans | 3040289.22 | 0
New Construction | CZ02 | cDXHP | Pumps | 1541.43 | 0
New Construction | CZ02 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXHP | Humidification | 0 | 0
New Construction | CZ02 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXHP | Water Systems | 0 | 607080.29
New Construction | CZ02 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ02 | cDXHP | Generators | 0 | 0
New Construction | CZ02 | cDXHP | Total End Uses | 10010725.4 | 12605501.14
New Construction | CZ03 | cDXHP | Heating | 60490.15 | 7810708.69
New Construction | CZ03 | cDXHP | Cooling | 294958.68 | 0
New Construction | CZ03 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ03 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ03 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXHP | Fans | 3012303.69 | 0
New Construction | CZ03 | cDXHP | Pumps | 1570.37 | 0
New Construction | CZ03 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXHP | Humidification | 0 | 0
New Construction | CZ03 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXHP | Water Systems | 0 | 604725.71
New Construction | CZ03 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ03 | cDXHP | Generators | 0 | 0
New Construction | CZ03 | cDXHP | Total End Uses | 9638046.62 | 11063474.81
New Construction | CZ04 | cDXHP | Heating | 51341.38 | 6869101.88
New Construction | CZ04 | cDXHP | Cooling | 725544.72 | 0
New Construction | CZ04 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ04 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ04 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXHP | Fans | 3052820.72 | 0
New Construction | CZ04 | cDXHP | Pumps | 1587.12 | 0
New Construction | CZ04 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXHP | Humidification | 0 | 0
New Construction | CZ04 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXHP | Water Systems | 0 | 583879.21
New Construction | CZ04 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ04 | cDXHP | Generators | 0 | 0
New Construction | CZ04 | cDXHP | Total End Uses | 10100017.66 | 10101021.51
New Construction | CZ05 | cDXHP | Heating | 57115.26 | 8145811.92
New Construction | CZ05 | cDXHP | Cooling | 392407.87 | 0
New Construction | CZ05 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ05 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ05 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXHP | Fans | 2978937.8 | 0
New Construction | CZ05 | cDXHP | Pumps | 1455.93 | 0
New Construction | CZ05 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXHP | Humidification | 0 | 0
New Construction | CZ05 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXHP | Water Systems | 0 | 604736.83
New Construction | CZ05 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ05 | cDXHP | Generators | 0 | 0
New Construction | CZ05 | cDXHP | Total End Uses | 9698640.58 | 11398589.16
New Construction | CZ06 | cDXHP | Heating | 11138.92 | 3179183.8
New Construction | CZ06 | cDXHP | Cooling | 593465.58 | 0
New Construction | CZ06 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ06 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ06 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXHP | Fans | 2987676.54 | 0
New Construction | CZ06 | cDXHP | Pumps | 1584.97 | 0
New Construction | CZ06 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXHP | Humidification | 0 | 0
New Construction | CZ06 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXHP | Water Systems | 0 | 556940.06
New Construction | CZ06 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ06 | cDXHP | Generators | 0 | 0
New Construction | CZ06 | cDXHP | Total End Uses | 9862589.74 | 6384164.27
New Construction | CZ07 | cDXHP | Heating | 10773.23 | 2952865.09
New Construction | CZ07 | cDXHP | Cooling | 712276.2 | 0
New Construction | CZ07 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ07 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ07 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXHP | Fans | 3040188.75 | 0
New Construction | CZ07 | cDXHP | Pumps | 1646.85 | 0
New Construction | CZ07 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXHP | Humidification | 0 | 0
New Construction | CZ07 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXHP | Water Systems | 0 | 549791.85
New Construction | CZ07 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ07 | cDXHP | Generators | 0 | 0
New Construction | CZ07 | cDXHP | Total End Uses | 10033608.75 | 6150697.36
New Construction | CZ08 | cDXHP | Heating | 16684.71 | 3665673.04
New Construction | CZ08 | cDXHP | Cooling | 963208.32 | 0
New Construction | CZ08 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ08 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ08 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXHP | Fans | 3064000.67 | 0
New Construction | CZ08 | cDXHP | Pumps | 1661.3 | 0
New Construction | CZ08 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXHP | Humidification | 0 | 0
New Construction | CZ08 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXHP | Water Systems | 0 | 548993.07
New Construction | CZ08 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ08 | cDXHP | Generators | 0 | 0
New Construction | CZ08 | cDXHP | Total End Uses | 10314278.71 | 6862706.52
New Construction | CZ09 | cDXHP | Heating | 12920.71 | 3248704.85
New Construction | CZ09 | cDXHP | Cooling | 1114327.07 | 0
New Construction | CZ09 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ09 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ09 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXHP | Fans | 3062836.46 | 0
New Construction | CZ09 | cDXHP | Pumps | 1675.39 | 0
New Construction | CZ09 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXHP | Humidification | 0 | 0
New Construction | CZ09 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXHP | Water Systems | 0 | 541308.27
New Construction | CZ09 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ09 | cDXHP | Generators | 0 | 0
New Construction | CZ09 | cDXHP | Total End Uses | 10460483.37 | 6438053.53
New Construction | CZ10 | cDXHP | Heating | 36766.86 | 4717555.39
New Construction | CZ10 | cDXHP | Cooling | 1825199.38 | 0
New Construction | CZ10 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ10 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ10 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXHP | Fans | 2995838.36 | 0
New Construction | CZ10 | cDXHP | Pumps | 1695.64 | 0
New Construction | CZ10 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXHP | Humidification | 0 | 0
New Construction | CZ10 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXHP | Water Systems | 0 | 536923.3
New Construction | CZ10 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ10 | cDXHP | Generators | 0 | 0
New Construction | CZ10 | cDXHP | Total End Uses | 11128223.97 | 7902519.1
New Construction | CZ11 | cDXHP | Heating | 93796.26 | 7417543.59
New Construction | CZ11 | cDXHP | Cooling | 2202308.99 | 0
New Construction | CZ11 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ11 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ11 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXHP | Fans | 3104736.77 | 0
New Construction | CZ11 | cDXHP | Pumps | 1685 | 0
New Construction | CZ11 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXHP | Humidification | 0 | 0
New Construction | CZ11 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXHP | Water Systems | 0 | 548883.25
New Construction | CZ11 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ11 | cDXHP | Generators | 0 | 0
New Construction | CZ11 | cDXHP | Total End Uses | 11671250.76 | 10614467.25
New Construction | CZ12 | cDXHP | Heating | 91913.29 | 7599813.6
New Construction | CZ12 | cDXHP | Cooling | 1620938.23 | 0
New Construction | CZ12 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ12 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ12 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXHP | Fans | 3097092.38 | 0
New Construction | CZ12 | cDXHP | Pumps | 1626.08 | 0
New Construction | CZ12 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXHP | Humidification | 0 | 0
New Construction | CZ12 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXHP | Water Systems | 0 | 564524.69
New Construction | CZ12 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ12 | cDXHP | Generators | 0 | 0
New Construction | CZ12 | cDXHP | Total End Uses | 11080293.71 | 10812378.7
New Construction | CZ13 | cDXHP | Heating | 73122.17 | 6306965.11
New Construction | CZ13 | cDXHP | Cooling | 2455073.23 | 0
New Construction | CZ13 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ13 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ13 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXHP | Fans | 3105225.09 | 0
New Construction | CZ13 | cDXHP | Pumps | 1778.48 | 0
New Construction | CZ13 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXHP | Humidification | 0 | 0
New Construction | CZ13 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXHP | Water Systems | 0 | 532837.7
New Construction | CZ13 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ13 | cDXHP | Generators | 0 | 0
New Construction | CZ13 | cDXHP | Total End Uses | 11903922.69 | 9487843.22
New Construction | CZ14 | cDXHP | Heating | 49826.03 | 4989483.64
New Construction | CZ14 | cDXHP | Cooling | 3342243.4 | 0
New Construction | CZ14 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ14 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ14 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXHP | Fans | 2979152.51 | 0
New Construction | CZ14 | cDXHP | Pumps | 1770.76 | 0
New Construction | CZ14 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXHP | Humidification | 0 | 0
New Construction | CZ14 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXHP | Water Systems | 0 | 505805.19
New Construction | CZ14 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ14 | cDXHP | Generators | 0 | 0
New Construction | CZ14 | cDXHP | Total End Uses | 12641716.42 | 8143329.25
New Construction | CZ15 | cDXHP | Heating | 13175.64 | 2783690.69
New Construction | CZ15 | cDXHP | Cooling | 4709778.68 | 0
New Construction | CZ15 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ15 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ15 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXHP | Fans | 3232070.84 | 0
New Construction | CZ15 | cDXHP | Pumps | 1882.21 | 0
New Construction | CZ15 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXHP | Humidification | 0 | 0
New Construction | CZ15 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXHP | Water Systems | 0 | 448862.48
New Construction | CZ15 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ15 | cDXHP | Generators | 0 | 0
New Construction | CZ15 | cDXHP | Total End Uses | 14225631.1 | 5880593.59
New Construction | CZ16 | cDXHP | Heating | 184254.5 | 8938350.06
New Construction | CZ16 | cDXHP | Cooling | 1860177.81 | 0
New Construction | CZ16 | cDXHP | Interior Lighting | 1500585.11 | 0
New Construction | CZ16 | cDXHP | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXHP | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ16 | cDXHP | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXHP | Fans | 2693911.48 | 0
New Construction | CZ16 | cDXHP | Pumps | 1493.2 | 0
New Construction | CZ16 | cDXHP | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXHP | Humidification | 0 | 0
New Construction | CZ16 | cDXHP | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXHP | Water Systems | 0 | 597053.13
New Construction | CZ16 | cDXHP | Refrigeration | 0 | 0
New Construction | CZ16 | cDXHP | Generators | 0 | 0
New Construction | CZ16 | cDXHP | Total End Uses | 11008560.72 | 12183443.6
Existing | CZ01 | cDXOH | Heating | 0 | 13557662.33
Existing | CZ01 | cDXOH | Cooling | 85622.95 | 0
Existing | CZ01 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ01 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ01 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ01 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ01 | cDXOH | Fans | 3184113.85 | 0
Existing | CZ01 | cDXOH | Pumps | 1665.37 | 0
Existing | CZ01 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ01 | cDXOH | Humidification | 0 | 0
Existing | CZ01 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ01 | cDXOH | Water Systems | 0 | 660965.32
Existing | CZ01 | cDXOH | Refrigeration | 0 | 0
Existing | CZ01 | cDXOH | Generators | 0 | 0
Existing | CZ01 | cDXOH | Total End Uses | 10467824.31 | 16866668.06
Existing | CZ02 | cDXOH | Heating | 0 | 9043917.78
Existing | CZ02 | cDXOH | Cooling | 683224.68 | 0
Existing | CZ02 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ02 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ02 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ02 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ02 | cDXOH | Fans | 3340358.71 | 0
Existing | CZ02 | cDXOH | Pumps | 1879.8 | 0
Existing | CZ02 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ02 | cDXOH | Humidification | 0 | 0
Existing | CZ02 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ02 | cDXOH | Water Systems | 0 | 607368.28
Existing | CZ02 | cDXOH | Refrigeration | 0 | 0
Existing | CZ02 | cDXOH | Generators | 0 | 0
Existing | CZ02 | cDXOH | Total End Uses | 11221885.33 | 12299326.47
Existing | CZ03 | cDXOH | Heating | 0 | 7446180.25
Existing | CZ03 | cDXOH | Cooling | 346567.04 | 0
Existing | CZ03 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ03 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ03 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ03 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ03 | cDXOH | Fans | 3287669.14 | 0
Existing | CZ03 | cDXOH | Pumps | 1893.45 | 0
Existing | CZ03 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ03 | cDXOH | Humidification | 0 | 0
Existing | CZ03 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ03 | cDXOH | Water Systems | 0 | 604995.64
Existing | CZ03 | cDXOH | Refrigeration | 0 | 0
Existing | CZ03 | cDXOH | Generators | 0 | 0
Existing | CZ03 | cDXOH | Total End Uses | 10832551.76 | 10699216.3
Existing | CZ04 | cDXOH | Heating | 0 | 6559018.06
Existing | CZ04 | cDXOH | Cooling | 837194.19 | 0
Existing | CZ04 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ04 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ04 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ04 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ04 | cDXOH | Fans | 3357239.17 | 0
Existing | CZ04 | cDXOH | Pumps | 1946.58 | 0
Existing | CZ04 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ04 | cDXOH | Humidification | 0 | 0
Existing | CZ04 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ04 | cDXOH | Water Systems | 0 | 584210.73
Existing | CZ04 | cDXOH | Refrigeration | 0 | 0
Existing | CZ04 | cDXOH | Generators | 0 | 0
Existing | CZ04 | cDXOH | Total End Uses | 11392802.08 | 9791269.2
Existing | CZ05 | cDXOH | Heating | 0 | 7758641.22
Existing | CZ05 | cDXOH | Cooling | 454187.07 | 0
Existing | CZ05 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ05 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ05 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ05 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ05 | cDXOH | Fans | 3251844.02 | 0
Existing | CZ05 | cDXOH | Pumps | 1795.72 | 0
Existing | CZ05 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ05 | cDXOH | Humidification | 0 | 0
Existing | CZ05 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ05 | cDXOH | Water Systems | 0 | 605036.11
Existing | CZ05 | cDXOH | Refrigeration | 0 | 0
Existing | CZ05 | cDXOH | Generators | 0 | 0
Existing | CZ05 | cDXOH | Total End Uses | 10904248.95 | 11011717.74
Existing | CZ06 | cDXOH | Heating | 0 | 2940932.79
Existing | CZ06 | cDXOH | Cooling | 729675.22 | 0
Existing | CZ06 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ06 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ06 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ06 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ06 | cDXOH | Fans | 3274573.39 | 0
Existing | CZ06 | cDXOH | Pumps | 1954.13 | 0
Existing | CZ06 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ06 | cDXOH | Humidification | 0 | 0
Existing | CZ06 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ06 | cDXOH | Water Systems | 0 | 557322.13
Existing | CZ06 | cDXOH | Refrigeration | 0 | 0
Existing | CZ06 | cDXOH | Generators | 0 | 0
Existing | CZ06 | cDXOH | Total End Uses | 11202624.87 | 6146295.33
Existing | CZ07 | cDXOH | Heating | 0 | 2745490.73
Existing | CZ07 | cDXOH | Cooling | 870802.38 | 0
Existing | CZ07 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ07 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ07 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ07 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ07 | cDXOH | Fans | 3319286.6 | 0
Existing | CZ07 | cDXOH | Pumps | 2009.24 | 0
Existing | CZ07 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ07 | cDXOH | Humidification | 0 | 0
Existing | CZ07 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ07 | cDXOH | Water Systems | 0 | 550196.9
Existing | CZ07 | cDXOH | Refrigeration | 0 | 0
Existing | CZ07 | cDXOH | Generators | 0 | 0
Existing | CZ07 | cDXOH | Total End Uses | 11388520.36 | 5943728.04
Existing | CZ08 | cDXOH | Heating | 0 | 3441172.38
Existing | CZ08 | cDXOH | Cooling | 1132717.33 | 0
Existing | CZ08 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ08 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ08 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ08 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ08 | cDXOH | Fans | 3372575.77 | 0
Existing | CZ08 | cDXOH | Pumps | 2051.92 | 0
Existing | CZ08 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ08 | cDXOH | Humidification | 0 | 0
Existing | CZ08 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ08 | cDXOH | Water Systems | 0 | 549415.17
Existing | CZ08 | cDXOH | Refrigeration | 0 | 0
Existing | CZ08 | cDXOH | Generators | 0 | 0
Existing | CZ08 | cDXOH | Total End Uses | 11703767.16 | 6638627.96
Existing | CZ09 | cDXOH | Heating | 0 | 3051687.02
Existing | CZ09 | cDXOH | Cooling | 1319902.72 | 0
Existing | CZ09 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ09 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ09 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ09 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ09 | cDXOH | Fans | 3402603.82 | 0
Existing | CZ09 | cDXOH | Pumps | 2077.88 | 0
Existing | CZ09 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ09 | cDXOH | Humidification | 0 | 0
Existing | CZ09 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ09 | cDXOH | Water Systems | 0 | 541821.21
Existing | CZ09 | cDXOH | Refrigeration | 0 | 0
Existing | CZ09 | cDXOH | Generators | 0 | 0
Existing | CZ09 | cDXOH | Total End Uses | 11921006.55 | 6241548.64
Existing | CZ10 | cDXOH | Heating | 0 | 4512040.45
Existing | CZ10 | cDXOH | Cooling | 2042845.83 | 0
Existing | CZ10 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ10 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ10 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ10 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ10 | cDXOH | Fans | 3304878.47 | 0
Existing | CZ10 | cDXOH | Pumps | 2103.98 | 0
Existing | CZ10 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ10 | cDXOH | Humidification | 0 | 0
Existing | CZ10 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ10 | cDXOH | Water Systems | 0 | 537466.72
Existing | CZ10 | cDXOH | Refrigeration | 0 | 0
Existing | CZ10 | cDXOH | Generators | 0 | 0
Existing | CZ10 | cDXOH | Total End Uses | 12546250.42 | 7697547.59
Existing | CZ11 | cDXOH | Heating | 0 | 7258526.89
Existing | CZ11 | cDXOH | Cooling | 2442517.99 | 0
Existing | CZ11 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ11 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ11 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ11 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ11 | cDXOH | Fans | 3468648.03 | 0
Existing | CZ11 | cDXOH | Pumps | 2089.66 | 0
Existing | CZ11 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ11 | cDXOH | Humidification | 0 | 0
Existing | CZ11 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ11 | cDXOH | Water Systems | 0 | 549490.21
Existing | CZ11 | cDXOH | Refrigeration | 0 | 0
Existing | CZ11 | cDXOH | Generators | 0 | 0
Existing | CZ11 | cDXOH | Total End Uses | 13109677.82 | 10456057.5
Existing | CZ12 | cDXOH | Heating | 0 | 7385526.96
Existing | CZ12 | cDXOH | Cooling | 1807611.7 | 0
Existing | CZ12 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ12 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ12 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ12 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ12 | cDXOH | Fans | 3418403.55 | 0
Existing | CZ12 | cDXOH | Pumps | 2026.77 | 0
Existing | CZ12 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ12 | cDXOH | Humidification | 0 | 0
Existing | CZ12 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ12 | cDXOH | Water Systems | 0 | 564949.87
Existing | CZ12 | cDXOH | Refrigeration | 0 | 0
Existing | CZ12 | cDXOH | Generators | 0 | 0
Existing | CZ12 | cDXOH | Total End Uses | 12424464.15 | 10598517.25
Existing | CZ13 | cDXOH | Heating | 0 | 6146325.83
Existing | CZ13 | cDXOH | Cooling | 2740881.28 | 0
Existing | CZ13 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ13 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ13 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ13 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ13 | cDXOH | Fans | 3454948.37 | 0
Existing | CZ13 | cDXOH | Pumps | 2186.17 | 0
Existing | CZ13 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ13 | cDXOH | Humidification | 0 | 0
Existing | CZ13 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ13 | cDXOH | Water Systems | 0 | 533506.19
Existing | CZ13 | cDXOH | Refrigeration | 0 | 0
Existing | CZ13 | cDXOH | Generators | 0 | 0
Existing | CZ13 | cDXOH | Total End Uses | 13394437.95 | 9327872.44
Existing | CZ14 | cDXOH | Heating | 0 | 4840157.45
Existing | CZ14 | cDXOH | Cooling | 3687329.97 | 0
Existing | CZ14 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ14 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ14 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ14 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ14 | cDXOH | Fans | 3367305.87 | 0
Existing | CZ14 | cDXOH | Pumps | 2181.28 | 0
Existing | CZ14 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ14 | cDXOH | Humidification | 0 | 0
Existing | CZ14 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ14 | cDXOH | Water Systems | 0 | 506422.51
Existing | CZ14 | cDXOH | Refrigeration | 0 | 0
Existing | CZ14 | cDXOH | Generators | 0 | 0
Existing | CZ14 | cDXOH | Total End Uses | 14253239.26 | 7994620.38
Existing | CZ15 | cDXOH | Heating | 0 | 2631983.66
Existing | CZ15 | cDXOH | Cooling | 5182733.87 | 0
Existing | CZ15 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ15 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ15 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ15 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ15 | cDXOH | Fans | 3608717.39 | 0
Existing | CZ15 | cDXOH | Pumps | 2327.48 | 0
Existing | CZ15 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ15 | cDXOH | Humidification | 0 | 0
Existing | CZ15 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ15 | cDXOH | Water Systems | 0 | 449566.22
Existing | CZ15 | cDXOH | Refrigeration | 0 | 0
Existing | CZ15 | cDXOH | Generators | 0 | 0
Existing | CZ15 | cDXOH | Total End Uses | 15990200.87 | 5729590.29
Existing | CZ16 | cDXOH | Heating | 0 | 8807575.22
Existing | CZ16 | cDXOH | Cooling | 2065725.72 | 0
Existing | CZ16 | cDXOH | Interior Lighting | 2428283.52 | 0
Existing | CZ16 | cDXOH | Exterior Lighting | 0 | 0
Existing | CZ16 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ16 | cDXOH | Exterior Equipment | 0 | 0
Existing | CZ16 | cDXOH | Fans | 3036470.54 | 0
Existing | CZ16 | cDXOH | Pumps | 1839.3 | 0
Existing | CZ16 | cDXOH | Heat Rejection | 0 | 0
Existing | CZ16 | cDXOH | Humidification | 0 | 0
Existing | CZ16 | cDXOH | Heat Recovery | 0 | 0
Existing | CZ16 | cDXOH | Water Systems | 0 | 597418.74
Existing | CZ16 | cDXOH | Refrigeration | 0 | 0
Existing | CZ16 | cDXOH | Generators | 0 | 0
Existing | CZ16 | cDXOH | Total End Uses | 12300457.69 | 12053034.37
New Construction | CZ01 | cDXOH | Heating | 0 | 13931843.35
New Construction | CZ01 | cDXOH | Cooling | 78021.23 | 0
New Construction | CZ01 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ01 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ01 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ01 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ01 | cDXOH | Fans | 2955776.94 | 0
New Construction | CZ01 | cDXOH | Pumps | 1393.81 | 0
New Construction | CZ01 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ01 | cDXOH | Humidification | 0 | 0
New Construction | CZ01 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ01 | cDXOH | Water Systems | 0 | 660797.51
New Construction | CZ01 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ01 | cDXOH | Generators | 0 | 0
New Construction | CZ01 | cDXOH | Total End Uses | 9303915.71 | 17240681.27
New Construction | CZ02 | cDXOH | Heating | 0 | 9389719.64
New Construction | CZ02 | cDXOH | Cooling | 595574.28 | 0
New Construction | CZ02 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ02 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ02 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ02 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ02 | cDXOH | Fans | 3040890.94 | 0
New Construction | CZ02 | cDXOH | Pumps | 1536.02 | 0
New Construction | CZ02 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ02 | cDXOH | Humidification | 0 | 0
New Construction | CZ02 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ02 | cDXOH | Water Systems | 0 | 607102.6
New Construction | CZ02 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ02 | cDXOH | Generators | 0 | 0
New Construction | CZ02 | cDXOH | Total End Uses | 9906724.98 | 12644862.65
New Construction | CZ03 | cDXOH | Heating | 0 | 7836992.07
New Construction | CZ03 | cDXOH | Cooling | 295335.29 | 0
New Construction | CZ03 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ03 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ03 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ03 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ03 | cDXOH | Fans | 3012330.66 | 0
New Construction | CZ03 | cDXOH | Pumps | 1569.54 | 0
New Construction | CZ03 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ03 | cDXOH | Humidification | 0 | 0
New Construction | CZ03 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ03 | cDXOH | Water Systems | 0 | 604765.06
New Construction | CZ03 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ03 | cDXOH | Generators | 0 | 0
New Construction | CZ03 | cDXOH | Total End Uses | 9577959.21 | 11089797.55
New Construction | CZ04 | cDXOH | Heating | 0 | 6889756.53
New Construction | CZ04 | cDXOH | Cooling | 723609.26 | 0
New Construction | CZ04 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ04 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ04 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ04 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ04 | cDXOH | Fans | 3053004.03 | 0
New Construction | CZ04 | cDXOH | Pumps | 1586.95 | 0
New Construction | CZ04 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ04 | cDXOH | Humidification | 0 | 0
New Construction | CZ04 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ04 | cDXOH | Water Systems | 0 | 583896.94
New Construction | CZ04 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ04 | cDXOH | Generators | 0 | 0
New Construction | CZ04 | cDXOH | Total End Uses | 10046923.97 | 10121693.88
New Construction | CZ05 | cDXOH | Heating | 0 | 8167993.87
New Construction | CZ05 | cDXOH | Cooling | 389894.77 | 0
New Construction | CZ05 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ05 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ05 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ05 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ05 | cDXOH | Fans | 2978927.11 | 0
New Construction | CZ05 | cDXOH | Pumps | 1455.66 | 0
New Construction | CZ05 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ05 | cDXOH | Humidification | 0 | 0
New Construction | CZ05 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ05 | cDXOH | Water Systems | 0 | 604742.61
New Construction | CZ05 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ05 | cDXOH | Generators | 0 | 0
New Construction | CZ05 | cDXOH | Total End Uses | 9639001.26 | 11420776.89
New Construction | CZ06 | cDXOH | Heating | 0 | 3183498.18
New Construction | CZ06 | cDXOH | Cooling | 605507.57 | 0
New Construction | CZ06 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ06 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ06 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ06 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ06 | cDXOH | Fans | 2987774.25 | 0
New Construction | CZ06 | cDXOH | Pumps | 1585.4 | 0
New Construction | CZ06 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ06 | cDXOH | Humidification | 0 | 0
New Construction | CZ06 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ06 | cDXOH | Water Systems | 0 | 556959.41
New Construction | CZ06 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ06 | cDXOH | Generators | 0 | 0
New Construction | CZ06 | cDXOH | Total End Uses | 9863590.96 | 6388498
New Construction | CZ07 | cDXOH | Heating | 0 | 2957182.87
New Construction | CZ07 | cDXOH | Cooling | 721059.96 | 0
New Construction | CZ07 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ07 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ07 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ07 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ07 | cDXOH | Fans | 3040197.33 | 0
New Construction | CZ07 | cDXOH | Pumps | 1646.87 | 0
New Construction | CZ07 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ07 | cDXOH | Humidification | 0 | 0
New Construction | CZ07 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ07 | cDXOH | Water Systems | 0 | 549777.73
New Construction | CZ07 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ07 | cDXOH | Generators | 0 | 0
New Construction | CZ07 | cDXOH | Total End Uses | 10031627.89 | 6155001.01
New Construction | CZ08 | cDXOH | Heating | 0 | 3671631.52
New Construction | CZ08 | cDXOH | Cooling | 968125.25 | 0
New Construction | CZ08 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ08 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ08 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ08 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ08 | cDXOH | Fans | 3064047.03 | 0
New Construction | CZ08 | cDXOH | Pumps | 1661.61 | 0
New Construction | CZ08 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ08 | cDXOH | Humidification | 0 | 0
New Construction | CZ08 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ08 | cDXOH | Water Systems | 0 | 549000.7
New Construction | CZ08 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ08 | cDXOH | Generators | 0 | 0
New Construction | CZ08 | cDXOH | Total End Uses | 10302557.62 | 6868672.64
New Construction | CZ09 | cDXOH | Heating | 0 | 3253125.58
New Construction | CZ09 | cDXOH | Cooling | 1119045.6 | 0
New Construction | CZ09 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ09 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ09 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ09 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ09 | cDXOH | Fans | 3062892.65 | 0
New Construction | CZ09 | cDXOH | Pumps | 1675.65 | 0
New Construction | CZ09 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ09 | cDXOH | Humidification | 0 | 0
New Construction | CZ09 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ09 | cDXOH | Water Systems | 0 | 541342.29
New Construction | CZ09 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ09 | cDXOH | Generators | 0 | 0
New Construction | CZ09 | cDXOH | Total End Uses | 10452337.62 | 6442508.29
New Construction | CZ10 | cDXOH | Heating | 0 | 4728800.98
New Construction | CZ10 | cDXOH | Cooling | 1817269.81 | 0
New Construction | CZ10 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ10 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ10 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ10 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ10 | cDXOH | Fans | 2995986.26 | 0
New Construction | CZ10 | cDXOH | Pumps | 1697.01 | 0
New Construction | CZ10 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ10 | cDXOH | Humidification | 0 | 0
New Construction | CZ10 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ10 | cDXOH | Water Systems | 0 | 536930.06
New Construction | CZ10 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ10 | cDXOH | Generators | 0 | 0
New Construction | CZ10 | cDXOH | Total End Uses | 11083676.81 | 7913771.45
New Construction | CZ11 | cDXOH | Heating | 0 | 7453560.33
New Construction | CZ11 | cDXOH | Cooling | 2187603.02 | 0
New Construction | CZ11 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ11 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ11 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ11 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ11 | cDXOH | Fans | 3106062.84 | 0
New Construction | CZ11 | cDXOH | Pumps | 1679.1 | 0
New Construction | CZ11 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ11 | cDXOH | Humidification | 0 | 0
New Construction | CZ11 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ11 | cDXOH | Water Systems | 0 | 548933.87
New Construction | CZ11 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ11 | cDXOH | Generators | 0 | 0
New Construction | CZ11 | cDXOH | Total End Uses | 11564068.69 | 10650534.61
New Construction | CZ12 | cDXOH | Heating | 0 | 7636554.93
New Construction | CZ12 | cDXOH | Cooling | 1607906.5 | 0
New Construction | CZ12 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ12 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ12 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ12 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ12 | cDXOH | Fans | 3098196.84 | 0
New Construction | CZ12 | cDXOH | Pumps | 1619.11 | 0
New Construction | CZ12 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ12 | cDXOH | Humidification | 0 | 0
New Construction | CZ12 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ12 | cDXOH | Water Systems | 0 | 564575.01
New Construction | CZ12 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ12 | cDXOH | Generators | 0 | 0
New Construction | CZ12 | cDXOH | Total End Uses | 10976446.18 | 10849170.35
New Construction | CZ13 | cDXOH | Heating | 0 | 6336775.68
New Construction | CZ13 | cDXOH | Cooling | 2443915.7 | 0
New Construction | CZ13 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ13 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ13 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ13 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ13 | cDXOH | Fans | 3105996.51 | 0
New Construction | CZ13 | cDXOH | Pumps | 1774.7 | 0
New Construction | CZ13 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ13 | cDXOH | Humidification | 0 | 0
New Construction | CZ13 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ13 | cDXOH | Water Systems | 0 | 532804.86
New Construction | CZ13 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ13 | cDXOH | Generators | 0 | 0
New Construction | CZ13 | cDXOH | Total End Uses | 11820410.64 | 9517620.95
New Construction | CZ14 | cDXOH | Heating | 0 | 5007221.81
New Construction | CZ14 | cDXOH | Cooling | 3324279.32 | 0
New Construction | CZ14 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ14 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ14 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ14 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ14 | cDXOH | Fans | 2979992.49 | 0
New Construction | CZ14 | cDXOH | Pumps | 1770.64 | 0
New Construction | CZ14 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ14 | cDXOH | Humidification | 0 | 0
New Construction | CZ14 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ14 | cDXOH | Water Systems | 0 | 505755.99
New Construction | CZ14 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ14 | cDXOH | Generators | 0 | 0
New Construction | CZ14 | cDXOH | Total End Uses | 12574766.18 | 8161018.2
New Construction | CZ15 | cDXOH | Heating | 0 | 2786575.29
New Construction | CZ15 | cDXOH | Cooling | 4703150.5 | 0
New Construction | CZ15 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ15 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ15 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ15 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ15 | cDXOH | Fans | 3232152.65 | 0
New Construction | CZ15 | cDXOH | Pumps | 1882.9 | 0
New Construction | CZ15 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ15 | cDXOH | Humidification | 0 | 0
New Construction | CZ15 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ15 | cDXOH | Water Systems | 0 | 448937.29
New Construction | CZ15 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ15 | cDXOH | Generators | 0 | 0
New Construction | CZ15 | cDXOH | Total End Uses | 14205909.78 | 5883552.99
New Construction | CZ16 | cDXOH | Heating | 0 | 9001688.99
New Construction | CZ16 | cDXOH | Cooling | 1836409.71 | 0
New Construction | CZ16 | cDXOH | Interior Lighting | 1500585.11 | 0
New Construction | CZ16 | cDXOH | Exterior Lighting | 0 | 0
New Construction | CZ16 | cDXOH | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ16 | cDXOH | Exterior Equipment | 0 | 0
New Construction | CZ16 | cDXOH | Fans | 2703847.27 | 0
New Construction | CZ16 | cDXOH | Pumps | 1454.67 | 0
New Construction | CZ16 | cDXOH | Heat Rejection | 0 | 0
New Construction | CZ16 | cDXOH | Humidification | 0 | 0
New Construction | CZ16 | cDXOH | Heat Recovery | 0 | 0
New Construction | CZ16 | cDXOH | Water Systems | 0 | 597084.19
New Construction | CZ16 | cDXOH | Refrigeration | 0 | 0
New Construction | CZ16 | cDXOH | Generators | 0 | 0
New Construction | CZ16 | cDXOH | Total End Uses | 10810435.38 | 12246813.59
Existing | CZ01 | cPVVG | Heating | 0 | 14420202.77
Existing | CZ01 | cPVVG | Cooling | 90439.53 | 0
Existing | CZ01 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ01 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ01 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ01 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ01 | cPVVG | Fans | 2659512.08 | 0
Existing | CZ01 | cPVVG | Pumps | 1661.34 | 0
Existing | CZ01 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ01 | cPVVG | Humidification | 0 | 0
Existing | CZ01 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ01 | cPVVG | Water Systems | 0 | 660961.95
Existing | CZ01 | cPVVG | Refrigeration | 0 | 0
Existing | CZ01 | cPVVG | Generators | 0 | 0
Existing | CZ01 | cPVVG | Total End Uses | 9948035.08 | 17729205.13
Existing | CZ02 | cPVVG | Heating | 0 | 9578025.06
Existing | CZ02 | cPVVG | Cooling | 674726.6 | 0
Existing | CZ02 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ02 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ02 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ02 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ02 | cPVVG | Fans | 2759874.16 | 0
Existing | CZ02 | cPVVG | Pumps | 1879.77 | 0
Existing | CZ02 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ02 | cPVVG | Humidification | 0 | 0
Existing | CZ02 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ02 | cPVVG | Water Systems | 0 | 607368.46
Existing | CZ02 | cPVVG | Refrigeration | 0 | 0
Existing | CZ02 | cPVVG | Generators | 0 | 0
Existing | CZ02 | cPVVG | Total End Uses | 10632902.67 | 12833433.94
Existing | CZ03 | cPVVG | Heating | 0 | 7797199.32
Existing | CZ03 | cPVVG | Cooling | 351922.24 | 0
Existing | CZ03 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ03 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ03 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ03 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ03 | cPVVG | Fans | 2711261.35 | 0
Existing | CZ03 | cPVVG | Pumps | 1888.04 | 0
Existing | CZ03 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ03 | cPVVG | Humidification | 0 | 0
Existing | CZ03 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ03 | cPVVG | Water Systems | 0 | 605001.35
Existing | CZ03 | cPVVG | Refrigeration | 0 | 0
Existing | CZ03 | cPVVG | Generators | 0 | 0
Existing | CZ03 | cPVVG | Total End Uses | 10261493.76 | 11050241.08
Existing | CZ04 | cPVVG | Heating | 0 | 6870538.26
Existing | CZ04 | cPVVG | Cooling | 828039.97 | 0
Existing | CZ04 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ04 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ04 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ04 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ04 | cPVVG | Fans | 2782088.97 | 0
Existing | CZ04 | cPVVG | Pumps | 1942.21 | 0
Existing | CZ04 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ04 | cPVVG | Humidification | 0 | 0
Existing | CZ04 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ04 | cPVVG | Water Systems | 0 | 584243.37
Existing | CZ04 | cPVVG | Refrigeration | 0 | 0
Existing | CZ04 | cPVVG | Generators | 0 | 0
Existing | CZ04 | cPVVG | Total End Uses | 10808493.28 | 10102822.04
Existing | CZ05 | cPVVG | Heating | 0 | 8074552.58
Existing | CZ05 | cPVVG | Cooling | 454214.32 | 0
Existing | CZ05 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ05 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ05 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ05 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ05 | cPVVG | Fans | 2693557.95 | 0
Existing | CZ05 | cPVVG | Pumps | 1789.34 | 0
Existing | CZ05 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ05 | cPVVG | Humidification | 0 | 0
Existing | CZ05 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ05 | cPVVG | Water Systems | 0 | 605012.35
Existing | CZ05 | cPVVG | Refrigeration | 0 | 0
Existing | CZ05 | cPVVG | Generators | 0 | 0
Existing | CZ05 | cPVVG | Total End Uses | 10345983.75 | 11327605.34
Existing | CZ06 | cPVVG | Heating | 0 | 3023882.21
Existing | CZ06 | cPVVG | Cooling | 734761 | 0
Existing | CZ06 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ06 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ06 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ06 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ06 | cPVVG | Fans | 2734252.45 | 0
Existing | CZ06 | cPVVG | Pumps | 1951.15 | 0
Existing | CZ06 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ06 | cPVVG | Humidification | 0 | 0
Existing | CZ06 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ06 | cPVVG | Water Systems | 0 | 557318.96
Existing | CZ06 | cPVVG | Refrigeration | 0 | 0
Existing | CZ06 | cPVVG | Generators | 0 | 0
Existing | CZ06 | cPVVG | Total End Uses | 10667386.74 | 6229241.58
Existing | CZ07 | cPVVG | Heating | 0 | 2823020.11
Existing | CZ07 | cPVVG | Cooling | 859362.42 | 0
Existing | CZ07 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ07 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ07 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ07 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ07 | cPVVG | Fans | 2792616.78 | 0
Existing | CZ07 | cPVVG | Pumps | 2006.91 | 0
Existing | CZ07 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ07 | cPVVG | Humidification | 0 | 0
Existing | CZ07 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ07 | cPVVG | Water Systems | 0 | 550197.57
Existing | CZ07 | cPVVG | Refrigeration | 0 | 0
Existing | CZ07 | cPVVG | Generators | 0 | 0
Existing | CZ07 | cPVVG | Total End Uses | 10850408.24 | 6021258.09
Existing | CZ08 | cPVVG | Heating | 0 | 3556067.37
Existing | CZ08 | cPVVG | Cooling | 1118685.03 | 0
Existing | CZ08 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ08 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ08 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ08 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ08 | cPVVG | Fans | 2820050.88 | 0
Existing | CZ08 | cPVVG | Pumps | 2048.92 | 0
Existing | CZ08 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ08 | cPVVG | Humidification | 0 | 0
Existing | CZ08 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ08 | cPVVG | Water Systems | 0 | 549442.54
Existing | CZ08 | cPVVG | Refrigeration | 0 | 0
Existing | CZ08 | cPVVG | Generators | 0 | 0
Existing | CZ08 | cPVVG | Total End Uses | 11137206.96 | 6753550.32
Existing | CZ09 | cPVVG | Heating | 0 | 3149476.76
Existing | CZ09 | cPVVG | Cooling | 1298496.64 | 0
Existing | CZ09 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ09 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ09 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ09 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ09 | cPVVG | Fans | 2833121.89 | 0
Existing | CZ09 | cPVVG | Pumps | 2075.44 | 0
Existing | CZ09 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ09 | cPVVG | Humidification | 0 | 0
Existing | CZ09 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ09 | cPVVG | Water Systems | 0 | 541823.06
Existing | CZ09 | cPVVG | Refrigeration | 0 | 0
Existing | CZ09 | cPVVG | Generators | 0 | 0
Existing | CZ09 | cPVVG | Total End Uses | 11330116.1 | 6339340.23
Existing | CZ10 | cPVVG | Heating | 0 | 4717716.26
Existing | CZ10 | cPVVG | Cooling | 2009497.22 | 0
Existing | CZ10 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ10 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ10 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ10 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ10 | cPVVG | Fans | 2752859.07 | 0
Existing | CZ10 | cPVVG | Pumps | 2101.08 | 0
Existing | CZ10 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ10 | cPVVG | Humidification | 0 | 0
Existing | CZ10 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ10 | cPVVG | Water Systems | 0 | 537463.04
Existing | CZ10 | cPVVG | Refrigeration | 0 | 0
Existing | CZ10 | cPVVG | Generators | 0 | 0
Existing | CZ10 | cPVVG | Total End Uses | 11960879.5 | 7903219.71
Existing | CZ11 | cPVVG | Heating | 0 | 7783132.82
Existing | CZ11 | cPVVG | Cooling | 2410109.4 | 0
Existing | CZ11 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ11 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ11 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ11 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ11 | cPVVG | Fans | 2877628.15 | 0
Existing | CZ11 | cPVVG | Pumps | 2089.61 | 0
Existing | CZ11 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ11 | cPVVG | Humidification | 0 | 0
Existing | CZ11 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ11 | cPVVG | Water Systems | 0 | 549485.1
Existing | CZ11 | cPVVG | Refrigeration | 0 | 0
Existing | CZ11 | cPVVG | Generators | 0 | 0
Existing | CZ11 | cPVVG | Total End Uses | 12486249.29 | 10980658.33
Existing | CZ12 | cPVVG | Heating | 0 | 7873864.43
Existing | CZ12 | cPVVG | Cooling | 1783536.09 | 0
Existing | CZ12 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ12 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ12 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ12 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ12 | cPVVG | Fans | 2859478.65 | 0
Existing | CZ12 | cPVVG | Pumps | 2027.79 | 0
Existing | CZ12 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ12 | cPVVG | Humidification | 0 | 0
Existing | CZ12 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ12 | cPVVG | Water Systems | 0 | 564940.74
Existing | CZ12 | cPVVG | Refrigeration | 0 | 0
Existing | CZ12 | cPVVG | Generators | 0 | 0
Existing | CZ12 | cPVVG | Total End Uses | 11841464.66 | 11086845.58
Existing | CZ13 | cPVVG | Heating | 0 | 6550463.64
Existing | CZ13 | cPVVG | Cooling | 2705209.62 | 0
Existing | CZ13 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ13 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ13 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ13 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ13 | cPVVG | Fans | 2890904.76 | 0
Existing | CZ13 | cPVVG | Pumps | 2184.86 | 0
Existing | CZ13 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ13 | cPVVG | Humidification | 0 | 0
Existing | CZ13 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ13 | cPVVG | Water Systems | 0 | 533490.66
Existing | CZ13 | cPVVG | Refrigeration | 0 | 0
Existing | CZ13 | cPVVG | Generators | 0 | 0
Existing | CZ13 | cPVVG | Total End Uses | 12794721.36 | 9731994.71
Existing | CZ14 | cPVVG | Heating | 0 | 5126232.9
Existing | CZ14 | cPVVG | Cooling | 3636537.82 | 0
Existing | CZ14 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ14 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ14 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ14 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ14 | cPVVG | Fans | 2780658.27 | 0
Existing | CZ14 | cPVVG | Pumps | 2181.05 | 0
Existing | CZ14 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ14 | cPVVG | Humidification | 0 | 0
Existing | CZ14 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ14 | cPVVG | Water Systems | 0 | 506424.14
Existing | CZ14 | cPVVG | Refrigeration | 0 | 0
Existing | CZ14 | cPVVG | Generators | 0 | 0
Existing | CZ14 | cPVVG | Total End Uses | 13615799.27 | 8280697.45
Existing | CZ15 | cPVVG | Heating | 0 | 2708940.6
Existing | CZ15 | cPVVG | Cooling | 5113696.77 | 0
Existing | CZ15 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ15 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ15 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ15 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ15 | cPVVG | Fans | 3083279.33 | 0
Existing | CZ15 | cPVVG | Pumps | 2326.49 | 0
Existing | CZ15 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ15 | cPVVG | Humidification | 0 | 0
Existing | CZ15 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ15 | cPVVG | Water Systems | 0 | 449554.45
Existing | CZ15 | cPVVG | Refrigeration | 0 | 0
Existing | CZ15 | cPVVG | Generators | 0 | 0
Existing | CZ15 | cPVVG | Total End Uses | 15395724.73 | 5806535.46
Existing | CZ16 | cPVVG | Heating | 0 | 9593155.34
Existing | CZ16 | cPVVG | Cooling | 2037292.47 | 0
Existing | CZ16 | cPVVG | Interior Lighting | 2428283.52 | 0
Existing | CZ16 | cPVVG | Exterior Lighting | 0 | 0
Existing | CZ16 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
Existing | CZ16 | cPVVG | Exterior Equipment | 0 | 0
Existing | CZ16 | cPVVG | Fans | 2382978.89 | 0
Existing | CZ16 | cPVVG | Pumps | 1860.08 | 0
Existing | CZ16 | cPVVG | Heat Rejection | 0 | 0
Existing | CZ16 | cPVVG | Humidification | 0 | 0
Existing | CZ16 | cPVVG | Heat Recovery | 0 | 0
Existing | CZ16 | cPVVG | Water Systems | 0 | 597407.6
Existing | CZ16 | cPVVG | Refrigeration | 0 | 0
Existing | CZ16 | cPVVG | Generators | 0 | 0
Existing | CZ16 | cPVVG | Total End Uses | 11618553.58 | 12838603.35
New Construction | CZ01 | cPVVG | Heating | 0 | 14707253.95
New Construction | CZ01 | cPVVG | Cooling | 83758.61 | 0
New Construction | CZ01 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ01 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ01 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ01 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ01 | cPVVG | Fans | 2607461.39 | 0
New Construction | CZ01 | cPVVG | Pumps | 1398.55 | 0
New Construction | CZ01 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ01 | cPVVG | Humidification | 0 | 0
New Construction | CZ01 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ01 | cPVVG | Water Systems | 0 | 660767.67
New Construction | CZ01 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ01 | cPVVG | Generators | 0 | 0
New Construction | CZ01 | cPVVG | Total End Uses | 8961342.27 | 18016062.03
New Construction | CZ02 | cPVVG | Heating | 0 | 9865035.39
New Construction | CZ02 | cPVVG | Cooling | 592489.22 | 0
New Construction | CZ02 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ02 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ02 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ02 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ02 | cPVVG | Fans | 2654735.15 | 0
New Construction | CZ02 | cPVVG | Pumps | 1540.98 | 0
New Construction | CZ02 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ02 | cPVVG | Humidification | 0 | 0
New Construction | CZ02 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ02 | cPVVG | Water Systems | 0 | 607082.02
New Construction | CZ02 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ02 | cPVVG | Generators | 0 | 0
New Construction | CZ02 | cPVVG | Total End Uses | 9517489.08 | 13120157.81
New Construction | CZ03 | cPVVG | Heating | 0 | 8160996.08
New Construction | CZ03 | cPVVG | Cooling | 299803.75 | 0
New Construction | CZ03 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ03 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ03 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ03 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ03 | cPVVG | Fans | 2625528.13 | 0
New Construction | CZ03 | cPVVG | Pumps | 1569.03 | 0
New Construction | CZ03 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ03 | cPVVG | Humidification | 0 | 0
New Construction | CZ03 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ03 | cPVVG | Water Systems | 0 | 604736.18
New Construction | CZ03 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ03 | cPVVG | Generators | 0 | 0
New Construction | CZ03 | cPVVG | Total End Uses | 9195624.65 | 11413772.67
New Construction | CZ04 | cPVVG | Heating | 0 | 7173822.46
New Construction | CZ04 | cPVVG | Cooling | 717558.89 | 0
New Construction | CZ04 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ04 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ04 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ04 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ04 | cPVVG | Fans | 2667821.14 | 0
New Construction | CZ04 | cPVVG | Pumps | 1586.11 | 0
New Construction | CZ04 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ04 | cPVVG | Humidification | 0 | 0
New Construction | CZ04 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ04 | cPVVG | Water Systems | 0 | 583886.91
New Construction | CZ04 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ04 | cPVVG | Generators | 0 | 0
New Construction | CZ04 | cPVVG | Total End Uses | 9655689.86 | 10405749.79
New Construction | CZ05 | cPVVG | Heating | 0 | 8462412.99
New Construction | CZ05 | cPVVG | Cooling | 391410.69 | 0
New Construction | CZ05 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ05 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ05 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ05 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ05 | cPVVG | Fans | 2603582.44 | 0
New Construction | CZ05 | cPVVG | Pumps | 1454.39 | 0
New Construction | CZ05 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ05 | cPVVG | Humidification | 0 | 0
New Construction | CZ05 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ05 | cPVVG | Water Systems | 0 | 604756.28
New Construction | CZ05 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ05 | cPVVG | Generators | 0 | 0
New Construction | CZ05 | cPVVG | Total End Uses | 9265171.25 | 11715209.68
New Construction | CZ06 | cPVVG | Heating | 0 | 3261092.07
New Construction | CZ06 | cPVVG | Cooling | 607506.49 | 0
New Construction | CZ06 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ06 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ06 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ06 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ06 | cPVVG | Fans | 2620550.46 | 0
New Construction | CZ06 | cPVVG | Pumps | 1584.46 | 0
New Construction | CZ06 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ06 | cPVVG | Humidification | 0 | 0
New Construction | CZ06 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ06 | cPVVG | Water Systems | 0 | 556891.17
New Construction | CZ06 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ06 | cPVVG | Generators | 0 | 0
New Construction | CZ06 | cPVVG | Total End Uses | 9498365.14 | 6466023.65
New Construction | CZ07 | cPVVG | Heating | 0 | 3030854.41
New Construction | CZ07 | cPVVG | Cooling | 711748.99 | 0
New Construction | CZ07 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ07 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ07 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ07 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ07 | cPVVG | Fans | 2680961.62 | 0
New Construction | CZ07 | cPVVG | Pumps | 1646.38 | 0
New Construction | CZ07 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ07 | cPVVG | Humidification | 0 | 0
New Construction | CZ07 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ07 | cPVVG | Water Systems | 0 | 549812.12
New Construction | CZ07 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ07 | cPVVG | Generators | 0 | 0
New Construction | CZ07 | cPVVG | Total End Uses | 9663080.71 | 6228706.93
New Construction | CZ08 | cPVVG | Heating | 0 | 3779517.39
New Construction | CZ08 | cPVVG | Cooling | 957653.95 | 0
New Construction | CZ08 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ08 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ08 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ08 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ08 | cPVVG | Fans | 2692539.88 | 0
New Construction | CZ08 | cPVVG | Pumps | 1660.82 | 0
New Construction | CZ08 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ08 | cPVVG | Humidification | 0 | 0
New Construction | CZ08 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ08 | cPVVG | Water Systems | 0 | 548972.19
New Construction | CZ08 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ08 | cPVVG | Generators | 0 | 0
New Construction | CZ08 | cPVVG | Total End Uses | 9920578.39 | 6976529.99
New Construction | CZ09 | cPVVG | Heating | 0 | 3344187.57
New Construction | CZ09 | cPVVG | Cooling | 1103437.26 | 0
New Construction | CZ09 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ09 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ09 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ09 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ09 | cPVVG | Fans | 2680028.02 | 0
New Construction | CZ09 | cPVVG | Pumps | 1674.6 | 0
New Construction | CZ09 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ09 | cPVVG | Humidification | 0 | 0
New Construction | CZ09 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ09 | cPVVG | Water Systems | 0 | 541312.31
New Construction | CZ09 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ09 | cPVVG | Generators | 0 | 0
New Construction | CZ09 | cPVVG | Total End Uses | 10053863.61 | 6533540.29
New Construction | CZ10 | cPVVG | Heating | 0 | 4918720.44
New Construction | CZ10 | cPVVG | Cooling | 1795944.16 | 0
New Construction | CZ10 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ10 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ10 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ10 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ10 | cPVVG | Fans | 2612364.55 | 0
New Construction | CZ10 | cPVVG | Pumps | 1696.16 | 0
New Construction | CZ10 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ10 | cPVVG | Humidification | 0 | 0
New Construction | CZ10 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ10 | cPVVG | Water Systems | 0 | 536963.03
New Construction | CZ10 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ10 | cPVVG | Generators | 0 | 0
New Construction | CZ10 | cPVVG | Total End Uses | 10678728.59 | 8103723.89
New Construction | CZ11 | cPVVG | Heating | 0 | 7920101.62
New Construction | CZ11 | cPVVG | Cooling | 2169340.19 | 0
New Construction | CZ11 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ11 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ11 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ11 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ11 | cPVVG | Fans | 2707227.5 | 0
New Construction | CZ11 | cPVVG | Pumps | 1685.6 | 0
New Construction | CZ11 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ11 | cPVVG | Humidification | 0 | 0
New Construction | CZ11 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ11 | cPVVG | Water Systems | 0 | 548940.05
New Construction | CZ11 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ11 | cPVVG | Generators | 0 | 0
New Construction | CZ11 | cPVVG | Total End Uses | 11146977.03 | 11117082.09
New Construction | CZ12 | cPVVG | Heating | 0 | 8075260.84
New Construction | CZ12 | cPVVG | Cooling | 1594066.62 | 0
New Construction | CZ12 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ12 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ12 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ12 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ12 | cPVVG | Fans | 2721689.7 | 0
New Construction | CZ12 | cPVVG | Pumps | 1626.18 | 0
New Construction | CZ12 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ12 | cPVVG | Humidification | 0 | 0
New Construction | CZ12 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ12 | cPVVG | Water Systems | 0 | 564522.95
New Construction | CZ12 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ12 | cPVVG | Generators | 0 | 0
New Construction | CZ12 | cPVVG | Total End Uses | 10586106.23 | 11287824.2
New Construction | CZ13 | cPVVG | Heating | 0 | 6707707.59
New Construction | CZ13 | cPVVG | Cooling | 2422376.22 | 0
New Construction | CZ13 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ13 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ13 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ13 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ13 | cPVVG | Fans | 2722036.38 | 0
New Construction | CZ13 | cPVVG | Pumps | 1778.17 | 0
New Construction | CZ13 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ13 | cPVVG | Humidification | 0 | 0
New Construction | CZ13 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ13 | cPVVG | Water Systems | 0 | 532860.14
New Construction | CZ13 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ13 | cPVVG | Generators | 0 | 0
New Construction | CZ13 | cPVVG | Total End Uses | 11414914.49 | 9888608.14
New Construction | CZ14 | cPVVG | Heating | 0 | 5280131.63
New Construction | CZ14 | cPVVG | Cooling | 3294209.95 | 0
New Construction | CZ14 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ14 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ14 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ14 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ14 | cPVVG | Fans | 2582838.63 | 0
New Construction | CZ14 | cPVVG | Pumps | 1772.65 | 0
New Construction | CZ14 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ14 | cPVVG | Humidification | 0 | 0
New Construction | CZ14 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ14 | cPVVG | Water Systems | 0 | 505709.22
New Construction | CZ14 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ14 | cPVVG | Generators | 0 | 0
New Construction | CZ14 | cPVVG | Total End Uses | 12147544.96 | 8433881.26
New Construction | CZ15 | cPVVG | Heating | 0 | 2870732.17
New Construction | CZ15 | cPVVG | Cooling | 4662215.85 | 0
New Construction | CZ15 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ15 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ15 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ15 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ15 | cPVVG | Fans | 2883073.02 | 0
New Construction | CZ15 | cPVVG | Pumps | 1882.74 | 0
New Construction | CZ15 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ15 | cPVVG | Humidification | 0 | 0
New Construction | CZ15 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ15 | cPVVG | Water Systems | 0 | 448838.92
New Construction | CZ15 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ15 | cPVVG | Generators | 0 | 0
New Construction | CZ15 | cPVVG | Total End Uses | 13815895.34 | 5967611.49
New Construction | CZ16 | cPVVG | Heating | 0 | 9719110.97
New Construction | CZ16 | cPVVG | Cooling | 1821914.17 | 0
New Construction | CZ16 | cPVVG | Interior Lighting | 1500585.11 | 0
New Construction | CZ16 | cPVVG | Exterior Lighting | 0 | 0
New Construction | CZ16 | cPVVG | Interior Equipment | 4768138.62 | 2648040.41
New Construction | CZ16 | cPVVG | Exterior Equipment | 0 | 0
New Construction | CZ16 | cPVVG | Fans | 2251083.36 | 0
New Construction | CZ16 | cPVVG | Pumps | 1492.87 | 0
New Construction | CZ16 | cPVVG | Heat Rejection | 0 | 0
New Construction | CZ16 | cPVVG | Humidification | 0 | 0
New Construction | CZ16 | cPVVG | Heat Recovery | 0 | 0
New Construction | CZ16 | cPVVG | Water Systems | 0 | 597036.12
New Construction | CZ16 | cPVVG | Refrigeration | 0 | 0
New Construction | CZ16 | cPVVG | Generators | 0 | 0
New Construction | CZ16 | cPVVG | Total End Uses | 10343214.13 | 12964187.5

## PV
PV - Manufacturing Biotech (NA)

## EV Charger
EV Charger - Manufacturing Biotech (NA)

## Raw_building (hidden)
Building Type | Building Category | Roof Type | Window Wall Ratio (%)
Manufacturing Biotech | Nonresidential | Flat Roof | 12

## Raw_windowdimensionsillheight (hidden)
Window Name | Width [ft] | Height [ft] | Sill Height [ft]
EL1 EAST WIN (G.E2.E2.W1) | 109.51 | 2.99 | 4.5
EL1 NORTH WIN (G.N3.E3.W1) | 657.28 | 2.99 | 4.5
EL1 SOUTH WIN (G.S1.E1.W1) | 657.28 | 2.99 | 4.5
EL1 WEST WIN (G.W4.E4.W1) | 109.51 | 2.99 | 4.5

## Raw_shadinggeometry (hidden)
Shading Name | Width [ft] | Length [ft]
No Shading

## Raw_zonesummary (hidden)
Vintage | Space | Zone Name | Conditioned | Area (Excluding Plenums and CrawlSpace) (ft2) | Area (Including Plenums and CrawlSpace) (ft2) | Width (ft) | Length (ft) | Volume (ft3) | Multipliers | People (Persons/1000 ft2) | Lighting (Btu/h-ft2) | Plug Loads (Btu/h-ft2) | Outdoor Air Flow per Person (cfm/person) | Outdoor Air Flow per Zone Floor Area (cfm/ft2) | Zone Type | HVAC System Identifier | Schedule Identifier | Height (ft)
Existing | COMPUTER EL1 CORE SPC (G.C8) | COMPUTER EL1 CORE SPC (G.C8) | Yes | 3997.96 | 3997.96 | 26.21 | 152.56 | 35983.42 | 1 | 1.5 | 3.7719 | 68.2333 | 0.0 | 0.15 | Computer | Customized | Computer room | 9.0004
Existing | CONFERENCE EL1 CORE SPC (G.C7) | CONFERENCE EL1 CORE SPC (G.C7) | Yes | 3999.03 | 3999.03 | 26.21 | 152.56 | 35993.03 | 1 | 33.33 | 4.8319 | 3.4117 | 0.0 | 0.5 | Conference | Main | Office | 9.0004
Existing | CORRIDOR EL1 CORE SPC (G.C6) | CORRIDOR EL1 CORE SPC (G.C6) | Yes | 40004.04 | 40004.04 | 262.2 | 152.56 | 360051.18 | 1 | 5 | 2.1238 | 0 | 0.0 | 0.15 | Corridor | Main | Office | 9.0004
Existing | DINING EL1 CORE SPC (G.C9) | DINING EL1 CORE SPC (G.C9) | Yes | 5998.85 | 5998.85 | 39.3 | 152.56 | 53987.72 | 1 | 33.33 | 4.1409 | 2.5588 | 0.0 | 0.5 | Dining_fast | Main | Office | 8.9997
Existing | EL1 CORE PLNM (G.C16) | EL1 CORE PLNM (G.C16) | No | 0 | 90670.84 | 594.32 | 152.56 | 544051.58 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
Existing | EL1 CORE PLNM (G.C17) | EL1 CORE PLNM (G.C17) | No | 0 | 40003.73 | 262.2 | 152.56 | 240035.65 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
Existing | EL1 CORE PLNM (G.C18) | EL1 CORE PLNM (G.C18) | No | 0 | 3999.03 | 26.21 | 152.56 | 23995.36 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
Existing | EL1 CORE PLNM (G.C19) | EL1 CORE PLNM (G.C19) | No | 0 | 3997.96 | 26.21 | 152.56 | 23990.47 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0007
Existing | EL1 CORE PLNM (G.C20) | EL1 CORE PLNM (G.C20) | No | 0 | 5998.85 | 39.3 | 152.56 | 35991.81 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 5.9998
Existing | EL1 CORE PLNM (G.C21) | EL1 CORE PLNM (G.C21) | No | 0 | 1999.36 | 13.09 | 152.56 | 11996.76 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
Existing | EL1 CORE PLNM (G.C22) | EL1 CORE PLNM (G.C22) | No | 0 | 15878.95 | 104.07 | 152.56 | 95284.47 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0007
Existing | EL1 EAST PERIM PLNM (G.E13) | EL1 EAST PERIM PLNM (G.E13) | No | 0 | 2513.5 | 21.23 | 182.55 | 15081.71 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
Existing | EL1 NORTH PERIM PLNM (G.N14) | EL1 NORTH PERIM PLNM (G.N14) | No | 0 | 16208.33 | 1095.44 | 21.23 | 97256.41 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0004
Existing | EL1 SOUTH PERIM PLNM (G.S12) | EL1 SOUTH PERIM PLNM (G.S12) | No | 0 | 16208.33 | 1095.44 | 21.23 | 97254.59 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
Existing | EL1 WEST PERIM PLNM (G.W15) | EL1 WEST PERIM PLNM (G.W15) | No | 0 | 2513.5 | 152.56 | 21.23 | 15081.71 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
Existing | KITCHEN EL1 CORE SPC (G.C10) | KITCHEN EL1 CORE SPC (G.C10) | Yes | 2000.13 | 2000.13 | 13.12 | 152.56 | 17995.14 | 1 | 2.5 | 5.6273 | 26.4716 | 0.0 | 0.15 | Kitchen | Customized | Kitchen | 8.997
Existing | LAB EL1 CORE SPC (G.C5) | LAB EL1 CORE SPC (G.C5) | Yes | 90670.84 | 90670.84 | 594.32 | 152.56 | 816077.38 | 1 | 5 | 4.5175 | 20.4693 | 0.0 | 1.0 | Lab | Customized | lab | 9.0004
Existing | OFFICE EL1 CORE SPC (G.C11) | OFFICE EL1 CORE SPC (G.C11) | Yes | 15879.72 | 15879.72 | 104.1 | 152.56 | 142926.71 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0006
Existing | OFFICE EL1 EAST PERIM SPC (G.E2) | OFFICE EL1 EAST PERIM SPC (G.E2) | Yes | 2513.5 | 2513.5 | 21.23 | 182.55 | 22622.56 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
Existing | OFFICE EL1 NORTH PERIM SPC (G.N3) | OFFICE EL1 NORTH PERIM SPC (G.N3) | Yes | 16208.33 | 16208.33 | 1095.44 | 21.23 | 145887.13 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0008
Existing | OFFICE EL1 SOUTH PERIM SPC (G.S1) | OFFICE EL1 SOUTH PERIM SPC (G.S1) | Yes | 16208.33 | 16208.33 | 1095.44 | 21.23 | 145881.65 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
Existing | OFFICE EL1 WEST PERIM SPC (G.W4) | OFFICE EL1 WEST PERIM SPC (G.W4) | Yes | 2513.5 | 2513.5 | 152.56 | 21.23 | 22622.56 | 1 | 5 | 4.2664 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
New Construction | COMPUTER EL1 CORE SPC (G.C8) | COMPUTER EL1 CORE SPC (G.C8) | Yes | 3997.96 | 3997.96 | 26.21 | 152.56 | 35983.42 | 1 | 1.5 | 1.7058 | 68.2333 | 0.0 | 0.15 | Computer | Customized | Computer room | 9.0004
New Construction | CONFERENCE EL1 CORE SPC (G.C7) | CONFERENCE EL1 CORE SPC (G.C7) | Yes | 3999.03 | 3999.03 | 26.21 | 152.56 | 35993.03 | 1 | 33.33 | 2.5588 | 3.4117 | 0.0 | 0.5 | Conference | Main | Office | 9.0004
New Construction | CORRIDOR EL1 CORE SPC (G.C6) | CORRIDOR EL1 CORE SPC (G.C6) | Yes | 40004.04 | 40004.04 | 262.2 | 152.56 | 360051.18 | 1 | 5 | 1.3647 | 0 | 0.0 | 0.15 | Corridor | Main | Office | 9.0004
New Construction | DINING EL1 CORE SPC (G.C9) | DINING EL1 CORE SPC (G.C9) | Yes | 5998.85 | 5998.85 | 39.3 | 152.56 | 53987.72 | 1 | 33.33 | 1.5353 | 2.5588 | 0.0 | 0.5 | Dining_fast | Main | Office | 8.9997
New Construction | EL1 CORE PLNM (G.C16) | EL1 CORE PLNM (G.C16) | No | 0 | 90670.84 | 594.32 | 152.56 | 544051.58 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
New Construction | EL1 CORE PLNM (G.C17) | EL1 CORE PLNM (G.C17) | No | 0 | 40003.73 | 262.2 | 152.56 | 240035.65 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
New Construction | EL1 CORE PLNM (G.C18) | EL1 CORE PLNM (G.C18) | No | 0 | 3999.03 | 26.21 | 152.56 | 23995.36 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
New Construction | EL1 CORE PLNM (G.C19) | EL1 CORE PLNM (G.C19) | No | 0 | 3997.96 | 26.21 | 152.56 | 23990.47 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0007
New Construction | EL1 CORE PLNM (G.C20) | EL1 CORE PLNM (G.C20) | No | 0 | 5998.85 | 39.3 | 152.56 | 35991.81 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 5.9998
New Construction | EL1 CORE PLNM (G.C21) | EL1 CORE PLNM (G.C21) | No | 0 | 1999.36 | 13.09 | 152.56 | 11996.76 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
New Construction | EL1 CORE PLNM (G.C22) | EL1 CORE PLNM (G.C22) | No | 0 | 15878.95 | 104.07 | 152.56 | 95284.47 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0007
New Construction | EL1 EAST PERIM PLNM (G.E13) | EL1 EAST PERIM PLNM (G.E13) | No | 0 | 2513.5 | 21.23 | 182.55 | 15081.71 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
New Construction | EL1 NORTH PERIM PLNM (G.N14) | EL1 NORTH PERIM PLNM (G.N14) | No | 0 | 16208.33 | 1095.44 | 21.23 | 97256.41 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0004
New Construction | EL1 SOUTH PERIM PLNM (G.S12) | EL1 SOUTH PERIM PLNM (G.S12) | No | 0 | 16208.33 | 1095.44 | 21.23 | 97254.59 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
New Construction | EL1 WEST PERIM PLNM (G.W15) | EL1 WEST PERIM PLNM (G.W15) | No | 0 | 2513.5 | 152.56 | 21.23 | 15081.71 | 1 | 0 | 0 | 0 | - | - | Plenum | - | Plenum | 6.0003
New Construction | KITCHEN EL1 CORE SPC (G.C10) | KITCHEN EL1 CORE SPC (G.C10) | Yes | 2000.13 | 2000.13 | 13.12 | 152.56 | 17995.14 | 1 | 2.5 | 3.2411 | 26.4716 | 0.0 | 0.15 | Kitchen | Customized | Kitchen | 8.997
New Construction | LAB EL1 CORE SPC (G.C5) | LAB EL1 CORE SPC (G.C5) | Yes | 90670.84 | 90670.84 | 594.32 | 152.56 | 816077.38 | 1 | 5 | 3.0705 | 20.4693 | 0.0 | 1.0 | Lab | Customized | lab | 9.0004
New Construction | OFFICE EL1 CORE SPC (G.C11) | OFFICE EL1 CORE SPC (G.C11) | Yes | 15879.72 | 15879.72 | 104.1 | 152.56 | 142926.71 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0006
New Construction | OFFICE EL1 EAST PERIM SPC (G.E2) | OFFICE EL1 EAST PERIM SPC (G.E2) | Yes | 2513.5 | 2513.5 | 21.23 | 182.55 | 22622.56 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
New Construction | OFFICE EL1 NORTH PERIM SPC (G.N3) | OFFICE EL1 NORTH PERIM SPC (G.N3) | Yes | 16208.33 | 16208.33 | 1095.44 | 21.23 | 145887.13 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0008
New Construction | OFFICE EL1 SOUTH PERIM SPC (G.S1) | OFFICE EL1 SOUTH PERIM SPC (G.S1) | Yes | 16208.33 | 16208.33 | 1095.44 | 21.23 | 145881.65 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004
New Construction | OFFICE EL1 WEST PERIM SPC (G.W4) | OFFICE EL1 WEST PERIM SPC (G.W4) | Yes | 2513.5 | 2513.5 | 152.56 | 21.23 | 22622.56 | 1 | 5 | 2.047 | 5.1175 | 0.0 | 0.15 | Office | Main | Office | 9.0004